## Summary
This sheet provides the fragility data for use by PACT.
2019-01-27
Sheet Names | NISTIR Classification | Component Name | Component Description | Construction Quality: | Seismic Installation Conditions: | Quantity Value: | Quantity Unit: | Demand Parameter (value): | Demand Parameter (unit): | Number of Damage States: | DS 1 | DS 2 | DS 3 | DS 4 | DS 5 | DS 1, Type | DS 2, Type | DS 3, Type | DS 4, Type | DS 5, Type | DS Hierarchy | Line Number | Fragility Unit of Measure | Round to Integer Unit? | Multi-Occupancy Fragility, allow summation by Floor or Building? | DS 1, Description | DS 2, Description | DS 3, Description | DS 4, Description | DS 5, Description | DS 1, Probability | DS 2, Probability | DS 3, Probability | DS 4, Probability | DS 5, Probability | DS 1, Median Demand | DS 2, Median Demand | DS 3, Median Demand | DS 4, Median Demand | DS 5, Median Demand | DS 1, Data Dispersion | DS 2, Data Dispersion | DS 3, Data Dispersion | DS 4, Data Dispersion | DS 5, Data Dispersion | DS 1, Uncertainty | DS 2, Uncertainty | DS 3, Uncertainty | DS 4, Uncertainty | DS 5, Uncertainty | DS 1, Total Dispersion (Beta) | DS 2, Total Dispersion (Beta) | DS 3, Total Dispersion (Beta) | DS 4, Total Dispersion (Beta) | DS 5, Total Dispersion (Beta) | Correlated? | Directional? | Data Quality | Data Relevance | Documentation Quality | Rationality | DS 1, Repair Description | DS 2, Repair Description | DS 3, Repair Description | DS 4, Repair Description | DS 5, Repair Description | DS 1, Long Lead Time | DS 2, Long Lead Time | DS 3, Long Lead Time | DS 4, Long Lead Time | DS 5, Long Lead Time | DS 1, Potential non-collapse casualty? | DS 2, Potential non-collapse casualty? | DS 3, Potential non-collapse casualty? | DS 4, Potential non-collapse casualty? | DS 5, Potential non-collapse casualty? | DS 1 - Casualty Affected Area | DS 2 - Casualty Affected Area | DS 3 - Casualty Affected Area | DS 4 - Casualty Affected Area | DS 5 - Casualty Affected Area | DS 1 Serious Injury Rate - Median | DS 1 Serious Injury Rate - Dispersion | DS 2 Serious Injury Rate - Median | DS 2 Serious Injury Rate - Dispersion | DS 3 Serious Injury Rate - Median | DS 3 Serious Injury Rate - Dispersion | DS 4 Serious Injury Rate - Median | DS 4 Serious Injury Rate - Dispersion | DS 5 Serious Injury Rate - Median | DS 5 Serious Injury Rate - Dispersion | DS 1 Loss of Life Rate - Median | DS 1 Loss of Life Rate - Dispersion | DS 2 Loss of Life Rate - Median | DS 2 Loss of Life Rate - Dispersion | DS 3 Loss of Life Rate - Median | DS 3 Loss of Life Rate - Dispersion | DS 4 Loss of Life Rate - Median | DS 4 Loss of Life Rate - Dispersion | DS 5 Loss of Life Rate - Median | DS 5 Loss of Life Rate - Dispersion | DS 1, Unsafe Placard Trigger Flag | DS 2, Unsafe Placard Trigger Flag | DS 3, Unsafe Placard Trigger Flag | DS 4, Unsafe Placard Trigger Flag | DS 5, Unsafe Placard Trigger Flag | DS 1, Unsafe Placard Damage Median | DS 2, Unsafe Placard Damage Median | DS 3, Unsafe Placard Damage Median | DS 4, Unsafe Placard Damage Median | DS 5, Unsafe Placard Damage Median | DS 1, Unsafe Placard Damage Dispersion | DS 2, Unsafe Placard Damage Dispersion | DS 3, Unsafe Placard Damage Dispersion | DS 4, Unsafe Placard Damage Dispersion | DS 5, Unsafe Placard Damage Dispersion | Comments / Notes | Date Created | Approved | Official | Author | DS1, Illustrations | DS2, Illustrations | DS3, Illustrations | DS4, Illustrations | DS5, Illustrations | Demand Location (use floor above? Yes/No) | Revision History | Component Sub Types?
B1031.001 | B1031.001 | Bolted shear tab gravity connections | Costing is on a per connection basis. Costing does not include fireproofing removal or reapplication cost. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 4 | DS1 | DS2 | DS3 | DS4 |  | Mutually Exclusive | Mutually Exclusive | Sequential | Sequential |  | Seq(MutEx(DS1,DS2),DS3,DS4) | 1 | EA 1 | YES | NO | Yielding of shear tab and elongation of bolt holes, possible crack initiation around bolt holes or at shear tab weld. Damage in field is either obscured or deemed to not warrant repair. No repair conducted. | Yielding of shear tab and elongation of bolt holes, possible crack initiation around bolt holes or at shear tab weld. | Partial tearing of shear tab and possibility of bolt shear failure (6-bolt or deeper connections). | Complete separation of shear tab, close to complete loss of vertical load resistance. |  | 0.95 | 0.05 | 1 | 1 |  | 0.04 | 0.04 | 0.08 | 0.11 |  | Not Specified | Not Specified | Not Specified | Not Specified |  | 0.4 | 0.4 | 0.4 | 0.4 |  | 0.4 | 0.4 | 0.4 | 0.4 |  | NO | YES | Superior | Superior | Superior | Superior | Careful inspection and welded repair to any cracks and possible replacement of shear tab if bolt hole deformations are excessive (possible for deeper 6-bolt or deeper shear tabs). Field condition is deemed to not warrant repair by field observation. This Damage State is Mutually Exclusive with DS2. See fragility DS1 and DS2 probabilities. | Careful inspection and welded repair to any cracks and possible replacement of shear tab if bolt hole deformations are excessive (possible for deeper 6-bolt or deeper shear tabs). | Repairs will include either welded repair of shear tab or possible complete replacement of shear tab and installation of new bolts. Repairs may require shoring of beam. | Repair will include complete replacement of shear tab and installation of new bolts. Repairs will require shoring of beam. |  | NO | NO | NO | NO |  | NO | NO | NO | NO |  | Not Applicable | Not Applicable | Not Applicable | Not Applicable |  | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 |  |  | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 |  |  | NO | NO | YES | YES |  | 0% | 0% | 20% | 10% |  | 0 | 0 | 0.5 | 0.5 |  | None | Not Given | By User | By User | Greg Deierlein | B1031.001-DS1-1.jpg | B1031.001-DS1-1.jpg | B1031.001-DS2-1.jpg | B1031.001-DS3-1.jpg |  | No | 2016-06-27 Revise DS1 to be MutEx zero cost version of itself. | NO
B1031.011a | B1031.011a | Steel Column Base Plates, Column W < 150 plf | Costing is on a per connection basis. Costing does not include fireproofing removal or reapplication cost. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 4 | DS1 | DS2 | DS3 | DS4 |  | Mutually Exclusive | Mutually Exclusive | Sequential | Sequential |  | Seq(MutEx(DS1,DS2),DS3,DS4) | 2 | EA 1 | YES | NO | Initiation of crack at the fusion line between the column flange and the base plate weld. Damage in field is either obscured or deemed to not warrant repair. No repair conducted. | Initiation of crack at the fusion line between the column flange and the base plate weld. | Propagation of brittle crack into column and/or base plate. | Complete fracture of the column (or column weld) and dislocation of column relative to the base. |  | 0.95 | 0.05 | 1 | 1 |  | 0.04 | 0.04 | 0.07 | 0.1 |  | Not Specified | Not Specified | Not Specified | Not Specified |  | 0.4 | 0.4 | 0.4 | 0.4 |  | 0.4 | 0.4 | 0.4 | 0.4 |  | NO | YES | Superior | Superior | Superior | Superior | The repair will involve removal of a portion of grade slab, gouging out material surrounding the fracture initiating and re-welding, then repair of slab. Field condition is deemed to not warrant repair by field observation. This Damage State is Mutually Exclusive with DS2. See fragility DS1 and DS2 probabilities. | The repair will involve removal of a portion of grade slab, gouging out material surrounding the fracture initiating and re-welding, then repair of slab. | Depending on the crack trajectory, the repair will range from replacement of a portion of the column or base plate to full replacement of the column base. Replacement will require shoring of column, torch cutting to remove damaged material, and fabrication and field welding to install replacement material. | Repair would likely involve replacing the entire base plate assembly and most of the column in the story above the base plate. |  | NO | NO | NO | NO |  | NO | NO | NO | NO |  | Not Applicable | Not Applicable | Not Applicable | Not Applicable |  | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 |  |  | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 |  |  | NO | NO | YES | YES |  | 0% | 0% | 25% | 10% |  | 0 | 0 | 0.5 | 0.5 |  | None | Not Given | By User | By User | Greg Deierlein | B1031.011a-schematic.JPG | B1031.011a-schematic.JPG | none | none |  | No | 2016-06-27 Revise DS1 to be MutEx zero cost version of itself. | YES
B1031.011b | B1031.011b | Steel Column Base Plates, Column 150 plf < W < 300 plf | Costing is on a per connection basis. Costing does not include fireproofing removal or reapplication cost. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 4 | DS1 | DS2 | DS3 | DS4 |  | Mutually Exclusive | Mutually Exclusive | Sequential | Sequential |  | Seq(MutEx(DS1,DS2),DS3,DS4) | 3 | EA 1 | YES | NO | Initiation of crack at the fusion line between the column flange and the base plate weld. Damage in field is either obscured or deemed to not warrant repair. No repair conducted. | Initiation of crack at the fusion line between the column flange and the base plate weld. | Propagation of brittle crack into column and/or base plate. | Complete fracture of the column (or column weld) and dislocation of column relative to the base. |  | 0.95 | 0.05 | 1 | 1 |  | 0.04 | 0.04 | 0.07 | 0.1 |  | Not Specified | Not Specified | Not Specified | Not Specified |  | 0.4 | 0.4 | 0.4 | 0.4 |  | 0.4 | 0.4 | 0.4 | 0.4 |  | NO | YES | Superior | Superior | Superior | Superior | The repair will involve removal of a portion of grade slab, gouging out material surrounding the fracture initiating and re-welding, then repair of slab. Field condition is deemed to not warrant repair by field observation. This Damage State is Mutually Exclusive with DS2. See fragility DS1 and DS2 probabilities. | The repair will involve removal of a portion of grade slab, gouging out material surrounding the fracture initiating and re-welding, then repair of slab. | Depending on the crack trajectory, the repair will range from replacement of a portion of the column or base plate to full replacement of the column base. Replacement will require shoring of column, torch cutting to remove damaged material, and fabrication | Repair would likely involve replacing the entire base plate assembly and most of the column in the story above the base plate. |  | NO | NO | NO | NO |  | NO | NO | NO | NO |  | Not Applicable | Not Applicable | Not Applicable | Not Applicable |  | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 |  |  | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 |  |  | NO | NO | YES | YES |  | 0% | 0% | 25% | 10% |  | 0 | 0 | 0.5 | 0.5 |  | None | Not Given | By User | By User | Greg Deierlein | B1031.011a-schematic.JPG | B1031.011a-schematic.JPG | none | none |  | No | 2016-06-27 Revise DS1 to be MutEx zero cost version of itself. | YES
B1031.011c | B1031.011c | Steel Column Base Plates, Column W > 300 plf | Costing is on a per connection basis. Costing does not include fireproofing removal or reapplication cost. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 4 | DS1 | DS2 | DS3 | DS4 |  | Mutually Exclusive | Mutually Exclusive | Sequential | Sequential |  | Seq(MutEx(DS1,DS2),DS3,DS4) | 4 | EA 1 | YES | NO | Initiation of crack at the fusion line between the column flange and the base plate weld. Damage in field is either obscured or deemed to not warrant repair. No repair conducted. | Initiation of crack at the fusion line between the column flange and the base plate weld. | Propagation of brittle crack into column and/or base plate. | Complete fracture of the column (or column weld) and dislocation of column relative to the base. |  | 0.95 | 0.05 | 1 | 1 |  | 0.04 | 0.04 | 0.07 | 0.1 |  | Not Specified | Not Specified | Not Specified | Not Specified |  | 0.4 | 0.4 | 0.4 | 0.4 |  | 0.4 | 0.4 | 0.4 | 0.4 |  | NO | YES | Superior | Superior | Superior | Superior | The repair will involve removal of a portion of grade slab, gouging out material surrounding the fracture initiating and re-welding, then repair of slab. Field condition is deemed to not warrant repair by field observation. This Damage State is Mutually Exclusive with DS2. See fragility DS1 and DS2 probabilities. | The repair will involve removal of a portion of grade slab, gouging out material surrounding the fracture initiating and re-welding, then repair of slab. | Depending on the crack trajectory, the repair will range from replacement of a portion of the column or base plate to full replacement of the column base. Replacement will require shoring of column, torch cutting to remove damaged material, and fabrication | Repair would likely involve replacing the entire base plate assembly and most of the column in the story above the base plate. |  | NO | NO | NO | NO |  | NO | NO | NO | NO |  | Not Applicable | Not Applicable | Not Applicable | Not Applicable |  | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 |  |  | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 |  |  | NO | NO | YES | YES |  | 0% | 0% | 25% | 10% |  | 0 | 0 | 0.5 | 0.5 |  | None | Not Given | By User | By User | Greg Deierlein | B1031.011a-schematic.JPG | B1031.011a-schematic.JPG | none | none |  | No | 2016-06-27 Revise DS1 to be MutEx zero cost version of itself. | YES
B1031.021a | B1031.021a | Welded column splices, Column W < 150 plf | Costing is on a per connection basis. Costing does not include fireproofing removal or reapplication cost. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 3 | DS1 | DS2 | DS3 |  |  | Mutually Exclusive | Mutually Exclusive | Sequential |  |  | Seq(MutEx(DS1,DS2),DS3) | 5 | EA 1 | YES | NO | Ductile fracture of the groove weld flange splice. Damage in field is either obscured or deemed to not warrant repair. No repair conducted. | Ductile fracture of the groove weld flange splice. | DS1 followed by complete failure of the web splice plate and dislocation of the two column segments on either side of the splice. |  |  | 0.95 | 0.05 | 1 |  |  | 0.02 | 0.02 | 0.05 |  |  | Not Specified | Not Specified | Not Specified |  |  | 0.4 | 0.4 | 0.4 |  |  | 0.4 | 0.4 | 0.4 |  |  | NO | YES | Superior | Superior | Superior | Superior | Repair would involve gouging out the material adjacent to the fracture and repairing with a new groove weld. Field condition is deemed to not warrant repair by field observation. This Damage State is Mutually Exclusive with DS2. See fragility DS1 and DS2 probabilities. | Repair would involve gouging out the material adjacent to the fracture and repairing with a new groove weld. | Repair may not be practically feasible, but would require either realignment or replacement of adjacent column segments and rewelding of splice. |  |  | NO | NO | NO |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | NO | YES |  |  | 0% | 0% | 2% |  |  | 0 | 0 | 0.5 |  |  | Fracture is not expected where weld has adequate toughness and the maximum weld root stress is below 1.5Fu from column P/A+M/S under story drift using A and S from weld root area. | Not Given | By User | By User | Greg Deierlein | B1031.021a-DS1-1.JPG | B1031.021a-DS1-1.JPG | B1031.021a-DS2-1.JPG |  |  | No | 2015-07-28 revise DS1 and DS2 description and repair to align with FEMA P-38 BD-3.8.3 Page 23. 2016-06-27 Revise DS1 to be MutEx zero cost version of itself. | YES
B1031.021b | B1031.021b | Welded column splices, Column 150 plf < W < 300 plf | Costing is on a per connection basis. Costing does not include fireproofing removal or reapplication cost. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 3 | DS1 | DS2 | DS3 |  |  | Mutually Exclusive | Mutually Exclusive | Sequential |  |  | Seq(MutEx(DS1,DS2),DS3) | 6 | EA 1 | YES | NO | Ductile fracture of the groove weld flange splice. Damage in field is either obscured or deemed to not warrant repair. No repair conducted. | Ductile fracture of the groove weld flange splice. | DS1 followed by complete failure of the web splice plate and dislocation of the two column segments on either side of the splice. |  |  | 0.95 | 0.05 | 1 |  |  | 0.02 | 0.02 | 0.05 |  |  | Not Specified | Not Specified | Not Specified |  |  | 0.4 | 0.4 | 0.4 |  |  | 0.4 | 0.4 | 0.4 |  |  | NO | YES | Superior | Superior | Superior | Superior | Repair would involve gouging out the material adjacent to the fracture and repairing with a new groove weld. Field condition is deemed to not warrant repair by field observation. This Damage State is Mutually Exclusive with DS2. See fragility DS1 and DS2 probabilities. | Repair would involve gouging out the material adjacent to the fracture and repairing with a new groove weld. | Repair may not be practically feasible, but would require either realignment or replacement of adjacent column segments and rewelding of splice. |  |  | NO | NO | NO |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | NO | YES |  |  | 0% | 0% | 2% |  |  | 0 | 0 | 0.5 |  |  | Fracture is not expected where weld has adequate toughness and the maximum weld root stress is below 1.5Fu from column P/A+M/S under story drift using A and S from weld root area. | Not Given | By User | By User | Greg Deierlein | B1031.021a-DS1-1.JPG | B1031.021a-DS1-1.JPG | B1031.021a-DS2-1.JPG |  |  | No | 2015-07-28 revise DS1 and DS2 description and repair to align with FEMA P-38 BD-3.8.3 Page 23. 2016-06-27 Revise DS1 to be MutEx zero cost version of itself. | YES
B1031.021c | B1031.021c | Welded column splices, Column W > 300 plf | Costing is on a per connection basis. Costing does not include fireproofing removal or reapplication cost. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 3 | DS1 | DS2 | DS3 |  |  | Mutually Exclusive | Mutually Exclusive | Sequential |  |  | Seq(MutEx(DS1,DS2),DS3) | 7 | EA 1 | YES | NO | Ductile fracture of the groove weld flange splice. Damage in field is either obscured or deemed to not warrant repair. No repair conducted. | Ductile fracture of the groove weld flange splice. | DS1 followed by complete failure of the web splice plate and dislocation of the two column segments on either side of the splice. |  |  | 0.95 | 0.05 | 1 |  |  | 0.02 | 0.02 | 0.05 |  |  | Not Specified | Not Specified | Not Specified |  |  | 0.4 | 0.4 | 0.4 |  |  | 0.4 | 0.4 | 0.4 |  |  | NO | YES | Superior | Superior | Superior | Superior | Repair would involve gouging out the material adjacent to the fracture and repairing with a new groove weld. Field condition is deemed to not warrant repair by field observation. This Damage State is Mutually Exclusive with DS2. See fragility DS1 and DS2 probabilities. | Repair would involve gouging out the material adjacent to the fracture and repairing with a new groove weld. | Repair may not be practically feasible, but would require either realignment or replacement of adjacent column segments and rewelding of splice. |  |  | NO | NO | NO |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | NO | YES |  |  | 0% | 0% | 2% |  |  | 0 | 0 | 0.5 |  |  | Fracture is not expected where weld has adequate toughness and the maximum weld root stress is below 1.5Fu from column P/A+M/S under story drift using A and S from weld root area. | Not Given | By User | By User | Greg Deierlein | B1031.021a-DS1-1.JPG | B1031.021a-DS1-1.JPG | B1031.021a-DS2-1.JPG |  |  | No | 2015-07-28 revise DS1 and DS2 description and repair to align with FEMA P-38 BD-3.8.3 Page 23. 2016-06-27 Revise DS1 to be MutEx zero cost version of itself. | YES
B1033.001a | B1033.001a | Special Concentric Braced Frame w WF braces, balanced design criteria, Chevron Brace, Brace w < 40 PLF | Costing is on a per bay basis. Costing does not include fireproofing removal or reapplication cost. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 4 | DS1 | DS2 | DS3 | DS4 |  | Sequential | Sequential | Sequential | Sequential |  | Seq(DS1,DS2,DS3,DS4) | 8 | EA 1 | YES | NO | Buckling of the brace has begun but does not exceed the depth of the brace. Initial yielding of the gusset has begun. Yielding has initiated in framing at gusset plates but no buckling has occurred. Residual buckling of the brace has occurred but is barely noticeable to the naked eye and does not exceed half the brace depth. Residual drift is slight. | Buckling of brace in excess of the brace depth. Initiation of yielding and out-of-plane deformation of the gusset. Initiation of cracking of welds of gusset. Initiation of yielding in beams and columns adjacent to gusset. | Buckling of brace in excess of 2 times brace depth. Yielding and out-of-plane deformation of gusset. Cracking and tearing of welds and gussets adjacent to welds but crack length is less than critical for fracture. Significant yielding and local buckling in beams and columns adjacent to gusset. | Fracture of brace or gusset. Buckling of gusset. Severe yielding of beams and columns adjacent to the gusset with possibility of local buckling and cracking in the yielded areas. |  | 1 | 1 | 1 | 1 |  | 0.0035 | 0.0058 | 0.0142 | 0.0283 |  | 0.38 | 0.6 | 0.45 | 0.05 |  | 0.25 | 0.25 | 0.25 | 0.25 |  | 0.45 | 0.65 | 0.5 | 0.25 |  | NO | YES | Superior | Superior | Average | Superior | Brace damage is largely aesthetic. Heat straightening may be desirable but replacement would be for aesthetic reasons. Gusset has minor loss of strength and stiffness and straightening or repair may be desirable aesthetic reasons. | Brace has lost significant axial capacity, and replacement of braces is likely required. The gusset plate may have significant deformation and replacement may also be needed. Local beam and column yielding has occurred and straightening may be desirable for aesthetic reasons. | Brace and gusset are severely damaged with significant loss in stiffness and resistance, and both likely require replacement. Yielding and local buckling of beams and columns may be repaired by heat straightening, stiffeners or reinforcement, if there is no cracking or tearing. If cracking or tearing has initiated more substantial repair is needed | Brace and or gusset have fractured and require replacement. Yielding and local buckling of beams and columns may be repaired by heat straightening, stiffeners or reinforcement, if there is no cracking or tearing. If cracking or tearing has initiated more substantial repair is needed |  | NO | NO | NO | NO |  | NO | NO | NO | NO |  | Not Applicable | Not Applicable | Not Applicable | Not Applicable |  | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 |  |  | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 |  |  | NO | YES | YES | YES |  | 0% | 60% | 40% | 20% |  | 0 | 0.5 | 0.5 | 0.5 |  | None | Not Given | By User | By User | Not Given | none | B1033.001a-DS2-1.JPG | B1033.001a-DS3-1.JPG | B1033.001a-DS4-1.JPG |  | No | 2011-08-24 Negative probability below 0.5% drift - overlap deemed acceptable. 2016-08-17 time consequence adjusted to avoid decreasing consequence with increasing member weight. | YES
B1033.001b | B1033.001b | Special Concentric Braced Frame w WF braces, balanced design criteria, Chevron Brace, Brace 41 PLF < w < 99 PLF | Costing is on a per bay basis. Costing does not include fireproofing removal or reapplication cost. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 4 | DS1 | DS2 | DS3 | DS4 |  | Sequential | Sequential | Sequential | Sequential |  | Seq(DS1,DS2,DS3,DS4) | 9 | EA 1 | YES | NO | Buckling of the brace has begun but does not exceed the depth of the brace. Initial yielding of the gusset has begun. Yielding has initiated in framing at gusset plates but no buckling has occurred. Residual buckling of the brace has occurred but is barely noticeable to the naked eye and does not exceed half the brace depth. Residual drift is slight. | Buckling of brace in excess of the brace depth. Initiation of yielding and out-of-plane deformation of the gusset. Initiation of cracking of welds of gusset. Initiation of yielding in beams and columns adjacent to gusset. | Buckling of brace in excess of 2 times brace depth. Yielding and out-of-plane deformation of gusset. Cracking and tearing of welds and gussets adjacent to welds but crack length is less than critical for fracture. Significant yielding and local buckling in beams and columns adjacent to gusset. | Fracture of brace or gusset. Buckling of gusset. Severe yielding of beams and columns adjacent to the gusset with possibility of local buckling and cracking in the yielded areas. |  | 1 | 1 | 1 | 1 |  | 0.0035 | 0.0058 | 0.0142 | 0.0283 |  | 0.38 | 0.6 | 0.45 | 0.05 |  | 0.25 | 0.25 | 0.25 | 0.25 |  | 0.45 | 0.65 | 0.5 | 0.25 |  | NO | YES | Superior | Superior | Average | Superior | Brace damage is largely aesthetic. Heat straightening may be desirable but replacement would be for aesthetic reasons. Gusset has minor loss of strength and stiffness and straightening or repair may be desirable aesthetic reasons. | Brace has lost significant axial capacity, and replacement of braces is likely required. The gusset plate may have significant deformation and replacement may also be needed. Local beam and column yielding has occurred and straightening may be desirable for aesthetic reasons. | Brace and gusset are severely damaged with significant loss in stiffness and resistance, and both likely require replacement. Yielding and local buckling of beams and columns may be repaired by heat straightening, stiffeners or reinforcement, if there is no cracking or tearing. If cracking or tearing has initiated more substantial repair is needed | Brace and or gusset have fractured and require replacement. Yielding and local buckling of beams and columns may be repaired by heat straightening, stiffeners or reinforcement, if there is no cracking or tearing. If cracking or tearing has initiated more substantial repair is needed |  | NO | NO | NO | NO |  | NO | NO | NO | NO |  | Not Applicable | Not Applicable | Not Applicable | Not Applicable |  | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 |  |  | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 |  |  | NO | YES | YES | YES |  | 0% | 60% | 40% | 20% |  | 0 | 0.5 | 0.5 | 0.5 |  | None | Not Given | By User | By User | Not Given | none | B1033.001a-DS2-1.JPG | B1033.001a-DS3-1.JPG | B1033.001a-DS4-1.JPG |  | No | 2011-08-24 Negative probability below 0.5% drift - overlap deemed acceptable. 2016-08-17 time consequence adjusted to avoid decreasing consequence with increasing member weight. | YES
B1033.001c | B1033.001c | Special Concentric Braced Frame w WF braces, balanced design criteria, Chevron Brace, Brace w > 100 PLF | Costing is on a per bay basis. Costing does not include fireproofing removal or reapplication cost. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 4 | DS1 | DS2 | DS3 | DS4 |  | Sequential | Sequential | Sequential | Sequential |  | Seq(DS1,DS2,DS3,DS4) | 10 | EA 1 | YES | NO | Buckling of the brace has begun but does not exceed the depth of the brace. Initial yielding of the gusset has begun. Yielding has initiated in framing at gusset plates but no buckling has occurred. Residual buckling of the brace has occurred but is barely noticeable to the naked eye and does not exceed half the brace depth. Residual drift is slight. | Buckling of brace in excess of the brace depth. Initiation of yielding and out-of-plane deformation of the gusset. Initiation of cracking of welds of gusset. Initiation of yielding in beams and columns adjacent to gusset. | Buckling of brace in excess of 2 times brace depth. Yielding and out-of-plane deformation of gusset. Cracking and tearing of welds and gussets adjacent to welds but crack length is less than critical for fracture. Significant yielding and local buckling in beams and columns adjacent to gusset. | Fracture of brace or gusset. Buckling of gusset. Severe yielding of beams and columns adjacent to the gusset with possibility of local buckling and cracking in the yielded areas. |  | 1 | 1 | 1 | 1 |  | 0.0035 | 0.0058 | 0.0142 | 0.0283 |  | 0.38 | 0.6 | 0.45 | 0.05 |  | 0.25 | 0.25 | 0.25 | 0.25 |  | 0.45 | 0.65 | 0.5 | 0.25 |  | NO | YES | Superior | Superior | Average | Superior | Brace damage is largely aesthetic. Heat straightening may be desirable but replacement would be for aesthetic reasons. Gusset has minor loss of strength and stiffness and straightening or repair may be desirable aesthetic reasons. | Brace has lost significant axial capacity, and replacement of braces is likely required. The gusset plate may have significant deformation and replacement may also be needed. Local beam and column yielding has occurred and straightening may be desirable for aesthetic reasons. | Brace and gusset are severely damaged with significant loss in stiffness and resistance, and both likely require replacement. Yielding and local buckling of beams and columns may be repaired by heat straightening, stiffeners or reinforcement, if there is no cracking or tearing. If cracking or tearing has initiated more substantial repair is needed | Brace and or gusset have fractured and require replacement. Yielding and local buckling of beams and columns may be repaired by heat straightening, stiffeners or reinforcement, if there is no cracking or tearing. If cracking or tearing has initiated more substantial repair is needed |  | NO | NO | NO | NO |  | NO | NO | NO | NO |  | Not Applicable | Not Applicable | Not Applicable | Not Applicable |  | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 |  |  | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 |  |  | NO | YES | YES | YES |  | 0% | 60% | 40% | 20% |  | 0 | 0.5 | 0.5 | 0.5 |  | None | Not Given | By User | By User | Not Given | none | B1033.001a-DS2-1.JPG | B1033.001a-DS3-1.JPG | B1033.001a-DS4-1.JPG |  | No | 2011-08-24 Negative probability below 0.5% drift - overlap deemed acceptable. 2016-08-17 time consequence adjusted to avoid decreasing consequence with increasing member weight. | YES
B1033.002a | B1033.002a | Special Concentric Braced Frame w WF braces, balanced design criteria, Single Diagonal Brace, Brace w < 40 PLF | Costing is on a per bay basis. Costing does not include fireproofing removal or reapplication cost. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 4 | DS1 | DS2 | DS3 | DS4 |  | Sequential | Sequential | Sequential | Sequential |  | Seq(DS1,DS2,DS3,DS4) | 11 | EA 1 | YES | NO | Buckling of the brace has begun but does not exceed the depth of the brace. Initial yielding of the gusset has begun. Yielding has initiated in framing at gusset plates but no buckling has occurred. Residual buckling of the brace has occurred but is barely noticeable to the naked eye and does not exceed half the brace depth. Residual drift is slight. | Buckling of brace in excess of the brace depth. Initiation of yielding and out-of-plane deformation of the gusset. Initiation of cracking of welds of gusset. Initiation of yielding in beams and columns adjacent to gusset. | Buckling of brace in excess of 2 times brace depth. Yielding and out-of-plane deformation of gusset. Cracking and tearing of welds and gussets adjacent to welds but crack length is less than critical for fracture. Significant yielding and local buckling in beams and columns adjacent to gusset. | Fracture of brace or gusset. Buckling of gusset. Severe yielding of beams and columns adjacent to the gusset with possibility of local buckling and cracking in the yielded areas. |  | 1 | 1 | 1 | 1 |  | 0.0035 | 0.0058 | 0.0142 | 0.0283 |  | 0.38 | 0.6 | 0.45 | 0.05 |  | 0.25 | 0.25 | 0.25 | 0.25 |  | 0.45 | 0.65 | 0.5 | 0.25 |  | NO | YES | Superior | Superior | Average | Superior | Brace damage is largely aesthetic. Heat straightening may be desirable but replacement would be for aesthetic reasons. Gusset has minor loss of strength and stiffness and straightening or repair may be desirable aesthetic reasons. | Brace has lost significant axial capacity, and replacement of braces is likely required. The gusset plate may have significant deformation and replacement may also be needed. Local beam and column yielding has occurred and straightening may be desirable for aesthetic reasons. | Brace and gusset are severely damaged with significant loss in stiffness and resistance, and both likely require replacement. Yielding and local buckling of beams and columns may be repaired by heat straightening, stiffeners or reinforcement, if there is no cracking or tearing. If cracking or tearing has initiated more substantial repair is needed | Brace and or gusset have fractured and require replacement. Yielding and local buckling of beams and columns may be repaired by heat straightening, stiffeners or reinforcement, if there is no cracking or tearing. If cracking or tearing has initiated more substantial repair is needed |  | NO | NO | NO | NO |  | NO | NO | NO | NO |  | Not Applicable | Not Applicable | Not Applicable | Not Applicable |  | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 |  |  | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 |  |  | NO | YES | YES | YES |  | 0% | 60% | 40% | 20% |  | 0 | 0.5 | 0.5 | 0.5 |  | None | Not Given | By User | By User | Not Given | none | B1033.001a-DS2-1.JPG | B1033.001a-DS3-1.JPG | B1033.001a-DS4-1.JPG |  | No | 2011-08-24 Negative probability below 0.5% drift - overlap deemed acceptable. 2016-08-17 time consequence adjusted to avoid decreasing consequence with increasing member weight. | YES
B1033.002b | B1033.002b | Special Concentric Braced Frame w WF braces, balanced design criteria, Single Diagonal Brace, 41 PLF < w < 99 PLF | Costing is on a per bay basis. Costing does not include fireproofing removal or reapplication cost. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 4 | DS1 | DS2 | DS3 | DS4 |  | Sequential | Sequential | Sequential | Sequential |  | Seq(DS1,DS2,DS3,DS4) | 12 | EA 1 | YES | NO | Buckling of the brace has begun but does not exceed the depth of the brace. Initial yielding of the gusset has begun. Yielding has initiated in framing at gusset plates but no buckling has occurred. Residual buckling of the brace has occurred but is barely noticeable to the naked eye and does not exceed half the brace depth. Residual drift is slight. | Buckling of brace in excess of the brace depth. Initiation of yielding and out-of-plane deformation of the gusset. Initiation of cracking of welds of gusset. Initiation of yielding in beams and columns adjacent to gusset. | Buckling of brace in excess of 2 times brace depth. Yielding and out-of-plane deformation of gusset. Cracking and tearing of welds and gussets adjacent to welds but crack length is less than critical for fracture. Significant yielding and local buckling in beams and columns adjacent to gusset. | Fracture of brace or gusset. Buckling of gusset. Severe yielding of beams and columns adjacent to the gusset with possibility of local buckling and cracking in the yielded areas. |  | 1 | 1 | 1 | 1 |  | 0.0035 | 0.0058 | 0.0142 | 0.0283 |  | 0.38 | 0.6 | 0.45 | 0.05 |  | 0.25 | 0.25 | 0.25 | 0.25 |  | 0.45 | 0.65 | 0.5 | 0.25 |  | NO | YES | Superior | Superior | Average | Superior | Brace damage is largely aesthetic. Heat straightening may be desirable but replacement would be for aesthetic reasons. Gusset has minor loss of strength and stiffness and straightening or repair may be desirable aesthetic reasons. | Brace has lost significant axial capacity, and replacement of braces is likely required. The gusset plate may have significant deformation and replacement may also be needed. Local beam and column yielding has occurred and straightening may be desirable for aesthetic reasons. | Brace and gusset are severely damaged with significant loss in stiffness and resistance, and both likely require replacement. Yielding and local buckling of beams and columns may be repaired by heat straightening, stiffeners or reinforcement, if there is no cracking or tearing. If cracking or tearing has initiated more substantial repair is needed | Brace and or gusset have fractured and require replacement. Yielding and local buckling of beams and columns may be repaired by heat straightening, stiffeners or reinforcement, if there is no cracking or tearing. If cracking or tearing has initiated more substantial repair is needed |  | NO | NO | NO | NO |  | NO | NO | NO | NO |  | Not Applicable | Not Applicable | Not Applicable | Not Applicable |  | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 |  |  | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 |  |  | NO | YES | YES | YES |  | 0% | 60% | 40% | 20% |  | 0 | 0.5 | 0.5 | 0.5 |  | None | Not Given | By User | By User | Not Given | none | B1033.001a-DS2-1.JPG | B1033.001a-DS3-1.JPG | B1033.001a-DS4-1.JPG |  | No | 2011-08-24 Negative probability below 0.5% drift - overlap deemed acceptable. 2016-08-17 time consequence adjusted to avoid decreasing consequence with increasing member weight. | YES
B1033.002c | B1033.002c | Special Concentric Braced Frame w WF braces, balanced design criteria, Single Diagonal Brace, Brace w > 100 PLF | Costing is on a per bay basis. Costing does not include fireproofing removal or reapplication cost. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 4 | DS1 | DS2 | DS3 | DS4 |  | Sequential | Sequential | Sequential | Sequential |  | Seq(DS1,DS2,DS3,DS4) | 13 | EA 1 | YES | NO | Buckling of the brace has begun but does not exceed the depth of the brace. Initial yielding of the gusset has begun. Yielding has initiated in framing at gusset plates but no buckling has occurred. Residual buckling of the brace has occurred but is barely noticeable to the naked eye and does not exceed half the brace depth. Residual drift is slight. | Buckling of brace in excess of the brace depth. Initiation of yielding and out-of-plane deformation of the gusset. Initiation of cracking of welds of gusset. Initiation of yielding in beams and columns adjacent to gusset. | Buckling of brace in excess of 2 times brace depth. Yielding and out-of-plane deformation of gusset. Cracking and tearing of welds and gussets adjacent to welds but crack length is less than critical for fracture. Significant yielding and local buckling in beams and columns adjacent to gusset. | Fracture of brace or gusset. Buckling of gusset. Severe yielding of beams and columns adjacent to the gusset with possibility of local buckling and cracking in the yielded areas. |  | 1 | 1 | 1 | 1 |  | 0.0035 | 0.0058 | 0.0142 | 0.0283 |  | 0.38 | 0.6 | 0.45 | 0.05 |  | 0.25 | 0.25 | 0.25 | 0.25 |  | 0.45 | 0.65 | 0.5 | 0.25 |  | NO | YES | Superior | Superior | Average | Superior | Brace damage is largely aesthetic. Heat straightening may be desirable but replacement would be for aesthetic reasons. Gusset has minor loss of strength and stiffness and straightening or repair may be desirable aesthetic reasons. | Brace has lost significant axial capacity, and replacement of braces is likely required. The gusset plate may have significant deformation and replacement may also be needed. Local beam and column yielding has occurred and straightening may be desirable for aesthetic reasons. | Brace and gusset are severely damaged with significant loss in stiffness and resistance, and both likely require replacement. Yielding and local buckling of beams and columns may be repaired by heat straightening, stiffeners or reinforcement, if there is no cracking or tearing. If cracking or tearing has initiated more substantial repair is needed | Brace and or gusset have fractured and require replacement. Yielding and local buckling of beams and columns may be repaired by heat straightening, stiffeners or reinforcement, if there is no cracking or tearing. If cracking or tearing has initiated more substantial repair is needed |  | NO | NO | NO | NO |  | NO | NO | NO | NO |  | Not Applicable | Not Applicable | Not Applicable | Not Applicable |  | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 |  |  | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 |  |  | NO | YES | YES | YES |  | 0% | 60% | 40% | 20% |  | 0 | 0.5 | 0.5 | 0.5 |  | None | Not Given | By User | By User | Not Given | none | B1033.001a-DS2-1.JPG | B1033.001a-DS3-1.JPG | B1033.001a-DS4-1.JPG |  | No | 2011-08-24 Negative probability below 0.5% drift - overlap deemed acceptable. 2016-08-17 time consequence adjusted to avoid decreasing consequence with increasing member weight. | YES
B1033.003a | B1033.003a | Special Concentric Braced Frame w WF braces, balanced design criteria, X Brace, Brace w < 40 PLF | Costing is on a per bay basis. Costing does not include fireproofing removal or reapplication cost. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 4 | DS1 | DS2 | DS3 | DS4 |  | Sequential | Sequential | Sequential | Sequential |  | Seq(DS1,DS2,DS3,DS4) | 14 | EA 1 | YES | NO | Buckling of the brace has begun but does not exceed the depth of the brace. Initial yielding of the gusset has begun. Yielding has initiated in framing at gusset plates but no buckling has occurred. Residual buckling of the brace has occurred but is barely noticeable to the naked eye and does not exceed half the brace depth. Residual drift is slight. | Buckling of brace in excess of the brace depth. Initiation of yielding and out-of-plane deformation of the gusset. Initiation of cracking of welds of gusset. Initiation of yielding in beams and columns adjacent to gusset. | Buckling of brace in excess of 2 times brace depth. Yielding and out-of-plane deformation of gusset. Cracking and tearing of welds and gussets adjacent to welds but crack length is less than critical for fracture. Significant yielding and local buckling in beams and columns adjacent to gusset. | Fracture of brace or gusset. Buckling of gusset. Severe yielding of beams and columns adjacent to the gusset with possibility of local buckling and cracking in the yielded areas. |  | 1 | 1 | 1 | 1 |  | 0.0035 | 0.0058 | 0.0142 | 0.0283 |  | 0.38 | 0.6 | 0.45 | 0.05 |  | 0.25 | 0.25 | 0.25 | 0.25 |  | 0.45 | 0.65 | 0.5 | 0.25 |  | NO | YES | Superior | Superior | Average | Superior | Brace damage is largely aesthetic. Heat straightening may be desirable but replacement would be for aesthetic reasons. Gusset has minor loss of strength and stiffness and straightening or repair may be desirable aesthetic reasons. | Brace has lost significant axial capacity, and replacement of braces is likely required. The gusset plate may have significant deformation and replacement may also be needed. Local beam and column yielding has occurred and straightening may be desirable for aesthetic reasons. | Brace and gusset are severely damaged with significant loss in stiffness and resistance, and both likely require replacement. Yielding and local buckling of beams and columns may be repaired by heat straightening, stiffeners or reinforcement, if there is no cracking or tearing. If cracking or tearing has initiated more substantial repair is needed | Brace and or gusset have fractured and require replacement. Yielding and local buckling of beams and columns may be repaired by heat straightening, stiffeners or reinforcement, if there is no cracking or tearing. If cracking or tearing has initiated more substantial repair is needed |  | NO | NO | NO | NO |  | NO | NO | NO | NO |  | Not Applicable | Not Applicable | Not Applicable | Not Applicable |  | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 |  |  | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 |  |  | NO | YES | YES | YES |  | 0% | 60% | 40% | 20% |  | 0 | 0.5 | 0.5 | 0.5 |  | None | Not Given | By User | By User | Not Given | none | B1033.001a-DS2-1.JPG | B1033.001a-DS3-1.JPG | B1033.001a-DS4-1.JPG |  | No | 2011-08-24 Negative probability below 0.5% drift - overlap deemed acceptable. 2016-08-17 time consequence adjusted to avoid decreasing consequence with increasing member weight. | YES
B1033.003b | B1033.003b | Special Concentric Braced Frame w WF braces, balanced design criteria, X Brace, 41 PLF < w < 99 PLF | Costing is on a per bay basis. Costing does not include fireproofing removal or reapplication cost. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 4 | DS1 | DS2 | DS3 | DS4 |  | Sequential | Sequential | Sequential | Sequential |  | Seq(DS1,DS2,DS3,DS4) | 15 | EA 1 | YES | NO | Buckling of the brace has begun but does not exceed the depth of the brace. Initial yielding of the gusset has begun. Yielding has initiated in framing at gusset plates but no buckling has occurred. Residual buckling of the brace has occurred but is barely noticeable to the naked eye and does not exceed half the brace depth. Residual drift is slight. | Buckling of brace in excess of the brace depth. Initiation of yielding and out-of-plane deformation of the gusset. Initiation of cracking of welds of gusset. Initiation of yielding in beams and columns adjacent to gusset. | Buckling of brace in excess of 2 times brace depth. Yielding and out-of-plane deformation of gusset. Cracking and tearing of welds and gussets adjacent to welds but crack length is less than critical for fracture. Significant yielding and local buckling in beams and columns adjacent to gusset. | Fracture of brace or gusset. Buckling of gusset. Severe yielding of beams and columns adjacent to the gusset with possibility of local buckling and cracking in the yielded areas. |  | 1 | 1 | 1 | 1 |  | 0.0035 | 0.0058 | 0.0142 | 0.0283 |  | 0.38 | 0.6 | 0.45 | 0.05 |  | 0.25 | 0.25 | 0.25 | 0.25 |  | 0.45 | 0.65 | 0.5 | 0.25 |  | NO | YES | Superior | Superior | Average | Superior | Brace damage is largely aesthetic. Heat straightening may be desirable but replacement would be for aesthetic reasons. Gusset has minor loss of strength and stiffness and straightening or repair may be desirable aesthetic reasons. | Brace has lost significant axial capacity, and replacement of braces is likely required. The gusset plate may have significant deformation and replacement may also be needed. Local beam and column yielding has occurred and straightening may be desirable for aesthetic reasons. | Brace and gusset are severely damaged with significant loss in stiffness and resistance, and both likely require replacement. Yielding and local buckling of beams and columns may be repaired by heat straightening, stiffeners or reinforcement, if there is no cracking or tearing. If cracking or tearing has initiated more substantial repair is needed | Brace and or gusset have fractured and require replacement. Yielding and local buckling of beams and columns may be repaired by heat straightening, stiffeners or reinforcement, if there is no cracking or tearing. If cracking or tearing has initiated more substantial repair is needed |  | NO | NO | NO | NO |  | NO | NO | NO | NO |  | Not Applicable | Not Applicable | Not Applicable | Not Applicable |  | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 |  |  | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 |  |  | NO | YES | YES | YES |  | 0% | 60% | 40% | 20% |  | 0 | 0.5 | 0.5 | 0.5 |  | None | Not Given | By User | By User | Not Given | none | B1033.001a-DS2-1.JPG | B1033.001a-DS3-1.JPG | B1033.001a-DS4-1.JPG |  | No | 2011-08-24 Negative probability below 0.5% drift - overlap deemed acceptable. 2016-08-17 time consequence adjusted to avoid decreasing consequence with increasing member weight. | YES
B1033.003c | B1033.003c | Special Concentric Braced Frame w WF braces, balanced design criteria, X Brace, Brace w > 100 PLF | Costing is on a per bay basis. Costing does not include fireproofing removal or reapplication cost. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 4 | DS1 | DS2 | DS3 | DS4 |  | Sequential | Sequential | Sequential | Sequential |  | Seq(DS1,DS2,DS3,DS4) | 16 | EA 1 | YES | NO | Buckling of the brace has begun but does not exceed the depth of the brace. Initial yielding of the gusset has begun. Yielding has initiated in framing at gusset plates but no buckling has occurred. Residual buckling of the brace has occurred but is barely noticeable to the naked eye and does not exceed half the brace depth. Residual drift is slight. | Buckling of brace in excess of the brace depth. Initiation of yielding and out-of-plane deformation of the gusset. Initiation of cracking of welds of gusset. Initiation of yielding in beams and columns adjacent to gusset. | Buckling of brace in excess of 2 times brace depth. Yielding and out-of-plane deformation of gusset. Cracking and tearing of welds and gussets adjacent to welds but crack length is less than critical for fracture. Significant yielding and local buckling in beams and columns adjacent to gusset. | Fracture of brace or gusset. Buckling of gusset. Severe yielding of beams and columns adjacent to the gusset with possibility of local buckling and cracking in the yielded areas. |  | 1 | 1 | 1 | 1 |  | 0.0035 | 0.0058 | 0.0142 | 0.0283 |  | 0.38 | 0.6 | 0.45 | 0.05 |  | 0.25 | 0.25 | 0.25 | 0.25 |  | 0.45 | 0.65 | 0.5 | 0.25 |  | NO | YES | Superior | Superior | Average | Superior | Brace damage is largely aesthetic. Heat straightening may be desirable but replacement would be for aesthetic reasons. Gusset has minor loss of strength and stiffness and straightening or repair may be desirable aesthetic reasons. | Brace has lost significant axial capacity, and replacement of braces is likely required. The gusset plate may have significant deformation and replacement may also be needed. Local beam and column yielding has occurred and straightening may be desirable for aesthetic reasons. | Brace and gusset are severely damaged with significant loss in stiffness and resistance, and both likely require replacement. Yielding and local buckling of beams and columns may be repaired by heat straightening, stiffeners or reinforcement, if there is no cracking or tearing. If cracking or tearing has initiated more substantial repair is needed | Brace and or gusset have fractured and require replacement. Yielding and local buckling of beams and columns may be repaired by heat straightening, stiffeners or reinforcement, if there is no cracking or tearing. If cracking or tearing has initiated more substantial repair is needed |  | NO | NO | NO | NO |  | NO | NO | NO | NO |  | Not Applicable | Not Applicable | Not Applicable | Not Applicable |  | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 |  |  | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 |  |  | NO | YES | YES | YES |  | 0% | 60% | 40% | 20% |  | 0 | 0.5 | 0.5 | 0.5 |  | None | Not Given | By User | By User | Not Given | none | B1033.001a-DS2-1.JPG | B1033.001a-DS3-1.JPG | B1033.001a-DS4-1.JPG |  | No | 2011-08-24 Negative probability below 0.5% drift - overlap deemed acceptable. 2016-08-17 time consequence adjusted to avoid decreasing consequence with increasing member weight. | YES
B1033.011a | B1033.011a | Special Concentric Braced Frame w HSS braces, balanced design criteria, Chevron Brace, Brace w < 40 PLF | Costing is on a per bay basis. Costing does not include fireproofing removal or reapplication cost. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 4 | DS1 | DS2 | DS3 | DS4 |  | Sequential | Sequential | Sequential | Sequential |  | Seq(DS1,DS2,DS3,DS4) | 17 | EA 1 | YES | NO | Buckling of the brace has begun but does not exceed the depth of the brace. Initial yielding of the gusset has begun. Yielding has initiated in framing at gusset plates but no buckling has occurred. Residual buckling of the brace has occurred but is barely noticeable to the naked eye and does not exceed half the brace depth. Residual drift is slight. | Buckling of brace in excess of the brace depth. Initiation of yielding and out-of-plane deformation of the gusset. Initiation of cracking of welds of gusset. Initiation of yielding in beams and columns adjacent to gusset. | Buckling of brace in excess of 2 times brace depth. Yielding and out-of-plane deformation of gusset. Cracking and tearing of welds and gussets adjacent to welds but crack length is less than critical for fracture. Significant yielding and local buckling in beams and columns adjacent to gusset. | Fracture of brace or gusset. Buckling of gusset. Severe yielding of beams and columns adjacent to the gusset with possibility of local buckling and cracking in the yielded areas. |  | 1 | 1 | 1 | 1 |  | 0.0035 | 0.0092 | 0.0167 | 0.0223 |  | 0.38 | 0.3 | 0.1 | 0.1 |  | 0.25 | 0.1 | 0.1 | 0.1 |  | 0.45 | 0.3 | 0.15 | 0.15 |  | NO | YES | Superior | Superior | Superior | Superior | Brace damage is largely aesthetic. Heat straightening may be desirable but replacement would be for aesthetic reasons. Gusset has minor loss of strength and stiffness and straightening or repair may be desirable aesthetic reasons. | Brace has lost significant axial capacity, and replacement of braces is likely required. The gusset plate may have significant deformation and replacement may also be needed. Local beam and column yielding has occurred and straightening may be desirable for aesthetic reasons. | Brace and gusset are severely damaged with significant loss in stiffness and resistance, and both likely require replacement. Yielding and local buckling of beams and columns may be repaired by heat straightening, stiffeners or reinforcement, if there is no cracking or tearing. If cracking or tearing has initiated more substantial repair is needed | Brace and or gusset have fractured and require replacement. Yielding and local buckling of beams and columns may be repaired by heat straightening, stiffeners or reinforcement, if there is no cracking or tearing. If cracking or tearing has initiated more substantial repair is needed |  | NO | NO | NO | NO |  | NO | NO | NO | NO |  | Not Applicable | Not Applicable | Not Applicable | Not Applicable |  | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 |  |  | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 |  |  | NO | YES | YES | YES |  | 60% | 40% | 20% | 20% |  | 0.5 | 0.5 | 0.5 | 0.5 |  | None | Not Given | By User | By User | Not Given | none | B1033.001a-DS2-1.JPG | B1033.001a-DS3-1.JPG | B1033.011a-DS3-2.JPG |  | No | 2016-08-17 time consequence adjusted to avoid decreasing consequence with increasing member weight. | YES
B1033.011b | B1033.011b | Special Concentric Braced Frame w HSS braces, balanced design criteria, Chevron Brace, Brace 41 PLF < w < 99 PLF | Costing is on a per bay basis. Costing does not include fireproofing removal or reapplication cost. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 4 | DS1 | DS2 | DS3 | DS4 |  | Sequential | Sequential | Sequential | Sequential |  | Seq(DS1,DS2,DS3,DS4) | 18 | EA 1 | YES | NO | Buckling of the brace has begun but does not exceed the depth of the brace. Initial yielding of the gusset has begun. Yielding has initiated in framing at gusset plates but no buckling has occurred. Residual buckling of the brace has occurred but is barely noticeable to the naked eye and does not exceed half the brace depth. Residual drift is slight. | Buckling of brace in excess of the brace depth. Initiation of yielding and out-of-plane deformation of the gusset. Initiation of cracking of welds of gusset. Initiation of yielding in beams and columns adjacent to gusset. | Buckling of brace in excess of 2 times brace depth. Yielding and out-of-plane deformation of gusset. Cracking and tearing of welds and gussets adjacent to welds but crack length is less than critical for fracture. Significant yielding and local buckling in beams and columns adjacent to gusset. | Fracture of brace or gusset. Buckling of gusset. Severe yielding of beams and columns adjacent to the gusset with possibility of local buckling and cracking in the yielded areas. |  | 1 | 1 | 1 | 1 |  | 0.0035 | 0.0092 | 0.0167 | 0.0223 |  | 0.38 | 0.3 | 0.1 | 0.1 |  | 0.25 | 0.1 | 0.1 | 0.1 |  | 0.45 | 0.3 | 0.15 | 0.15 |  | NO | YES | Superior | Superior | Superior | Superior | Brace damage is largely aesthetic. Heat straightening may be desirable but replacement would be for aesthetic reasons. Gusset has minor loss of strength and stiffness and straightening or repair may be desirable aesthetic reasons. | Brace has lost significant axial capacity, and replacement of braces is likely required. The gusset plate may have significant deformation and replacement may also be needed. Local beam and column yielding has occurred and straightening may be desirable for aesthetic reasons. | Brace and gusset are severely damaged with significant loss in stiffness and resistance, and both likely require replacement. Yielding and local buckling of beams and columns may be repaired by heat straightening, stiffeners or reinforcement, if there is no cracking or tearing. If cracking or tearing has initiated more substantial repair is needed | Brace and or gusset have fractured and require replacement. Yielding and local buckling of beams and columns may be repaired by heat straightening, stiffeners or reinforcement, if there is no cracking or tearing. If cracking or tearing has initiated more substantial repair is needed |  | NO | NO | NO | NO |  | NO | NO | NO | NO |  | Not Applicable | Not Applicable | Not Applicable | Not Applicable |  | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 |  |  | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 |  |  | NO | YES | YES | YES |  | 60% | 40% | 20% | 20% |  | 0.5 | 0.5 | 0.5 | 0.5 |  | None | Not Given | By User | By User | Not Given | none | B1033.001a-DS2-1.JPG | B1033.001a-DS3-1.JPG | B1033.011a-DS3-2.JPG |  | No | 2016-08-17 time consequence adjusted to avoid decreasing consequence with increasing member weight. | YES
B1033.011c | B1033.011c | Special Concentric Braced Frame w HSS braces, balanced design criteria, Chevron Brace, Brace w > 100 PLF | Costing is on a per bay basis. Costing does not include fireproofing removal or reapplication cost. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 4 | DS1 | DS2 | DS3 | DS4 |  | Sequential | Sequential | Sequential | Sequential |  | Seq(DS1,DS2,DS3,DS4) | 19 | EA 1 | YES | NO | Buckling of the brace has begun but does not exceed the depth of the brace. Initial yielding of the gusset has begun. Yielding has initiated in framing at gusset plates but no buckling has occurred. Residual buckling of the brace has occurred but is barely noticeable to the naked eye and does not exceed half the brace depth. Residual drift is slight. | Buckling of brace in excess of the brace depth. Initiation of yielding and out-of-plane deformation of the gusset. Initiation of cracking of welds of gusset. Initiation of yielding in beams and columns adjacent to gusset. | Buckling of brace in excess of 2 times brace depth. Yielding and out-of-plane deformation of gusset. Cracking and tearing of welds and gussets adjacent to welds but crack length is less than critical for fracture. Significant yielding and local buckling in beams and columns adjacent to gusset. | Fracture of brace or gusset. Buckling of gusset. Severe yielding of beams and columns adjacent to the gusset with possibility of local buckling and cracking in the yielded areas. |  | 1 | 1 | 1 | 1 |  | 0.0035 | 0.0092 | 0.0167 | 0.0223 |  | 0.38 | 0.3 | 0.1 | 0.1 |  | 0.25 | 0.1 | 0.1 | 0.1 |  | 0.45 | 0.3 | 0.15 | 0.15 |  | NO | YES | Superior | Superior | Superior | Superior | Brace damage is largely aesthetic. Heat straightening may be desirable but replacement would be for aesthetic reasons. Gusset has minor loss of strength and stiffness and straightening or repair may be desirable aesthetic reasons. | Brace has lost significant axial capacity, and replacement of braces is likely required. The gusset plate may have significant deformation and replacement may also be needed. Local beam and column yielding has occurred and straightening may be desirable for aesthetic reasons. | Brace and gusset are severely damaged with significant loss in stiffness and resistance, and both likely require replacement. Yielding and local buckling of beams and columns may be repaired by heat straightening, stiffeners or reinforcement, if there is no cracking or tearing. If cracking or tearing has initiated more substantial repair is needed | Brace and or gusset have fractured and require replacement. Yielding and local buckling of beams and columns may be repaired by heat straightening, stiffeners or reinforcement, if there is no cracking or tearing. If cracking or tearing has initiated more substantial repair is needed |  | NO | NO | NO | NO |  | NO | NO | NO | NO |  | Not Applicable | Not Applicable | Not Applicable | Not Applicable |  | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 |  |  | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 |  |  | NO | YES | YES | YES |  | 60% | 40% | 20% | 20% |  | 0.5 | 0.5 | 0.5 | 0.5 |  | None | Not Given | By User | By User | Not Given | none | B1033.001a-DS2-1.JPG | B1033.001a-DS3-1.JPG | B1033.011a-DS3-2.JPG |  | No | 2016-08-17 time consequence adjusted to avoid decreasing consequence with increasing member weight. | YES
B1033.012a | B1033.012a | Special Concentric Braced Frame w HSS braces, balanced design criteria, Single Diagonal Brace, Brace w < 40 PLF | Costing is on a per bay basis. Costing does not include fireproofing removal or reapplication cost. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 4 | DS1 | DS2 | DS3 | DS4 |  | Sequential | Sequential | Sequential | Sequential |  | Seq(DS1,DS2,DS3,DS4) | 20 | EA 1 | YES | NO | Buckling of the brace has begun but does not exceed the depth of the brace. Initial yielding of the gusset has begun. Yielding has initiated in framing at gusset plates but no buckling has occurred. Residual buckling of the brace has occurred but is barely noticeable to the naked eye and does not exceed half the brace depth. Residual drift is slight. | Buckling of brace in excess of the brace depth. Initiation of yielding and out-of-plane deformation of the gusset. Initiation of cracking of welds of gusset. Initiation of yielding in beams and columns adjacent to gusset. | Buckling of brace in excess of 2 times brace depth. Yielding and out-of-plane deformation of gusset. Cracking and tearing of welds and gussets adjacent to welds but crack length is less than critical for fracture. Significant yielding and local buckling in beams and columns adjacent to gusset. | Fracture of brace or gusset. Buckling of gusset. Severe yielding of beams and columns adjacent to the gusset with possibility of local buckling and cracking in the yielded areas. |  | 1 | 1 | 1 | 1 |  | 0.0035 | 0.0092 | 0.0167 | 0.0223 |  | 0.38 | 0.3 | 0.1 | 0.1 |  | 0.25 | 0.1 | 0.1 | 0.1 |  | 0.45 | 0.3 | 0.15 | 0.15 |  | NO | YES | Superior | Superior | Superior | Superior | Brace damage is largely aesthetic. Heat straightening may be desirable but replacement would be for aesthetic reasons. Gusset has minor loss of strength and stiffness and straightening or repair may be desirable aesthetic reasons. | Brace has lost significant axial capacity, and replacement of braces is likely required. The gusset plate may have significant deformation and replacement may also be needed. Local beam and column yielding has occurred and straightening may be desirable for aesthetic reasons. | Brace and gusset are severely damaged with significant loss in stiffness and resistance, and both likely require replacement. Yielding and local buckling of beams and columns may be repaired by heat straightening, stiffeners or reinforcement, if there is no cracking or tearing. If cracking or tearing has initiated more substantial repair is needed | Brace and or gusset have fractured and require replacement. Yielding and local buckling of beams and columns may be repaired by heat straightening, stiffeners or reinforcement, if there is no cracking or tearing. If cracking or tearing has initiated more substantial repair is needed |  | NO | NO | NO | NO |  | NO | NO | NO | NO |  | Not Applicable | Not Applicable | Not Applicable | Not Applicable |  | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 |  |  | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 |  |  | NO | YES | YES | YES |  | 60% | 40% | 20% | 20% |  | 0.5 | 0.5 | 0.5 | 0.5 |  | None | Not Given | By User | By User | Not Given | none | B1033.001a-DS2-1.JPG | B1033.001a-DS3-1.JPG | B1033.011a-DS3-2.JPG |  | No | 2016-08-17 time consequence adjusted to avoid decreasing consequence with increasing member weight. | YES
B1033.012b | B1033.012b | Special Concentric Braced Frame w HSS braces, balanced design criteria, Single Diagonal Brace, Brace 41 PLF < w < 99 PLF | Costing is on a per bay basis. Costing does not include fireproofing removal or reapplication cost. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 4 | DS1 | DS2 | DS3 | DS4 |  | Sequential | Sequential | Sequential | Sequential |  | Seq(DS1,DS2,DS3,DS4) | 21 | EA 1 | YES | NO | Buckling of the brace has begun but does not exceed the depth of the brace. Initial yielding of the gusset has begun. Yielding has initiated in framing at gusset plates but no buckling has occurred. Residual buckling of the brace has occurred but is barely noticeable to the naked eye and does not exceed half the brace depth. Residual drift is slight. | Buckling of brace in excess of the brace depth. Initiation of yielding and out-of-plane deformation of the gusset. Initiation of cracking of welds of gusset. Initiation of yielding in beams and columns adjacent to gusset. | Buckling of brace in excess of 2 times brace depth. Yielding and out-of-plane deformation of gusset. Cracking and tearing of welds and gussets adjacent to welds but crack length is less than critical for fracture. Significant yielding and local buckling in beams and columns adjacent to gusset. | Fracture of brace or gusset. Buckling of gusset. Severe yielding of beams and columns adjacent to the gusset with possibility of local buckling and cracking in the yielded areas. |  | 1 | 1 | 1 | 1 |  | 0.0035 | 0.0092 | 0.0167 | 0.0223 |  | 0.38 | 0.3 | 0.1 | 0.1 |  | 0.25 | 0.1 | 0.1 | 0.1 |  | 0.45 | 0.3 | 0.15 | 0.15 |  | NO | YES | Superior | Superior | Superior | Superior | Brace damage is largely aesthetic. Heat straightening may be desirable but replacement would be for aesthetic reasons. Gusset has minor loss of strength and stiffness and straightening or repair may be desirable aesthetic reasons. | Brace has lost significant axial capacity, and replacement of braces is likely required. The gusset plate may have significant deformation and replacement may also be needed. Local beam and column yielding has occurred and straightening may be desirable for aesthetic reasons. | Brace and gusset are severely damaged with significant loss in stiffness and resistance, and both likely require replacement. Yielding and local buckling of beams and columns may be repaired by heat straightening, stiffeners or reinforcement, if there is no cracking or tearing. If cracking or tearing has initiated more substantial repair is needed | Brace and or gusset have fractured and require replacement. Yielding and local buckling of beams and columns may be repaired by heat straightening, stiffeners or reinforcement, if there is no cracking or tearing. If cracking or tearing has initiated more substantial repair is needed |  | NO | NO | NO | NO |  | NO | NO | NO | NO |  | Not Applicable | Not Applicable | Not Applicable | Not Applicable |  | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 |  |  | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 |  |  | NO | YES | YES | YES |  | 60% | 40% | 20% | 20% |  | 0.5 | 0.5 | 0.5 | 0.5 |  | None | Not Given | By User | By User | Not Given | none | B1033.001a-DS2-1.JPG | B1033.001a-DS3-1.JPG | B1033.011a-DS3-2.JPG |  | No | 2016-08-17 time consequence adjusted to avoid decreasing consequence with increasing member weight. | YES
B1033.012c | B1033.012c | Special Concentric Braced Frame w HSS braces, balanced design criteria, Single Diagonal Brace, Brace w > 100 PLF | Costing is on a per bay basis. Costing does not include fireproofing removal or reapplication cost. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 4 | DS1 | DS2 | DS3 | DS4 |  | Sequential | Sequential | Sequential | Sequential |  | Seq(DS1,DS2,DS3,DS4) | 22 | EA 1 | YES | NO | Buckling of the brace has begun but does not exceed the depth of the brace. Initial yielding of the gusset has begun. Yielding has initiated in framing at gusset plates but no buckling has occurred. Residual buckling of the brace has occurred but is barely noticeable to the naked eye and does not exceed half the brace depth. Residual drift is slight. | Buckling of brace in excess of the brace depth. Initiation of yielding and out-of-plane deformation of the gusset. Initiation of cracking of welds of gusset. Initiation of yielding in beams and columns adjacent to gusset. | Buckling of brace in excess of 2 times brace depth. Yielding and out-of-plane deformation of gusset. Cracking and tearing of welds and gussets adjacent to welds but crack length is less than critical for fracture. Significant yielding and local buckling in beams and columns adjacent to gusset. | Fracture of brace or gusset. Buckling of gusset. Severe yielding of beams and columns adjacent to the gusset with possibility of local buckling and cracking in the yielded areas. |  | 1 | 1 | 1 | 1 |  | 0.0035 | 0.0092 | 0.0167 | 0.0223 |  | 0.38 | 0.3 | 0.1 | 0.1 |  | 0.25 | 0.1 | 0.1 | 0.1 |  | 0.45 | 0.3 | 0.15 | 0.15 |  | NO | YES | Superior | Superior | Superior | Superior | Brace damage is largely aesthetic. Heat straightening may be desirable but replacement would be for aesthetic reasons. Gusset has minor loss of strength and stiffness and straightening or repair may be desirable aesthetic reasons. | Brace has lost significant axial capacity, and replacement of braces is likely required. The gusset plate may have significant deformation and replacement may also be needed. Local beam and column yielding has occurred and straightening may be desirable for aesthetic reasons. | Brace and gusset are severely damaged with significant loss in stiffness and resistance, and both likely require replacement. Yielding and local buckling of beams and columns may be repaired by heat straightening, stiffeners or reinforcement, if there is no cracking or tearing. If cracking or tearing has initiated more substantial repair is needed | Brace and or gusset have fractured and require replacement. Yielding and local buckling of beams and columns may be repaired by heat straightening, stiffeners or reinforcement, if there is no cracking or tearing. If cracking or tearing has initiated more substantial repair is needed |  | NO | NO | NO | NO |  | NO | NO | NO | NO |  | Not Applicable | Not Applicable | Not Applicable | Not Applicable |  | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 |  |  | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 |  |  | NO | YES | YES | YES |  | 60% | 40% | 20% | 20% |  | 0.5 | 0.5 | 0.5 | 0.5 |  | None | Not Given | By User | By User | Not Given | none | B1033.001a-DS2-1.JPG | B1033.001a-DS3-1.JPG | B1033.011a-DS3-2.JPG |  | No | 2016-08-17 time consequence adjusted to avoid decreasing consequence with increasing member weight. | YES
B1033.013a | B1033.013a | Special Concentric Braced Frame w HSS braces, balanced design criteria, X Brace, Brace w < 40 PLF | Costing is on a per bay basis. Costing does not include fireproofing removal or reapplication cost. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 4 | DS1 | DS2 | DS3 | DS4 |  | Sequential | Sequential | Sequential | Sequential |  | Seq(DS1,DS2,DS3,DS4) | 23 | EA 1 | YES | NO | Buckling of the brace has begun but does not exceed the depth of the brace. Initial yielding of the gusset has begun. Yielding has initiated in framing at gusset plates but no buckling has occurred. Residual buckling of the brace has occurred but is barely noticeable to the naked eye and does not exceed half the brace depth. Residual drift is slight. | Buckling of brace in excess of the brace depth. Initiation of yielding and out-of-plane deformation of the gusset. Initiation of cracking of welds of gusset. Initiation of yielding in beams and columns adjacent to gusset. | Buckling of brace in excess of 2 times brace depth. Yielding and out-of-plane deformation of gusset. Cracking and tearing of welds and gussets adjacent to welds but crack length is less than critical for fracture. Significant yielding and local buckling in beams and columns adjacent to gusset. | Fracture of brace or gusset. Buckling of gusset. Severe yielding of beams and columns adjacent to the gusset with possibility of local buckling and cracking in the yielded areas. |  | 1 | 1 | 1 | 1 |  | 0.0035 | 0.0092 | 0.0167 | 0.0223 |  | 0.38 | 0.3 | 0.1 | 0.1 |  | 0.25 | 0.1 | 0.1 | 0.1 |  | 0.45 | 0.3 | 0.15 | 0.15 |  | NO | YES | Superior | Superior | Superior | Superior | Brace damage is largely aesthetic. Heat straightening may be desirable but replacement would be for aesthetic reasons. Gusset has minor loss of strength and stiffness and straightening or repair may be desirable aesthetic reasons. | Brace has lost significant axial capacity, and replacement of braces is likely required. The gusset plate may have significant deformation and replacement may also be needed. Local beam and column yielding has occurred and straightening may be desirable for aesthetic reasons. | Brace and gusset are severely damaged with significant loss in stiffness and resistance, and both likely require replacement. Yielding and local buckling of beams and columns may be repaired by heat straightening, stiffeners or reinforcement, if there is no cracking or tearing. If cracking or tearing has initiated more substantial repair is needed | Brace and or gusset have fractured and require replacement. Yielding and local buckling of beams and columns may be repaired by heat straightening, stiffeners or reinforcement, if there is no cracking or tearing. If cracking or tearing has initiated more substantial repair is needed |  | NO | NO | NO | NO |  | NO | NO | NO | NO |  | Not Applicable | Not Applicable | Not Applicable | Not Applicable |  | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 |  |  | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 |  |  | NO | YES | YES | YES |  | 60% | 40% | 20% | 20% |  | 0.5 | 0.5 | 0.5 | 0.5 |  | None | Not Given | By User | By User | Not Given | none | B1033.001a-DS2-1.JPG | B1033.001a-DS3-1.JPG | B1033.011a-DS3-2.JPG |  | No | 2016-08-17 time consequence adjusted to avoid decreasing consequence with increasing member weight. | YES
B1033.013b | B1033.013b | Special Concentric Braced Frame w HSS braces, balanced design criteria, X Brace, Brace 41 PLF < w < 99 PLF | Costing is on a per bay basis. Costing does not include fireproofing removal or reapplication cost. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 4 | DS1 | DS2 | DS3 | DS4 |  | Sequential | Sequential | Sequential | Sequential |  | Seq(DS1,DS2,DS3,DS4) | 24 | EA 1 | YES | NO | Buckling of the brace has begun but does not exceed the depth of the brace. Initial yielding of the gusset has begun. Yielding has initiated in framing at gusset plates but no buckling has occurred. Residual buckling of the brace has occurred but is barely noticeable to the naked eye and does not exceed half the brace depth. Residual drift is slight. | Buckling of brace in excess of the brace depth. Initiation of yielding and out-of-plane deformation of the gusset. Initiation of cracking of welds of gusset. Initiation of yielding in beams and columns adjacent to gusset. | Buckling of brace in excess of 2 times brace depth. Yielding and out-of-plane deformation of gusset. Cracking and tearing of welds and gussets adjacent to welds but crack length is less than critical for fracture. Significant yielding and local buckling in beams and columns adjacent to gusset. | Fracture of brace or gusset. Buckling of gusset. Severe yielding of beams and columns adjacent to the gusset with possibility of local buckling and cracking in the yielded areas. |  | 1 | 1 | 1 | 1 |  | 0.0035 | 0.0092 | 0.0167 | 0.0223 |  | 0.38 | 0.3 | 0.1 | 0.1 |  | 0.25 | 0.1 | 0.1 | 0.1 |  | 0.45 | 0.3 | 0.15 | 0.15 |  | NO | YES | Superior | Superior | Superior | Superior | Brace damage is largely aesthetic. Heat straightening may be desirable but replacement would be for aesthetic reasons. Gusset has minor loss of strength and stiffness and straightening or repair may be desirable aesthetic reasons. | Brace has lost significant axial capacity, and replacement of braces is likely required. The gusset plate may have significant deformation and replacement may also be needed. Local beam and column yielding has occurred and straightening may be desirable for aesthetic reasons. | Brace and gusset are severely damaged with significant loss in stiffness and resistance, and both likely require replacement. Yielding and local buckling of beams and columns may be repaired by heat straightening, stiffeners or reinforcement, if there is no cracking or tearing. If cracking or tearing has initiated more substantial repair is needed | Brace and or gusset have fractured and require replacement. Yielding and local buckling of beams and columns may be repaired by heat straightening, stiffeners or reinforcement, if there is no cracking or tearing. If cracking or tearing has initiated more substantial repair is needed |  | NO | NO | NO | NO |  | NO | NO | NO | NO |  | Not Applicable | Not Applicable | Not Applicable | Not Applicable |  | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 |  |  | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 |  |  | NO | YES | YES | YES |  | 60% | 40% | 20% | 20% |  | 0.5 | 0.5 | 0.5 | 0.5 |  | None | Not Given | By User | By User | Not Given | none | B1033.001a-DS2-1.JPG | B1033.001a-DS3-1.JPG | B1033.011a-DS3-2.JPG |  | No | 2016-08-17 time consequence adjusted to avoid decreasing consequence with increasing member weight. | YES
B1033.013c | B1033.013c | Special Concentric Braced Frame w HSS braces, balanced design criteria, X Brace, Brace w > 100 PLF | Costing is on a per bay basis. Costing does not include fireproofing removal or reapplication cost. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 4 | DS1 | DS2 | DS3 | DS4 |  | Sequential | Sequential | Sequential | Sequential |  | Seq(DS1,DS2,DS3,DS4) | 25 | EA 1 | YES | NO | Buckling of the brace has begun but does not exceed the depth of the brace. Initial yielding of the gusset has begun. Yielding has initiated in framing at gusset plates but no buckling has occurred. Residual buckling of the brace has occurred but is barely noticeable to the naked eye and does not exceed half the brace depth. Residual drift is slight. | Buckling of brace in excess of the brace depth. Initiation of yielding and out-of-plane deformation of the gusset. Initiation of cracking of welds of gusset. Initiation of yielding in beams and columns adjacent to gusset. | Buckling of brace in excess of 2 times brace depth. Yielding and out-of-plane deformation of gusset. Cracking and tearing of welds and gussets adjacent to welds but crack length is less than critical for fracture. Significant yielding and local buckling in beams and columns adjacent to gusset. | Fracture of brace or gusset. Buckling of gusset. Severe yielding of beams and columns adjacent to the gusset with possibility of local buckling and cracking in the yielded areas. |  | 1 | 1 | 1 | 1 |  | 0.0035 | 0.0092 | 0.0167 | 0.0223 |  | 0.38 | 0.3 | 0.1 | 0.1 |  | 0.25 | 0.1 | 0.1 | 0.1 |  | 0.45 | 0.3 | 0.15 | 0.15 |  | NO | YES | Superior | Superior | Superior | Superior | Brace damage is largely aesthetic. Heat straightening may be desirable but replacement would be for aesthetic reasons. Gusset has minor loss of strength and stiffness and straightening or repair may be desirable aesthetic reasons. | Brace has lost significant axial capacity, and replacement of braces is likely required. The gusset plate may have significant deformation and replacement may also be needed. Local beam and column yielding has occurred and straightening may be desirable for aesthetic reasons. | Brace and gusset are severely damaged with significant loss in stiffness and resistance, and both likely require replacement. Yielding and local buckling of beams and columns may be repaired by heat straightening, stiffeners or reinforcement, if there is no cracking or tearing. If cracking or tearing has initiated more substantial repair is needed | Brace and or gusset have fractured and require replacement. Yielding and local buckling of beams and columns may be repaired by heat straightening, stiffeners or reinforcement, if there is no cracking or tearing. If cracking or tearing has initiated more substantial repair is needed |  | NO | NO | NO | NO |  | NO | NO | NO | NO |  | Not Applicable | Not Applicable | Not Applicable | Not Applicable |  | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 |  |  | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 |  |  | NO | YES | YES | YES |  | 60% | 40% | 20% | 20% |  | 0.5 | 0.5 | 0.5 | 0.5 |  | None | Not Given | By User | By User | Not Given | none | B1033.001a-DS2-1.JPG | B1033.001a-DS3-1.JPG | B1033.011a-DS3-2.JPG |  | No | 2016-08-17 time consequence adjusted to avoid decreasing consequence with increasing member weight. | YES
B1033.021a | B1033.021a | Special Concentric Braced Frame w HSS braces, tapered gusset plates & design to AISC minimum standard, Chevron Brace, Brace w < 40 PLF | Costing is on a per bay basis. Costing does not include fireproofing removal or reapplication cost. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 4 | DS1 | DS2 | DS3 | DS4 |  | Sequential | Sequential | Sequential | Sequential |  | Seq(DS1,DS2,DS3,DS4) | 26 | EA 1 | YES | NO | Buckling of the brace has begun but does not exceed the depth of the brace. Initial yielding of the gusset has begun. Yielding has initiated in framing at gusset plates but no buckling has occurred. Residual buckling of the brace has occurred but is barely noticeable to the naked eye and does not exceed half the brace depth. Residual drift is slight. | Buckling of brace in excess of the brace depth. Initiation of yielding and out-of-plane deformation of the gusset. Initiation of cracking of welds of gusset. Initiation of yielding in beams and columns adjacent to gusset. | Buckling of brace in excess of 2 time brace depth . Yielding and out-of-plane deformation of gusset . Cracking and tearing of welds and gussets adjacent to welds but crack length is less than critical for fracture . Significant yielding and local buckling in beams and columns adjacent to gusset . | Fracture of brace or gusset. Buckling of gusset. Severe yielding of beams and columns adjacent to the gusset with possibility of local buckling and cracking in the yielded areas. |  | 1 | 1 | 1 | 1 |  | 0.0037 | 0.0075 | 0.0145 | 0.0199 |  | 0.26 | 0.25 | 0.2 | 0.35 |  | 0.1 | 0.1 | 0.1 | 0.1 |  | 0.3 | 0.25 | 0.25 | 0.35 |  | NO | YES | Superior | Superior | Average | Superior | Brace damage is largely aesthetic. Heat straightening may be desirable but replacement would be for aesthetic reasons. Gusset has minor loss of strength and stiffness and straightening or repair may be desirable aesthetic reasons. | Brace has lost significant axial capacity, and replacement of braces is likely required. Tapered gusset plates typically sustain greater damage and there is a higher probability that replacement will be needed. Local beam and column yielding has occurred and straightening may be desirable for aesthetic reasons. | Brace and gusset are severely damaged with significant loss in stiffness and resistance, and both likely require replacement. Yielding and local buckling of beams and columns may be repaired by heat straightening, stiffeners or reinforcement, if there is no cracking or tearing. If cracking or tearing has initiated more substantial repair is needed | Brace and or gusset have fractured and require replacement. Yielding and local buckling of beams and columns may be repaired by heat straightening, stiffeners or reinforcement, if there is no cracking or tearing. If cracking or tearing has initiated more substantial repair is needed |  | NO | NO | NO | NO |  | NO | NO | NO | NO |  | Not Applicable | Not Applicable | Not Applicable | Not Applicable |  | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 |  |  | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 |  |  | NO | YES | YES | YES |  | 0% | 60% | 40% | 20% |  | 0 | 0.5 | 0.5 | 0.5 |  | None | Not Given | By User | By User | Not Given | none | B1033.001a-DS2-1.JPG | B1033.001a-DS3-1.JPG | B1033.011a-DS3-2.JPG |  | No | 2011-08-24 Negative probability below 0.5% drift - overlap deemed acceptable. 2016-08-17 time consequence adjusted to avoid decreasing consequence with increasing member weight. | YES
B1033.021b | B1033.021b | Special Concentric Braced Frame w HSS braces, tapered gusset plates & design to AISC minimum standard, Chevron Brace, Brace 41 PLF < w < 99 PLF | Costing is on a per bay basis. Costing does not include fireproofing removal or reapplication cost. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 4 | DS1 | DS2 | DS3 | DS4 |  | Sequential | Sequential | Sequential | Sequential |  | Seq(DS1,DS2,DS3,DS4) | 27 | EA 1 | YES | NO | Buckling of the brace has begun but does not exceed the depth of the brace. Initial yielding of the gusset has begun. Yielding has initiated in framing at gusset plates but no buckling has occurred. Residual buckling of the brace has occurred but is barely noticeable to the naked eye and does not exceed half the brace depth. Residual drift is slight. | Buckling of brace in excess of the brace depth. Initiation of yielding and out-of-plane deformation of the gusset. Initiation of cracking of welds of gusset. Initiation of yielding in beams and columns adjacent to gusset. | Buckling of brace in excess of 2 time brace depth . Yielding and out-of-plane deformation of gusset . Cracking and tearing of welds and gussets adjacent to welds but crack length is less than critical for fracture . Significant yielding and local buckling in beams and columns adjacent to gusset . | Fracture of brace or gusset. Buckling of gusset. Severe yielding of beams and columns adjacent to the gusset with possibility of local buckling and cracking in the yielded areas. |  | 1 | 1 | 1 | 1 |  | 0.0037 | 0.0075 | 0.0145 | 0.0199 |  | 0.26 | 0.25 | 0.2 | 0.35 |  | 0.1 | 0.1 | 0.1 | 0.1 |  | 0.3 | 0.25 | 0.25 | 0.35 |  | NO | YES | Superior | Superior | Average | Superior | Brace damage is largely aesthetic. Heat straightening may be desirable but replacement would be for aesthetic reasons. Gusset has minor loss of strength and stiffness and straightening or repair may be desirable aesthetic reasons. | Brace has lost significant axial capacity, and replacement of braces is likely required. Tapered gusset plates typically sustain greater damage and there is a higher probability that replacement will be needed. Local beam and column yielding has occurred and straightening may be desirable for aesthetic reasons. | Brace and gusset are severely damaged with significant loss in stiffness and resistance, and both likely require replacement. Yielding and local buckling of beams and columns may be repaired by heat straightening, stiffeners or reinforcement, if there is no cracking or tearing. If cracking or tearing has initiated more substantial repair is needed | Brace and or gusset have fractured and require replacement. Yielding and local buckling of beams and columns may be repaired by heat straightening, stiffeners or reinforcement, if there is no cracking or tearing. If cracking or tearing has initiated more substantial repair is needed |  | NO | NO | NO | NO |  | NO | NO | NO | NO |  | Not Applicable | Not Applicable | Not Applicable | Not Applicable |  | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 |  |  | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 |  |  | NO | YES | YES | YES |  | 0% | 60% | 40% | 20% |  | 0 | 0.5 | 0.5 | 0.5 |  | None | Not Given | By User | By User | Not Given | none | B1033.001a-DS2-1.JPG | B1033.001a-DS3-1.JPG | B1033.011a-DS3-2.JPG |  | No | 2011-08-24 Negative probability below 0.5% drift - overlap deemed acceptable. 2016-08-17 time consequence adjusted to avoid decreasing consequence with increasing member weight. | YES
B1033.021c | B1033.021c | Special Concentric Braced Frame w HSS braces, tapered gusset plates & design to AISC minimum standard, Chevron Brace, Brace w > 100 PLF | Costing is on a per bay basis. Costing does not include fireproofing removal or reapplication cost. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 4 | DS1 | DS2 | DS3 | DS4 |  | Sequential | Sequential | Sequential | Sequential |  | Seq(DS1,DS2,DS3,DS4) | 28 | EA 1 | YES | NO | Buckling of the brace has begun but does not exceed the depth of the brace. Initial yielding of the gusset has begun. Yielding has initiated in framing at gusset plates but no buckling has occurred. Residual buckling of the brace has occurred but is barely noticeable to the naked eye and does not exceed half the brace depth. Residual drift is slight. | Buckling of brace in excess of the brace depth. Initiation of yielding and out-of-plane deformation of the gusset. Initiation of cracking of welds of gusset. Initiation of yielding in beams and columns adjacent to gusset. | Buckling of brace in excess of 2 time brace depth . Yielding and out-of-plane deformation of gusset . Cracking and tearing of welds and gussets adjacent to welds but crack length is less than critical for fracture . Significant yielding and local buckling in beams and columns adjacent to gusset . | Fracture of brace or gusset. Buckling of gusset. Severe yielding of beams and columns adjacent to the gusset with possibility of local buckling and cracking in the yielded areas. |  | 1 | 1 | 1 | 1 |  | 0.0037 | 0.0075 | 0.0145 | 0.0199 |  | 0.26 | 0.25 | 0.2 | 0.35 |  | 0.1 | 0.1 | 0.1 | 0.1 |  | 0.3 | 0.25 | 0.25 | 0.35 |  | NO | YES | Superior | Superior | Average | Superior | Brace damage is largely aesthetic. Heat straightening may be desirable but replacement would be for aesthetic reasons. Gusset has minor loss of strength and stiffness and straightening or repair may be desirable aesthetic reasons. | Brace has lost significant axial capacity, and replacement of braces is likely required. Tapered gusset plates typically sustain greater damage and there is a higher probability that replacement will be needed. Local beam and column yielding has occurred and straightening may be desirable for aesthetic reasons. | Brace and gusset are severely damaged with significant loss in stiffness and resistance, and both likely require replacement. Yielding and local buckling of beams and columns may be repaired by heat straightening, stiffeners or reinforcement, if there is no cracking or tearing. If cracking or tearing has initiated more substantial repair is needed | Brace and or gusset have fractured and require replacement. Yielding and local buckling of beams and columns may be repaired by heat straightening, stiffeners or reinforcement, if there is no cracking or tearing. If cracking or tearing has initiated more substantial repair is needed |  | NO | NO | NO | NO |  | NO | NO | NO | NO |  | Not Applicable | Not Applicable | Not Applicable | Not Applicable |  | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 |  |  | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 |  |  | NO | YES | YES | YES |  | 0% | 60% | 40% | 20% |  | 0 | 0.5 | 0.5 | 0.5 |  | None | Not Given | By User | By User | Not Given | none | B1033.001a-DS2-1.JPG | B1033.001a-DS3-1.JPG | B1033.011a-DS3-2.JPG |  | No | 2011-08-24 Negative probability below 0.5% drift - overlap deemed acceptable. 2016-08-17 time consequence adjusted to avoid decreasing consequence with increasing member weight. | YES
B1033.022a | B1033.022a | Special Concentric Braced Frame w HSS braces, tapered gusset plates & design to AISC minimum standard Single Diagonal Brace, Brace w < 40 PLF | Costing is on a per bay basis. Costing does not include fireproofing removal or reapplication cost. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 4 | DS1 | DS2 | DS3 | DS4 |  | Sequential | Sequential | Sequential | Sequential |  | Seq(DS1,DS2,DS3,DS4) | 29 | EA 1 | YES | NO | Buckling of the brace has begun but does not exceed the depth of the brace. Initial yielding of the gusset has begun. Yielding has initiated in framing at gusset plates but no buckling has occurred. Residual buckling of the brace has occurred but is barely noticeable to the naked eye and does not exceed half the brace depth. Residual drift is slight. | Buckling of brace in excess of the brace depth. Initiation of yielding and out-of-plane deformation of the gusset. Initiation of cracking of welds of gusset. Initiation of yielding in beams and columns adjacent to gusset. | Buckling of brace in excess of 2 time brace depth . Yielding and out-of-plane deformation of gusset . Cracking and tearing of welds and gussets adjacent to welds but crack length is less than critical for fracture . Significant yielding and local buckling in beams and columns adjacent to gusset . | Fracture of brace or gusset. Buckling of gusset. Severe yielding of beams and columns adjacent to the gusset with possibility of local buckling and cracking in the yielded areas. |  | 1 | 1 | 1 | 1 |  | 0.0037 | 0.0075 | 0.0145 | 0.0199 |  | 0.26 | 0.25 | 0.2 | 0.35 |  | 0.1 | 0.1 | 0.1 | 0.1 |  | 0.3 | 0.25 | 0.25 | 0.35 |  | NO | YES | Superior | Superior | Average | Superior | Brace damage is largely aesthetic. Heat straightening may be desirable but replacement would be for aesthetic reasons. Gusset has minor loss of strength and stiffness and straightening or repair may be desirable aesthetic reasons. | Brace has lost significant axial capacity, and replacement of braces is likely required. Tapered gusset plates typically sustain greater damage and there is a higher probability that replacement will be needed. Local beam and column yielding has occurred and straightening may be desirable for aesthetic reasons. | Brace and gusset are severely damaged with significant loss in stiffness and resistance, and both likely require replacement. Yielding and local buckling of beams and columns may be repaired by heat straightening, stiffeners or reinforcement, if there is no cracking or tearing. If cracking or tearing has initiated more substantial repair is needed | Brace and or gusset have fractured and require replacement. Yielding and local buckling of beams and columns may be repaired by heat straightening, stiffeners or reinforcement, if there is no cracking or tearing. If cracking or tearing has initiated more substantial repair is needed |  | NO | NO | NO | NO |  | NO | NO | NO | NO |  | Not Applicable | Not Applicable | Not Applicable | Not Applicable |  | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 |  |  | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 |  |  | NO | YES | YES | YES |  | 0% | 60% | 40% | 20% |  | 0 | 0.5 | 0.5 | 0.5 |  | None | Not Given | By User | By User | Not Given | none | B1033.001a-DS2-1.JPG | B1033.001a-DS3-1.JPG | B1033.011a-DS3-2.JPG |  | No | 2011-08-24 Negative probability below 0.5% drift - overlap deemed acceptable. 2016-08-17 time consequence adjusted to avoid decreasing consequence with increasing member weight. | YES
B1033.022b | B1033.022b | Special Concentric Braced Frame w HSS braces, tapered gusset plates & design to AISC minimum standard, Single Diagonal Brace, Brace 41 PLF < w < 99 PLF | Costing is on a per bay basis. Costing does not include fireproofing removal or reapplication cost. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 4 | DS1 | DS2 | DS3 | DS4 |  | Sequential | Sequential | Sequential | Sequential |  | Seq(DS1,DS2,DS3,DS4) | 30 | EA 1 | YES | NO | Buckling of the brace has begun but does not exceed the depth of the brace. Initial yielding of the gusset has begun. Yielding has initiated in framing at gusset plates but no buckling has occurred. Residual buckling of the brace has occurred but is barely noticeable to the naked eye and does not exceed half the brace depth. Residual drift is slight. | Buckling of brace in excess of the brace depth. Initiation of yielding and out-of-plane deformation of the gusset. Initiation of cracking of welds of gusset. Initiation of yielding in beams and columns adjacent to gusset. | Buckling of brace in excess of 2 time brace depth . Yielding and out-of-plane deformation of gusset . Cracking and tearing of welds and gussets adjacent to welds but crack length is less than critical for fracture . Significant yielding and local buckling in beams and columns adjacent to gusset . | Fracture of brace or gusset. Buckling of gusset. Severe yielding of beams and columns adjacent to the gusset with possibility of local buckling and cracking in the yielded areas. |  | 1 | 1 | 1 | 1 |  | 0.0037 | 0.0075 | 0.0145 | 0.0199 |  | 0.26 | 0.25 | 0.2 | 0.35 |  | 0.1 | 0.1 | 0.1 | 0.1 |  | 0.3 | 0.25 | 0.25 | 0.35 |  | NO | YES | Superior | Superior | Average | Superior | Brace damage is largely aesthetic. Heat straightening may be desirable but replacement would be for aesthetic reasons. Gusset has minor loss of strength and stiffness and straightening or repair may be desirable aesthetic reasons. | Brace has lost significant axial capacity, and replacement of braces is likely required. Tapered gusset plates typically sustain greater damage and there is a higher probability that replacement will be needed. Local beam and column yielding has occurred and straightening may be desirable for aesthetic reasons. | Brace and gusset are severely damaged with significant loss in stiffness and resistance, and both likely require replacement. Yielding and local buckling of beams and columns may be repaired by heat straightening, stiffeners or reinforcement, if there is no cracking or tearing. If cracking or tearing has initiated more substantial repair is needed | Brace and or gusset have fractured and require replacement. Yielding and local buckling of beams and columns may be repaired by heat straightening, stiffeners or reinforcement, if there is no cracking or tearing. If cracking or tearing has initiated more substantial repair is needed |  | NO | NO | NO | NO |  | NO | NO | NO | NO |  | Not Applicable | Not Applicable | Not Applicable | Not Applicable |  | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 |  |  | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 |  |  | NO | YES | YES | YES |  | 0% | 60% | 40% | 20% |  | 0 | 0.5 | 0.5 | 0.5 |  | None | Not Given | By User | By User | Not Given | none | B1033.001a-DS2-1.JPG | B1033.001a-DS3-1.JPG | B1033.011a-DS3-2.JPG |  | No | 2011-08-24 Negative probability below 0.5% drift - overlap deemed acceptable. 2016-08-17 time consequence adjusted to avoid decreasing consequence with increasing member weight. | YES
B1033.022c | B1033.022c | Special Concentric Braced Frame w HSS braces, tapered gusset plates & design to AISC minimum standard, Single Diagonal Brace, Brace w > 100 PLF | Costing is on a per bay basis. Costing does not include fireproofing removal or reapplication cost. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 4 | DS1 | DS2 | DS3 | DS4 |  | Sequential | Sequential | Sequential | Sequential |  | Seq(DS1,DS2,DS3,DS4) | 31 | EA 1 | YES | NO | Buckling of the brace has begun but does not exceed the depth of the brace. Initial yielding of the gusset has begun. Yielding has initiated in framing at gusset plates but no buckling has occurred. Residual buckling of the brace has occurred but is barely noticeable to the naked eye and does not exceed half the brace depth. Residual drift is slight. | Buckling of brace in excess of the brace depth. Initiation of yielding and out-of-plane deformation of the gusset. Initiation of cracking of welds of gusset. Initiation of yielding in beams and columns adjacent to gusset. | Buckling of brace in excess of 2 time brace depth . Yielding and out-of-plane deformation of gusset . Cracking and tearing of welds and gussets adjacent to welds but crack length is less than critical for fracture . Significant yielding and local buckling in beams and columns adjacent to gusset . | Fracture of brace or gusset. Buckling of gusset. Severe yielding of beams and columns adjacent to the gusset with possibility of local buckling and cracking in the yielded areas. |  | 1 | 1 | 1 | 1 |  | 0.0037 | 0.0075 | 0.0145 | 0.0199 |  | 0.26 | 0.25 | 0.2 | 0.35 |  | 0.1 | 0.1 | 0.1 | 0.1 |  | 0.3 | 0.25 | 0.25 | 0.35 |  | NO | YES | Superior | Superior | Average | Superior | Brace damage is largely aesthetic. Heat straightening may be desirable but replacement would be for aesthetic reasons. Gusset has minor loss of strength and stiffness and straightening or repair may be desirable aesthetic reasons. | Brace has lost significant axial capacity, and replacement of braces is likely required. Tapered gusset plates typically sustain greater damage and there is a higher probability that replacement will be needed. Local beam and column yielding has occurred and straightening may be desirable for aesthetic reasons. | Brace and gusset are severely damaged with significant loss in stiffness and resistance, and both likely require replacement. Yielding and local buckling of beams and columns may be repaired by heat straightening, stiffeners or reinforcement, if there is no cracking or tearing. If cracking or tearing has initiated more substantial repair is needed | Brace and or gusset have fractured and require replacement. Yielding and local buckling of beams and columns may be repaired by heat straightening, stiffeners or reinforcement, if there is no cracking or tearing. If cracking or tearing has initiated more substantial repair is needed |  | NO | NO | NO | NO |  | NO | NO | NO | NO |  | Not Applicable | Not Applicable | Not Applicable | Not Applicable |  | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 |  |  | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 |  |  | NO | YES | YES | YES |  | 0% | 60% | 40% | 20% |  | 0 | 0.5 | 0.5 | 0.5 |  | None | Not Given | By User | By User | Not Given | none | B1033.001a-DS2-1.JPG | B1033.001a-DS3-1.JPG | B1033.011a-DS3-2.JPG |  | No | 2011-08-24 Negative probability below 0.5% drift - overlap deemed acceptable. 2016-08-17 time consequence adjusted to avoid decreasing consequence with increasing member weight. | YES
B1033.023a | B1033.023a | Special Concentric Braced Frame w HSS braces, tapered gusset plates & design to AISC minimum standard, X Brace, Brace w < 40 PLF | Costing is on a per bay basis. Costing does not include fireproofing removal or reapplication cost. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 4 | DS1 | DS2 | DS3 | DS4 |  | Sequential | Sequential | Sequential | Sequential |  | Seq(DS1,DS2,DS3,DS4) | 32 | EA 1 | YES | NO | Buckling of the brace has begun but does not exceed the depth of the brace. Initial yielding of the gusset has begun. Yielding has initiated in framing at gusset plates but no buckling has occurred. Residual buckling of the brace has occurred but is barely noticeable to the naked eye and does not exceed half the brace depth. Residual drift is slight. | Buckling of brace in excess of the brace depth. Initiation of yielding and out-of-plane deformation of the gusset. Initiation of cracking of welds of gusset. Initiation of yielding in beams and columns adjacent to gusset. | Buckling of brace in excess of 2 time brace depth . Yielding and out-of-plane deformation of gusset . Cracking and tearing of welds and gussets adjacent to welds but crack length is less than critical for fracture . Significant yielding and local buckling in beams and columns adjacent to gusset . | Fracture of brace or gusset. Buckling of gusset. Severe yielding of beams and columns adjacent to the gusset with possibility of local buckling and cracking in the yielded areas. |  | 1 | 1 | 1 | 1 |  | 0.0037 | 0.0075 | 0.0145 | 0.0199 |  | 0.26 | 0.25 | 0.2 | 0.35 |  | 0.1 | 0.1 | 0.1 | 0.1 |  | 0.3 | 0.25 | 0.25 | 0.35 |  | NO | YES | Superior | Superior | Average | Superior | Brace damage is largely aesthetic. Heat straightening may be desirable but replacement would be for aesthetic reasons. Gusset has minor loss of strength and stiffness and straightening or repair may be desirable aesthetic reasons. | Brace has lost significant axial capacity, and replacement of braces is likely required. Tapered gusset plates typically sustain greater damage and there is a higher probability that replacement will be needed. Local beam and column yielding has occurred and straightening may be desirable for aesthetic reasons. | Brace and gusset are severely damaged with significant loss in stiffness and resistance, and both likely require replacement. Yielding and local buckling of beams and columns may be repaired by heat straightening, stiffeners or reinforcement, if there is no cracking or tearing. If cracking or tearing has initiated more substantial repair is needed | Brace and or gusset have fractured and require replacement. Yielding and local buckling of beams and columns may be repaired by heat straightening, stiffeners or reinforcement, if there is no cracking or tearing. If cracking or tearing has initiated more substantial repair is needed |  | NO | NO | NO | NO |  | NO | NO | NO | NO |  | Not Applicable | Not Applicable | Not Applicable | Not Applicable |  | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 |  |  | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 |  |  | NO | YES | YES | YES |  | 0% | 60% | 40% | 20% |  | 0 | 0.5 | 0.5 | 0.5 |  | None | Not Given | By User | By User | Not Given | none | B1033.001a-DS2-1.JPG | B1033.001a-DS3-1.JPG | B1033.011a-DS3-2.JPG |  | No | 2011-08-24 Negative probability below 0.5% drift - overlap deemed acceptable. 2016-08-17 time consequence adjusted to avoid decreasing consequence with increasing member weight. | YES
B1033.023b | B1033.023b | Special Concentric Braced Frame w HSS braces, tapered gusset plates & design to AISC minimum standard, X Brace, Brace 41 PLF < w < 99 PLF | Costing is on a per bay basis. Costing does not include fireproofing removal or reapplication cost. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 4 | DS1 | DS2 | DS3 | DS4 |  | Sequential | Sequential | Sequential | Sequential |  | Seq(DS1,DS2,DS3,DS4) | 33 | EA 1 | YES | NO | Buckling of the brace has begun but does not exceed the depth of the brace. Initial yielding of the gusset has begun. Yielding has initiated in framing at gusset plates but no buckling has occurred. Residual buckling of the brace has occurred but is barely noticeable to the naked eye and does not exceed half the brace depth. Residual drift is slight. | Buckling of brace in excess of the brace depth. Initiation of yielding and out-of-plane deformation of the gusset. Initiation of cracking of welds of gusset. Initiation of yielding in beams and columns adjacent to gusset. | Buckling of brace in excess of 2 time brace depth . Yielding and out-of-plane deformation of gusset . Cracking and tearing of welds and gussets adjacent to welds but crack length is less than critical for fracture . Significant yielding and local buckling in beams and columns adjacent to gusset . | Fracture of brace or gusset. Buckling of gusset. Severe yielding of beams and columns adjacent to the gusset with possibility of local buckling and cracking in the yielded areas. |  | 1 | 1 | 1 | 1 |  | 0.0037 | 0.0075 | 0.0145 | 0.0199 |  | 0.26 | 0.25 | 0.2 | 0.35 |  | 0.1 | 0.1 | 0.1 | 0.1 |  | 0.3 | 0.25 | 0.25 | 0.35 |  | NO | YES | Superior | Superior | Average | Superior | Brace damage is largely aesthetic. Heat straightening may be desirable but replacement would be for aesthetic reasons. Gusset has minor loss of strength and stiffness and straightening or repair may be desirable aesthetic reasons. | Brace has lost significant axial capacity, and replacement of braces is likely required. Tapered gusset plates typically sustain greater damage and there is a higher probability that replacement will be needed. Local beam and column yielding has occurred and straightening may be desirable for aesthetic reasons. | Brace and gusset are severely damaged with significant loss in stiffness and resistance, and both likely require replacement. Yielding and local buckling of beams and columns may be repaired by heat straightening, stiffeners or reinforcement, if there is no cracking or tearing. If cracking or tearing has initiated more substantial repair is needed | Brace and or gusset have fractured and require replacement. Yielding and local buckling of beams and columns may be repaired by heat straightening, stiffeners or reinforcement, if there is no cracking or tearing. If cracking or tearing has initiated more substantial repair is needed |  | NO | NO | NO | NO |  | NO | NO | NO | NO |  | Not Applicable | Not Applicable | Not Applicable | Not Applicable |  | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 |  |  | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 |  |  | NO | YES | YES | YES |  | 0% | 60% | 40% | 20% |  | 0 | 0.5 | 0.5 | 0.5 |  | None | Not Given | By User | By User | Not Given | none | B1033.001a-DS2-1.JPG | B1033.001a-DS3-1.JPG | B1033.011a-DS3-2.JPG |  | No | 2011-08-24 Negative probability below 0.5% drift - overlap deemed acceptable. 2016-08-17 time consequence adjusted to avoid decreasing consequence with increasing member weight. | YES
B1033.023c | B1033.023c | Special Concentric Braced Frame w HSS braces, tapered gusset plates & design to AISC minimum standard, X Brace, Brace w > 100 PLF | Costing is on a per bay basis. Costing does not include fireproofing removal or reapplication cost. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 4 | DS1 | DS2 | DS3 | DS4 |  | Sequential | Sequential | Sequential | Sequential |  | Seq(DS1,DS2,DS3,DS4) | 34 | EA 1 | YES | NO | Buckling of the brace has begun but does not exceed the depth of the brace. Initial yielding of the gusset has begun. Yielding has initiated in framing at gusset plates but no buckling has occurred. Residual buckling of the brace has occurred but is barely noticeable to the naked eye and does not exceed half the brace depth. Residual drift is slight. | Buckling of brace in excess of the brace depth. Initiation of yielding and out-of-plane deformation of the gusset. Initiation of cracking of welds of gusset. Initiation of yielding in beams and columns adjacent to gusset. | Buckling of brace in excess of 2 time brace depth . Yielding and out-of-plane deformation of gusset . Cracking and tearing of welds and gussets adjacent to welds but crack length is less than critical for fracture . Significant yielding and local buckling in beams and columns adjacent to gusset . | Fracture of brace or gusset. Buckling of gusset. Severe yielding of beams and columns adjacent to the gusset with possibility of local buckling and cracking in the yielded areas. |  | 1 | 1 | 1 | 1 |  | 0.0037 | 0.0075 | 0.0145 | 0.0199 |  | 0.26 | 0.25 | 0.2 | 0.35 |  | 0.1 | 0.1 | 0.1 | 0.1 |  | 0.3 | 0.25 | 0.25 | 0.35 |  | NO | YES | Superior | Superior | Average | Superior | Brace damage is largely aesthetic. Heat straightening may be desirable but replacement would be for aesthetic reasons. Gusset has minor loss of strength and stiffness and straightening or repair may be desirable aesthetic reasons. | Brace has lost significant axial capacity, and replacement of braces is likely required. Tapered gusset plates typically sustain greater damage and there is a higher probability that replacement will be needed. Local beam and column yielding has occurred and straightening may be desirable for aesthetic reasons. | Brace and gusset are severely damaged with significant loss in stiffness and resistance, and both likely require replacement. Yielding and local buckling of beams and columns may be repaired by heat straightening, stiffeners or reinforcement, if there is no cracking or tearing. If cracking or tearing has initiated more substantial repair is needed | Brace and or gusset have fractured and require replacement. Yielding and local buckling of beams and columns may be repaired by heat straightening, stiffeners or reinforcement, if there is no cracking or tearing. If cracking or tearing has initiated more substantial repair is needed |  | NO | NO | NO | NO |  | NO | NO | NO | NO |  | Not Applicable | Not Applicable | Not Applicable | Not Applicable |  | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 |  |  | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 |  |  | NO | YES | YES | YES |  | 0% | 60% | 40% | 20% |  | 0 | 0.5 | 0.5 | 0.5 |  | None | Not Given | By User | By User | Not Given | none | B1033.001a-DS2-1.JPG | B1033.001a-DS3-1.JPG | B1033.011a-DS3-2.JPG |  | No | 2011-08-24 Negative probability below 0.5% drift - overlap deemed acceptable. 2016-08-17 time consequence adjusted to avoid decreasing consequence with increasing member weight. | YES
B1033.031a | B1033.031a | Special Concentric Braced Frame, design to AISC minimum standards, Chevron Brace, Brace w < 40 PLF | Costing is on a per bay basis. Costing does not include fireproofing removal or reapplication cost. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 35 | EA 1 | YES | NO | Buckling of brace in excess of the brace depth. Initiation of yielding and out-of-plane deformation of the gusset. Initiation of cracking of welds of gusset. Initiation of yielding in beams and columns adjacent to gusset. | Buckling of brace in excess of 2 time brace depth . Yielding and out-of-plane deformation of gusset . Cracking and tearing of welds and gussets adjacent to welds but crack length is less than critical for fracture . Significant yielding and local buckling in beams and columns adjacent to gusset . | Fracture of brace or gusset. Buckling of gusset. Severe yielding of beams and columns adjacent to the gusset with possibility of local buckling and cracking in the yielded areas. |  |  | 1 | 1 | 1 |  |  | 0.0074 | 0.0121 | 0.0152 |  |  | 0.3 | 0.25 | 0.35 |  |  | 0.1 | 0.1 | 0.1 |  |  | 0.3 | 0.25 | 0.35 |  |  | NO | YES | Superior | Superior | Superior | Superior | Brace has lost significant axial capacity, and replacement of braces is likely required. The gusset plate may have significant deformation and replacement may also be needed. Local beam and column yielding has occurred and straightening may be desirable for aesthetic reasons. | Brace has lost significant axial capacity, and replacement of braces is likely required. The gusset plate may have significant deformation and replacement may also be needed. Local beam and column yielding has occurred and straightening may be desirable for aesthetic reasons. | Brace and gusset are severely damaged with significant loss in stiffness and resistance, and both likely require replacement. Yielding and local buckling of beams and columns may be repaired by heat straightening, stiffeners or reinforcement, if there is no cracking or tearing. If cracking or tearing has initiated more substantial repair is needed |  |  | NO | NO | NO |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | YES | YES | YES |  |  | 60% | 40% | 20% |  |  | 0.5 | 0.5 | 0.5 |  |  | None | Not Given | By User | By User | Not Given | B1033.001a-DS2-1.JPG | B1033.001a-DS3-1.JPG | B1033.011a-DS3-2.JPG |  |  | No | 2011-08-24 Negative probability below 0.5% drift - overlap deemed acceptable. 2016-08-17 time consequence adjusted to avoid decreasing consequence with increasing member weight. | YES
B1033.031b | B1033.031b | Special Concentric Braced Frame, design to AISC minimum standards, Chevron Brace, Brace 41 PLF < w < 99 PLF | Costing is on a per bay basis. Costing does not include fireproofing removal or reapplication cost. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 36 | EA 1 | YES | NO | Buckling of brace in excess of the brace depth. Initiation of yielding and out-of-plane deformation of the gusset. Initiation of cracking of welds of gusset. Initiation of yielding in beams and columns adjacent to gusset. | Buckling of brace in excess of 2 time brace depth . Yielding and out-of-plane deformation of gusset . Cracking and tearing of welds and gussets adjacent to welds but crack length is less than critical for fracture . Significant yielding and local buckling in beams and columns adjacent to gusset . | Fracture of brace or gusset. Buckling of gusset. Severe yielding of beams and columns adjacent to the gusset with possibility of local buckling and cracking in the yielded areas. |  |  | 1 | 1 | 1 |  |  | 0.0074 | 0.0121 | 0.0152 |  |  | 0.3 | 0.25 | 0.35 |  |  | 0.1 | 0.1 | 0.1 |  |  | 0.3 | 0.25 | 0.35 |  |  | NO | YES | Superior | Superior | Superior | Superior | Brace has lost significant axial capacity, and replacement of braces is likely required. The gusset plate may have significant deformation and replacement may also be needed. Local beam and column yielding has occurred and straightening may be desirable for aesthetic reasons. | Brace has lost significant axial capacity, and replacement of braces is likely required. The gusset plate may have significant deformation and replacement may also be needed. Local beam and column yielding has occurred and straightening may be desirable for aesthetic reasons. | Brace and gusset are severely damaged with significant loss in stiffness and resistance, and both likely require replacement. Yielding and local buckling of beams and columns may be repaired by heat straightening, stiffeners or reinforcement, if there is no cracking or tearing. If cracking or tearing has initiated more substantial repair is needed |  |  | NO | NO | NO |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | YES | YES | YES |  |  | 60% | 40% | 20% |  |  | 0.5 | 0.5 | 0.5 |  |  | None | Not Given | By User | By User | Not Given | B1033.001a-DS2-1.JPG | B1033.001a-DS3-1.JPG | B1033.011a-DS3-2.JPG |  |  | No | 2011-08-24 Negative probability below 0.5% drift - overlap deemed acceptable. 2016-08-17 time consequence adjusted to avoid decreasing consequence with increasing member weight. | YES
B1033.031c | B1033.031c | Special Concentric Braced Frame, design to AISC minimum standards, Chevron Brace, Brace w > 100 PLF | Costing is on a per bay basis. Costing does not include fireproofing removal or reapplication cost. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 37 | EA 1 | YES | NO | Buckling of brace in excess of the brace depth. Initiation of yielding and out-of-plane deformation of the gusset. Initiation of cracking of welds of gusset. Initiation of yielding in beams and columns adjacent to gusset. | Buckling of brace in excess of 2 time brace depth . Yielding and out-of-plane deformation of gusset . Cracking and tearing of welds and gussets adjacent to welds but crack length is less than critical for fracture . Significant yielding and local buckling in beams and columns adjacent to gusset . | Fracture of brace or gusset. Buckling of gusset. Severe yielding of beams and columns adjacent to the gusset with possibility of local buckling and cracking in the yielded areas. |  |  | 1 | 1 | 1 |  |  | 0.0074 | 0.0121 | 0.0152 |  |  | 0.3 | 0.25 | 0.35 |  |  | 0.1 | 0.1 | 0.1 |  |  | 0.3 | 0.25 | 0.35 |  |  | NO | YES | Superior | Superior | Superior | Superior | Brace has lost significant axial capacity, and replacement of braces is likely required. The gusset plate may have significant deformation and replacement may also be needed. Local beam and column yielding has occurred and straightening may be desirable for aesthetic reasons. | Brace has lost significant axial capacity, and replacement of braces is likely required. The gusset plate may have significant deformation and replacement may also be needed. Local beam and column yielding has occurred and straightening may be desirable for aesthetic reasons. | Brace and gusset are severely damaged with significant loss in stiffness and resistance, and both likely require replacement. Yielding and local buckling of beams and columns may be repaired by heat straightening, stiffeners or reinforcement, if there is no cracking or tearing. If cracking or tearing has initiated more substantial repair is needed |  |  | NO | NO | NO |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | YES | YES | YES |  |  | 60% | 40% | 20% |  |  | 0.5 | 0.5 | 0.5 |  |  | None | Not Given | By User | By User | Not Given | B1033.001a-DS2-1.JPG | B1033.001a-DS3-1.JPG | B1033.011a-DS3-2.JPG |  |  | No | 2011-08-24 Negative probability below 0.5% drift - overlap deemed acceptable. 2016-08-17 time consequence adjusted to avoid decreasing consequence with increasing member weight. | YES
B1033.032a | B1033.032a | Special Concentric Braced Frame, design to AISC minimum standards, Single Diagonal Brace, Brace w < 40 PLF | Costing is on a per bay basis. Costing does not include fireproofing removal or reapplication cost. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 38 | EA 1 | YES | NO | Buckling of brace in excess of the brace depth. Initiation of yielding and out-of-plane deformation of the gusset. Initiation of cracking of welds of gusset. Initiation of yielding in beams and columns adjacent to gusset. | Buckling of brace in excess of 2 time brace depth . Yielding and out-of-plane deformation of gusset . Cracking and tearing of welds and gussets adjacent to welds but crack length is less than critical for fracture . Significant yielding and local buckling in beams and columns adjacent to gusset . | Fracture of brace or gusset. Buckling of gusset. Severe yielding of beams and columns adjacent to the gusset with possibility of local buckling and cracking in the yielded areas. |  |  | 1 | 1 | 1 |  |  | 0.0074 | 0.0121 | 0.0152 |  |  | 0.3 | 0.25 | 0.35 |  |  | 0.1 | 0.1 | 0.1 |  |  | 0.3 | 0.25 | 0.35 |  |  | NO | YES | Superior | Superior | Superior | Superior | Brace has lost significant axial capacity, and replacement of braces is likely required. The gusset plate may have significant deformation and replacement may also be needed. Local beam and column yielding has occurred and straightening may be desirable for aesthetic reasons. | Brace has lost significant axial capacity, and replacement of braces is likely required. The gusset plate may have significant deformation and replacement may also be needed. Local beam and column yielding has occurred and straightening may be desirable for aesthetic reasons. | Brace and gusset are severely damaged with significant loss in stiffness and resistance, and both likely require replacement. Yielding and local buckling of beams and columns may be repaired by heat straightening, stiffeners or reinforcement, if there is no cracking or tearing. If cracking or tearing has initiated more substantial repair is needed |  |  | NO | NO | NO |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | YES | YES | YES |  |  | 60% | 40% | 20% |  |  | 0.5 | 0.5 | 0.5 |  |  | None | Not Given | By User | By User | Not Given | B1033.001a-DS2-1.JPG | B1033.001a-DS3-1.JPG | B1033.011a-DS3-2.JPG |  |  | No | 2011-08-24 Negative probability below 0.5% drift - overlap deemed acceptable. 2016-08-17 time consequence adjusted to avoid decreasing consequence with increasing member weight. | YES
B1033.032b | B1033.032b | Special Concentric Braced Frame, design to AISC minimum standards, Single Diagonal Brace, Brace 41 PLF < w < 99 PLF | Costing is on a per bay basis. Costing does not include fireproofing removal or reapplication cost. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 39 | EA 1 | YES | NO | Buckling of brace in excess of the brace depth. Initiation of yielding and out-of-plane deformation of the gusset. Initiation of cracking of welds of gusset. Initiation of yielding in beams and columns adjacent to gusset. | Buckling of brace in excess of 2 time brace depth . Yielding and out-of-plane deformation of gusset . Cracking and tearing of welds and gussets adjacent to welds but crack length is less than critical for fracture . Significant yielding and local buckling in beams and columns adjacent to gusset . | Fracture of brace or gusset. Buckling of gusset. Severe yielding of beams and columns adjacent to the gusset with possibility of local buckling and cracking in the yielded areas. |  |  | 1 | 1 | 1 |  |  | 0.0074 | 0.0121 | 0.0152 |  |  | 0.3 | 0.25 | 0.35 |  |  | 0.1 | 0.1 | 0.1 |  |  | 0.3 | 0.25 | 0.35 |  |  | NO | YES | Superior | Superior | Superior | Superior | Brace has lost significant axial capacity, and replacement of braces is likely required. The gusset plate may have significant deformation and replacement may also be needed. Local beam and column yielding has occurred and straightening may be desirable for aesthetic reasons. | Brace has lost significant axial capacity, and replacement of braces is likely required. The gusset plate may have significant deformation and replacement may also be needed. Local beam and column yielding has occurred and straightening may be desirable for aesthetic reasons. | Brace and gusset are severely damaged with significant loss in stiffness and resistance, and both likely require replacement. Yielding and local buckling of beams and columns may be repaired by heat straightening, stiffeners or reinforcement, if there is no cracking or tearing. If cracking or tearing has initiated more substantial repair is needed |  |  | NO | NO | NO |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | YES | YES | YES |  |  | 60% | 40% | 20% |  |  | 0.5 | 0.5 | 0.5 |  |  | None | Not Given | By User | By User | Not Given | B1033.001a-DS2-1.JPG | B1033.001a-DS3-1.JPG | B1033.011a-DS3-2.JPG |  |  | No | 2011-08-24 Negative probability below 0.5% drift - overlap deemed acceptable. 2016-08-17 time consequence adjusted to avoid decreasing consequence with increasing member weight. | YES
B1033.032c | B1033.032c | Special Concentric Braced Frame, design to AISC minimum standards, Single Diagonal Brace, Brace w > 100 PLF | Costing is on a per bay basis. Costing does not include fireproofing removal or reapplication cost. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 40 | EA 1 | YES | NO | Buckling of brace in excess of the brace depth. Initiation of yielding and out-of-plane deformation of the gusset. Initiation of cracking of welds of gusset. Initiation of yielding in beams and columns adjacent to gusset. | Buckling of brace in excess of 2 time brace depth . Yielding and out-of-plane deformation of gusset . Cracking and tearing of welds and gussets adjacent to welds but crack length is less than critical for fracture . Significant yielding and local buckling in beams and columns adjacent to gusset . | Fracture of brace or gusset. Buckling of gusset. Severe yielding of beams and columns adjacent to the gusset with possibility of local buckling and cracking in the yielded areas. |  |  | 1 | 1 | 1 |  |  | 0.0074 | 0.0121 | 0.0152 |  |  | 0.3 | 0.25 | 0.35 |  |  | 0.1 | 0.1 | 0.1 |  |  | 0.3 | 0.25 | 0.35 |  |  | NO | YES | Superior | Superior | Superior | Superior | Brace has lost significant axial capacity, and replacement of braces is likely required. The gusset plate may have significant deformation and replacement may also be needed. Local beam and column yielding has occurred and straightening may be desirable for aesthetic reasons. | Brace has lost significant axial capacity, and replacement of braces is likely required. The gusset plate may have significant deformation and replacement may also be needed. Local beam and column yielding has occurred and straightening may be desirable for aesthetic reasons. | Brace and gusset are severely damaged with significant loss in stiffness and resistance, and both likely require replacement. Yielding and local buckling of beams and columns may be repaired by heat straightening, stiffeners or reinforcement, if there is no cracking or tearing. If cracking or tearing has initiated more substantial repair is needed |  |  | NO | NO | NO |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | YES | YES | YES |  |  | 60% | 40% | 20% |  |  | 0.5 | 0.5 | 0.5 |  |  | None | Not Given | By User | By User | Not Given | B1033.001a-DS2-1.JPG | B1033.001a-DS3-1.JPG | B1033.011a-DS3-2.JPG |  |  | No | 2011-08-24 Negative probability below 0.5% drift - overlap deemed acceptable. 2016-08-17 time consequence adjusted to avoid decreasing consequence with increasing member weight. | YES
B1033.033a | B1033.033a | Special Concentric Braced Frame, design to AISC minimum standards, X Brace, Brace w < 40 PLF | Costing is on a per bay basis. Costing does not include fireproofing removal or reapplication cost. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 4 | DS1 | DS2 | DS3 | DS4 |  | Sequential | Sequential | Sequential | Sequential |  | Seq(DS1,DS2,DS3,DS4) | 41 | EA 1 | YES | NO | Buckling of the brace has begun but does not exceed the depth of the brace. Initial yielding of the gusset has begun. Yielding has initiated in framing at gusset plates but no buckling has occurred. Residual buckling of the brace has occurred but is barely noticeable to the naked eye and does not exceed half the brace depth. Residual drift is slight. | Buckling of brace in excess of the brace depth. Initiation of yielding and out-of-plane deformation of the gusset. Initiation of cracking of welds of gusset. Initiation of yielding in beams and columns adjacent to gusset. | Buckling of brace in excess of 2 times brace depth . Yielding and out-of-plane deformation of gusset . Cracking and tearing of welds and gussets adjacent to welds but crack length is less than critical for fracture. Significant yielding and local buckling in beams and columns adjacent to gusset . | Fracture of brace or gusset. Buckling of gusset. Severe yielding of beams and columns adjacent to the gusset with possibly local buckling and cracking in the yielded areas. |  | 1 | 1 | 1 | 1 |  | 0.0038 | 0.0075 | 0.0145 | 0.0185 |  | 0.29 | 0.5 | 0.1 | 0.25 |  | 0.1 | 0.25 | 0.25 | 0.25 |  | 0.3 | 0.55 | 0.25 | 0.35 |  | NO | YES | Marginal | Average | Marginal | Average | Brace damage is largely aesthetic. Heat straightening may be desirable but replacement would be for aesthetic reasons. Gusset has minor loss of strength and stiffness and straightening or repair may be desirable aesthetic reasons. | Brace has lost significant axial capacity, and replacement of braces is likely required. The gusset plate may have significant deformation and replacement may also be needed. Local beam and column yielding has occurred and straightening may be desirable for aesthetic reasons. | Brace and gusset are severely damaged with significant loss in stiffness and resistance, and both likely require replacement. Yielding and local buckling of beams and columns may be repaired by heat straightening, stiffeners or reinforcement, if there is no cracking or tearing. If cracking or tearing has initiated more substantial repair is needed | Brace and or gusset have fractured and require replacement. Yielding and local buckling of beams and columns may be repaired by heat straightening, stiffeners or reinforcement, if there is no cracking or tearing. If cracking or tearing has initiated more substantial repair is needed |  | NO | NO | NO | NO |  | NO | NO | NO | NO |  | Not Applicable | Not Applicable | Not Applicable | Not Applicable |  | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 |  |  | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 |  |  | NO | YES | YES | YES |  | 0% | 60% | 40% | 20% |  | 0 | 0.5 | 0.5 | 0.5 |  | None | Not Given | By User | By User | Not Given | none | B1033.001a-DS2-1.JPG | B1033.001a-DS3-1.JPG | B1033.011a-DS3-2.JPG |  | No | 2011-08-24 Negative probability below 0.5% drift - overlap deemed acceptable. 2016-08-17 time consequence adjusted to avoid decreasing consequence with increasing member weight. | YES
B1033.033b | B1033.033b | Special Concentric Braced Frame, design to AISC minimum standards, X Brace, Brace 41 PLF < w < 99 PLF | Costing is on a per bay basis. Costing does not include fireproofing removal or reapplication cost. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 4 | DS1 | DS2 | DS3 | DS4 |  | Sequential | Sequential | Sequential | Sequential |  | Seq(DS1,DS2,DS3,DS4) | 42 | EA 1 | YES | NO | Buckling of the brace has begun but does not exceed the depth of the brace. Initial yielding of the gusset has begun. Yielding has initiated in framing at gusset plates but no buckling has occurred. Residual buckling of the brace has occurred but is barely noticeable to the naked eye and does not exceed half the brace depth. Residual drift is slight. | Buckling of brace in excess of the brace depth. Initiation of yielding and out-of-plane deformation of the gusset. Initiation of cracking of welds of gusset. Initiation of yielding in beams and columns adjacent to gusset. | Buckling of brace in excess of 2 times brace depth . Yielding and out-of-plane deformation of gusset . Cracking and tearing of welds and gussets adjacent to welds but crack length is less than critical for fracture . Significant yielding and local buckling in beams and columns adjacent to gusset . | Fracture of brace or gusset. Buckling of gusset. Severe yielding of beams and columns adjacent to the gusset with possibly local buckling and cracking in the yielded areas. |  | 1 | 1 | 1 | 1 |  | 0.0038 | 0.0075 | 0.0145 | 0.0185 |  | 0.29 | 0.5 | 0.1 | 0.25 |  | 0.1 | 0.25 | 0.25 | 0.25 |  | 0.3 | 0.55 | 0.25 | 0.35 |  | NO | YES | Marginal | Average | Marginal | Average | Brace damage is largely aesthetic. Heat straightening may be desirable but replacement would be for aesthetic reasons. Gusset has minor loss of strength and stiffness and straightening or repair may be desirable aesthetic reasons. | Brace has lost significant axial capacity, and replacement of braces is likely required. The gusset plate may have significant deformation and replacement may also be needed. Local beam and column yielding has occurred and straightening may be desirable for aesthetic reasons. | Brace and gusset are severely damaged with significant loss in stiffness and resistance, and both likely require replacement. Yielding and local buckling of beams and columns may be repaired by heat straightening, stiffeners or reinforcement, if there is no cracking or tearing. If cracking or tearing has initiated more substantial repair is needed | Brace and or gusset have fractured and require replacement. Yielding and local buckling of beams and columns may be repaired by heat straightening, stiffeners or reinforcement, if there is no cracking or tearing. If cracking or tearing has initiated more substantial repair is needed |  | NO | NO | NO | NO |  | NO | NO | NO | NO |  | Not Applicable | Not Applicable | Not Applicable | Not Applicable |  | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 |  |  | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 |  |  | NO | YES | YES | YES |  | 0% | 60% | 40% | 20% |  | 0 | 0.5 | 0.5 | 0.5 |  | None | Not Given | By User | By User | Not Given | none | B1033.001a-DS2-1.JPG | B1033.001a-DS3-1.JPG | B1033.011a-DS3-2.JPG |  | No | 2011-08-24 Negative probability below 0.5% drift - overlap deemed acceptable. 2016-08-17 time consequence adjusted to avoid decreasing consequence with increasing member weight. | YES
B1033.033c | B1033.033c | Special Concentric Braced Frame, design to AISC minimum standards, X Brace, Brace w > 100 PLF | Costing is on a per bay basis. Costing does not include fireproofing removal or reapplication cost. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 4 | DS1 | DS2 | DS3 | DS4 |  | Sequential | Sequential | Sequential | Sequential |  | Seq(DS1,DS2,DS3,DS4) | 43 | EA 1 | YES | NO | Buckling of the brace has begun but does not exceed the depth of the brace. Initial yielding of the gusset has begun. Yielding has initiated in framing at gusset plates but no buckling has occurred. Residual buckling of the brace has occurred but is barely noticeable to the naked eye and does not exceed half the brace depth. Residual drift is slight. | Buckling of brace in excess of the brace depth. Initiation of yielding and out-of-plane deformation of the gusset. Initiation of cracking of welds of gusset. Initiation of yielding in beams and columns adjacent to gusset. | Buckling of brace in excess of 2 times brace depth . Yielding and out-of-plane deformation of gusset . Cracking and tearing of welds and gussets adjacent to welds but crack length is less than critical for fracture . Significant yielding and local buckling in beams and columns adjacent to gusset . | Fracture of brace or gusset. Buckling of gusset. Severe yielding of beams and columns adjacent to the gusset with possibly local buckling and cracking in the yielded areas. |  | 1 | 1 | 1 | 1 |  | 0.0038 | 0.0075 | 0.0145 | 0.0185 |  | 0.29 | 0.5 | 0.1 | 0.25 |  | 0.1 | 0.25 | 0.25 | 0.25 |  | 0.3 | 0.55 | 0.25 | 0.35 |  | NO | YES | Marginal | Average | Marginal | Average | Brace damage is largely aesthetic. Heat straightening may be desirable but replacement would be for aesthetic reasons. Gusset has minor loss of strength and stiffness and straightening or repair may be desirable aesthetic reasons. | Brace has lost significant axial capacity, and replacement of braces is likely required. The gusset plate may have significant deformation and replacement may also be needed. Local beam and column yielding has occurred and straightening may be desirable for aesthetic reasons. | Brace and gusset are severely damaged with significant loss in stiffness and resistance, and both likely require replacement. Yielding and local buckling of beams and columns may be repaired by heat straightening, stiffeners or reinforcement, if there is no cracking or tearing. If cracking or tearing has initiated more substantial repair is needed | Brace and or gusset have fractured and require replacement. Yielding and local buckling of beams and columns may be repaired by heat straightening, stiffeners or reinforcement, if there is no cracking or tearing. If cracking or tearing has initiated more substantial repair is needed |  | NO | NO | NO | NO |  | NO | NO | NO | NO |  | Not Applicable | Not Applicable | Not Applicable | Not Applicable |  | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 |  |  | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 |  |  | NO | YES | YES | YES |  | 0% | 60% | 40% | 20% |  | 0 | 0.5 | 0.5 | 0.5 |  | None | Not Given | By User | By User | Not Given | none | B1033.001a-DS2-1.JPG | B1033.001a-DS3-1.JPG | B1033.011a-DS3-2.JPG |  | No | 2011-08-24 Negative probability below 0.5% drift - overlap deemed acceptable. 2016-08-17 time consequence adjusted to avoid decreasing consequence with increasing member weight. | YES
B1033.041a | B1033.041a | Special Concentric Braced Frame w double angle braces, Chevron Brace, Brace w < 40 PLF | Costing on a per bay basis, equivalent to AISC minimum SCBF criteria. Costing does not include fireproofing removal or reapplication cost. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 44 | EA 1 | YES | NO | Buckling of the brace has begun but does not exceed the depth of the brace. Initial yielding of the gusset has begun. Yielding has initiated in framing at gusset plates but no buckling has occurred. Residual buckling of the brace has occurred but is barely noticeable to the naked eye and does not exceed half the brace depth. Residual drift is slight. | Buckling of brace in excess of the brace depth. Initiation of yielding and out-of-plane deformation of the gusset. Initiation of cracking of welds of gusset. Initiation of yielding in beams and columns adjacent to gusset. | Fracture of brace or gusset. Buckling of gusset. Severe yielding of beams and columns adjacent to the gusset with possibility of local buckling and cracking in the yielded areas. |  |  | 1 | 1 | 1 |  |  | 0.00256 | 0.0048 | 0.0112 |  |  | 0.28 | 0.3 | 0.5 |  |  | 0.1 | 0.1 | 0.1 |  |  | 0.3 | 0.3 | 0.3 |  |  | NO | YES | Marginal | Average | Marginal | Average | Brace damage is largely aesthetic. Heat straightening may be desirable but replacement would be for aesthetic reasons. Gusset has minor loss of strength and stiffness and straightening or repair may be desirable aesthetic reasons. | Brace has lost significant axial capacity, and replacement braces is likely required. The gusset plate may have significant deformation and replacement may also be needed. Local beam and column yielding has occurred and straightening may be desirable for aesthetic reasons. | Brace and gusset are severely damaged with significant loss in stiffness and resistance, and both likely require replacement. Yielding and local buckling of beams and columns may be repaired by heat straightening, stiffeners or reinforcement, if there is no cracking or tearing. If cracking or tearing has initiated more substantial repair is needed |  |  | NO | NO | NO |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | YES | YES |  |  | 0% | 60% | 40% |  |  | 0 | 0.5 | 0.5 |  |  | None | Not Given | By User | By User | Not Given | none | none | none |  |  | No | 2011-08-24 DS3 beta changed from 0.5 to 0.30 to avoid negative probability. 2016-08-17 time consequence adjusted to avoid decreasing consequence with increasing member weight. | YES
B1033.041b | B1033.041b | Special Concentric Braced Frame w double angle braces, Chevron Brace, Brace 41 PLF < w < 99 PLF | Costing on a per bay basis, equivalent to AISC minimum SCBF criteria. Costing does not include fireproofing removal or reapplication cost. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 45 | EA 1 | YES | NO | Buckling of the brace has begun but does not exceed the depth of the brace. Initial yielding of the gusset has begun. Yielding has initiated in framing at gusset plates but no buckling has occurred. Residual buckling of the brace has occurred but is barely noticeable to the naked eye and does not exceed half the brace depth. Residual drift is slight. | Buckling of brace in excess of the brace depth. Initiation of yielding and out-of-plane deformation of the gusset. Initiation of cracking of welds of gusset. Initiation of yielding in beams and columns adjacent to gusset. | Fracture of brace or gusset. Buckling of gusset. Severe yielding of beams and columns adjacent to the gusset with possibility of local buckling and cracking in the yielded areas. |  |  | 1 | 1 | 1 |  |  | 0.00256 | 0.0048 | 0.0112 |  |  | 0.28 | 0.3 | 0.5 |  |  | 0.1 | 0.1 | 0.1 |  |  | 0.3 | 0.3 | 0.3 |  |  | NO | YES | Marginal | Average | Marginal | Average | Brace damage is largely aesthetic. Heat straightening may be desirable but replacement would be for aesthetic reasons. Gusset has minor loss of strength and stiffness and straightening or repair may be desirable aesthetic reasons. | Brace has lost significant axial capacity, and replacement braces is likely required. The gusset plate may have significant deformation and replacement may also be needed. Local beam and column yielding has occurred and straightening may be desirable for aesthetic reasons. | Brace and gusset are severely damaged with significant loss in stiffness and resistance, and both likely require replacement. Yielding and local buckling of beams and columns may be repaired by heat straightening, stiffeners or reinforcement, if there is no cracking or tearing. If cracking or tearing has initiated more substantial repair is needed |  |  | NO | NO | NO |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | YES | YES |  |  | 0% | 60% | 40% |  |  | 0 | 0.5 | 0.5 |  |  | None | Not Given | By User | By User | Not Given | none | none | none |  |  | No | 2011-08-24 DS3 beta changed from 0.5 to 0.30 to avoid negative probability. 2016-08-17 time consequence adjusted to avoid decreasing consequence with increasing member weight. | YES
B1033.041c | B1033.041c | Special Concentric Braced Frame w double angle braces, Chevron Brace, Brace w > 100 PLF | Costing on a per bay basis, equivalent to AISC minimum SCBF criteria. Costing does not include fireproofing removal or reapplication cost. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 46 | EA 1 | YES | NO | Buckling of the brace has begun but does not exceed the depth of the brace. Initial yielding of the gusset has begun. Yielding has initiated in framing at gusset plates but no buckling has occurred. Residual buckling of the brace has occurred but is barely noticeable to the naked eye and does not exceed half the brace depth. Residual drift is slight. | Buckling of brace in excess of the brace depth. Initiation of yielding and out-of-plane deformation of the gusset. Initiation of cracking of welds of gusset. Initiation of yielding in beams and columns adjacent to gusset. | Fracture of brace or gusset. Buckling of gusset. Severe yielding of beams and columns adjacent to the gusset with possibility of local buckling and cracking in the yielded areas. |  |  | 1 | 1 | 1 |  |  | 0.00256 | 0.0048 | 0.0112 |  |  | 0.28 | 0.3 | 0.5 |  |  | 0.1 | 0.1 | 0.1 |  |  | 0.3 | 0.3 | 0.3 |  |  | NO | YES | Marginal | Average | Marginal | Average | Brace damage is largely aesthetic. Heat straightening may be desirable but replacement would be for aesthetic reasons. Gusset has minor loss of strength and stiffness and straightening or repair may be desirable aesthetic reasons. | Brace has lost significant axial capacity, and replacement braces is likely required. The gusset plate may have significant deformation and replacement may also be needed. Local beam and column yielding has occurred and straightening may be desirable for aesthetic reasons. | Brace and gusset are severely damaged with significant loss in stiffness and resistance, and both likely require replacement. Yielding and local buckling of beams and columns may be repaired by heat straightening, stiffeners or reinforcement, if there is no cracking or tearing. If cracking or tearing has initiated more substantial repair is needed |  |  | NO | NO | NO |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | YES | YES |  |  | 0% | 60% | 40% |  |  | 0 | 0.5 | 0.5 |  |  | None | Not Given | By User | By User | Not Given | none | none | none |  |  | No | 2011-08-24 DS3 beta changed from 0.5 to 0.30 to avoid negative probability. 2016-08-17 time consequence adjusted to avoid decreasing consequence with increasing member weight. | YES
B1033.042a | B1033.042a | Special Concentric Braced Frame w double angle braces, Single Diagonal Brace, Brace w < 40 PLF | Costing on a per bay basis, equivalent to AISC minimum SCBF criteria. Costing does not include fireproofing removal or reapplication cost. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 47 | EA 1 | YES | NO | Buckling of the brace has begun but does not exceed the depth of the brace. Initial yielding of the gusset has begun. Yielding has initiated in framing at gusset plates but no buckling has occurred. Residual buckling of the brace has occurred but is barely noticeable to the naked eye and does not exceed half the brace depth. Residual drift is slight. | Buckling of brace in excess of the brace depth. Initiation of yielding and out-of-plane deformation of the gusset. Initiation of cracking of welds of gusset. Initiation of yielding in beams and columns adjacent to gusset. | Fracture of brace or gusset. Buckling of gusset. Severe yielding of beams and columns adjacent to the gusset with possibility of local buckling and cracking in the yielded areas. |  |  | 1 | 1 | 1 |  |  | 0.00256 | 0.0048 | 0.0112 |  |  | 0.28 | 0.3 | 0.5 |  |  | 0.1 | 0.1 | 0.1 |  |  | 0.3 | 0.3 | 0.3 |  |  | NO | YES | Marginal | Average | Marginal | Average | Brace damage is largely aesthetic. Heat straightening may be desirable but replacement would be for aesthetic reasons. Gusset has minor loss of strength and stiffness and straightening or repair may be desirable aesthetic reasons. | Brace has lost significant axial capacity, and replacement braces is likely required. The gusset plate may have significant deformation and replacement may also be needed. Local beam and column yielding has occurred and straightening may be desirable for aesthetic reasons. | Brace and gusset are severely damaged with significant loss in stiffness and resistance, and both likely require replacement. Yielding and local buckling of beams and columns may be repaired by heat straightening, stiffeners or reinforcement, if there is no cracking or tearing. If cracking or tearing has initiated more substantial repair is needed |  |  | NO | NO | NO |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | YES | YES |  |  | 0% | 60% | 40% |  |  | 0 | 0.5 | 0.5 |  |  | None | Not Given | By User | By User | Not Given | none | none | none |  |  | No | 2011-08-24 DS3 beta changed from 0.5 to 0.30 to avoid negative probability. 2016-08-17 time consequence adjusted to avoid decreasing consequence with increasing member weight. | YES
B1033.042b | B1033.042b | Special Concentric Braced Frame w double angle braces, Single Diagonal Brace, Brace 41 PLF < w < 99 PLF | Costing on a per bay basis, equivalent to AISC minimum SCBF criteria. Costing does not include fireproofing removal or reapplication cost. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 48 | EA 1 | YES | NO | Buckling of the brace has begun but does not exceed the depth of the brace. Initial yielding of the gusset has begun. Yielding has initiated in framing at gusset plates but no buckling has occurred. Residual buckling of the brace has occurred but is barely noticeable to the naked eye and does not exceed half the brace depth. Residual drift is slight. | Buckling of brace in excess of the brace depth. Initiation of yielding and out-of-plane deformation of the gusset. Initiation of cracking of welds of gusset. Initiation of yielding in beams and columns adjacent to gusset. | Fracture of brace or gusset. Buckling of gusset. Severe yielding of beams and columns adjacent to the gusset with possibility of local buckling and cracking in the yielded areas. |  |  | 1 | 1 | 1 |  |  | 0.00256 | 0.0048 | 0.0112 |  |  | 0.28 | 0.3 | 0.5 |  |  | 0.1 | 0.1 | 0.1 |  |  | 0.3 | 0.3 | 0.3 |  |  | NO | YES | Marginal | Average | Marginal | Average | Brace damage is largely aesthetic. Heat straightening may be desirable but replacement would be for aesthetic reasons. Gusset has minor loss of strength and stiffness and straightening or repair may be desirable aesthetic reasons. | Brace has lost significant axial capacity, and replacement braces is likely required. The gusset plate may have significant deformation and replacement may also be needed. Local beam and column yielding has occurred and straightening may be desirable for aesthetic reasons. | Brace and gusset are severely damaged with significant loss in stiffness and resistance, and both likely require replacement. Yielding and local buckling of beams and columns may be repaired by heat straightening, stiffeners or reinforcement, if there is no cracking or tearing. If cracking or tearing has initiated more substantial repair is needed |  |  | NO | NO | NO |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | YES | YES |  |  | 0% | 60% | 40% |  |  | 0 | 0.5 | 0.5 |  |  | None | Not Given | By User | By User | Not Given | none | none | none |  |  | No | 2011-08-24 DS3 beta changed from 0.5 to 0.30 to avoid negative probability. 2016-08-17 time consequence adjusted to avoid decreasing consequence with increasing member weight. | YES
B1033.042c | B1033.042c | Special Concentric Braced Frame w double angle braces, Single Diagonal Brace, Brace w > 100 PLF | Costing on a per bay basis, equivalent to AISC minimum SCBF criteria. Costing does not include fireproofing removal or reapplication cost. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 49 | EA 1 | YES | NO | Buckling of the brace has begun but does not exceed the depth of the brace. Initial yielding of the gusset has begun. Yielding has initiated in framing at gusset plates but no buckling has occurred. Residual buckling of the brace has occurred but is barely noticeable to the naked eye and does not exceed half the brace depth. Residual drift is slight. | Buckling of brace in excess of the brace depth. Initiation of yielding and out-of-plane deformation of the gusset. Initiation of cracking of welds of gusset. Initiation of yielding in beams and columns adjacent to gusset. | Fracture of brace or gusset. Buckling of gusset. Severe yielding of beams and columns adjacent to the gusset with possibility of local buckling and cracking in the yielded areas. |  |  | 1 | 1 | 1 |  |  | 0.00256 | 0.0048 | 0.0112 |  |  | 0.28 | 0.3 | 0.5 |  |  | 0.1 | 0.1 | 0.1 |  |  | 0.3 | 0.3 | 0.3 |  |  | NO | YES | Marginal | Average | Marginal | Average | Brace damage is largely aesthetic. Heat straightening may be desirable but replacement would be for aesthetic reasons. Gusset has minor loss of strength and stiffness and straightening or repair may be desirable aesthetic reasons. | Brace has lost significant axial capacity, and replacement braces is likely required. The gusset plate may have significant deformation and replacement may also be needed. Local beam and column yielding has occurred and straightening may be desirable for aesthetic reasons. | Brace and gusset are severely damaged with significant loss in stiffness and resistance, and both likely require replacement. Yielding and local buckling of beams and columns may be repaired by heat straightening, stiffeners or reinforcement, if there is no cracking or tearing. If cracking or tearing has initiated more substantial repair is needed |  |  | NO | NO | NO |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | YES | YES |  |  | 0% | 60% | 40% |  |  | 0 | 0.5 | 0.5 |  |  | None | Not Given | By User | By User | Not Given | none | none | none |  |  | No | 2011-08-24 DS3 beta changed from 0.5 to 0.30 to avoid negative probability. 2016-08-17 time consequence adjusted to avoid decreasing consequence with increasing member weight. | YES
B1033.043a | B1033.043a | Special Concentric Braced Frame w double angle braces, X Brace, Brace w < 40 PLF | Costing on a per bay basis, equivalent to AISC minimum SCBF criteria. Costing does not include fireproofing removal or reapplication cost. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 50 | EA 1 | YES | NO | Buckling of the brace has begun but does not exceed the depth of the brace. Initial yielding of the gusset has begun. Yielding has initiated in framing at gusset plates but no buckling has occurred. Residual buckling of the brace has occurred but is barely noticeable to the naked eye and does not exceed half the brace depth. Residual drift is slight. | Buckling of brace in excess of the brace depth. Initiation of yielding and out-of-plane deformation of the gusset. Initiation of cracking of welds of gusset. Initiation of yielding in beams and columns adjacent to gusset. | Fracture of brace or gusset. Buckling of gusset. Severe yielding of beams and columns adjacent to the gusset with possibility of local buckling and cracking in the yielded areas. |  |  | 1 | 1 | 1 |  |  | 0.00256 | 0.0048 | 0.0112 |  |  | 0.28 | 0.3 | 0.5 |  |  | 0.1 | 0.1 | 0.1 |  |  | 0.3 | 0.3 | 0.3 |  |  | NO | YES | Marginal | Average | Marginal | Average | Brace damage is largely aesthetic. Heat straightening may be desirable but replacement would be for aesthetic reasons. Gusset has minor loss of strength and stiffness and straightening or repair may be desirable aesthetic reasons. | Brace has lost significant axial capacity, and replacement braces is likely required. The gusset plate may have significant deformation and replacement may also be needed. Local beam and column yielding has occurred and straightening may be desirable for aesthetic reasons. | Brace and gusset are severely damaged with significant loss in stiffness and resistance, and both likely require replacement. Yielding and local buckling of beams and columns may be repaired by heat straightening, stiffeners or reinforcement, if there is no cracking or tearing. If cracking or tearing has initiated more substantial repair is needed |  |  | NO | NO | NO |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | YES | YES |  |  | 0% | 60% | 40% |  |  | 0 | 0.5 | 0.5 |  |  | None | Not Given | By User | By User | Not Given | none | none | none |  |  | No | 2011-08-24 DS3 beta changed from 0.5 to 0.30 to avoid negative probability. 2016-08-17 time consequence adjusted to avoid decreasing consequence with increasing member weight. | YES
B1033.043b | B1033.043b | Special Concentric Braced Frame w double angle braces, X Brace, Brace 41 PLF < w < 99 PLF | Costing on a per bay basis, equivalent to AISC minimum SCBF criteria. Costing does not include fireproofing removal or reapplication cost. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 51 | EA 1 | YES | NO | Buckling of the brace has begun but does not exceed the depth of the brace. Initial yielding of the gusset has begun. Yielding has initiated in framing at gusset plates but no buckling has occurred. Residual buckling of the brace has occurred but is barely noticeable to the naked eye and does not exceed half the brace depth. Residual drift is slight. | Buckling of brace in excess of the brace depth. Initiation of yielding and out-of-plane deformation of the gusset. Initiation of cracking of welds of gusset. Initiation of yielding in beams and columns adjacent to gusset. | Fracture of brace or gusset. Buckling of gusset. Severe yielding of beams and columns adjacent to the gusset with possibility of local buckling and cracking in the yielded areas. |  |  | 1 | 1 | 1 |  |  | 0.00256 | 0.0048 | 0.0112 |  |  | 0.28 | 0.3 | 0.5 |  |  | 0.1 | 0.1 | 0.1 |  |  | 0.3 | 0.3 | 0.3 |  |  | NO | YES | Marginal | Average | Marginal | Average | Brace damage is largely aesthetic. Heat straightening may be desirable but replacement would be for aesthetic reasons. Gusset has minor loss of strength and stiffness and straightening or repair may be desirable aesthetic reasons. | Brace has lost significant axial capacity, and replacement braces is likely required. The gusset plate may have significant deformation and replacement may also be needed. Local beam and column yielding has occurred and straightening may be desirable for aesthetic reasons. | Brace and gusset are severely damaged with significant loss in stiffness and resistance, and both likely require replacement. Yielding and local buckling of beams and columns may be repaired by heat straightening, stiffeners or reinforcement, if there is no cracking or tearing. If cracking or tearing has initiated more substantial repair is needed |  |  | NO | NO | NO |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | YES | YES |  |  | 0% | 60% | 40% |  |  | 0 | 0.5 | 0.5 |  |  | None | Not Given | By User | By User | Not Given | none | none | none |  |  | No | 2011-08-24 DS3 beta changed from 0.5 to 0.30 to avoid negative probability. 2016-08-17 time consequence adjusted to avoid decreasing consequence with increasing member weight. | YES
B1033.043c | B1033.043c | Special Concentric Braced Frame w double angle braces, X Brace, Brace w > 100 PLF | Costing on a per bay basis, equivalent to AISC minimum SCBF criteria. Costing does not include fireproofing removal or reapplication cost. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 52 | EA 1 | YES | NO | Buckling of the brace has begun but does not exceed the depth of the brace. Initial yielding of the gusset has begun. Yielding has initiated in framing at gusset plates but no buckling has occurred. Residual buckling of the brace has occurred but is barely noticeable to the naked eye and does not exceed half the brace depth. Residual drift is slight. | Buckling of brace in excess of the brace depth. Initiation of yielding and out-of-plane deformation of the gusset. Initiation of cracking of welds of gusset. Initiation of yielding in beams and columns adjacent to gusset. | Fracture of brace or gusset. Buckling of gusset. Severe yielding of beams and columns adjacent to the gusset with possibility of local buckling and cracking in the yielded areas. |  |  | 1 | 1 | 1 |  |  | 0.00256 | 0.0048 | 0.0112 |  |  | 0.28 | 0.3 | 0.5 |  |  | 0.1 | 0.1 | 0.1 |  |  | 0.3 | 0.3 | 0.3 |  |  | NO | YES | Marginal | Average | Marginal | Average | Brace damage is largely aesthetic. Heat straightening may be desirable but replacement would be for aesthetic reasons. Gusset has minor loss of strength and stiffness and straightening or repair may be desirable aesthetic reasons. | Brace has lost significant axial capacity, and replacement braces is likely required. The gusset plate may have significant deformation and replacement may also be needed. Local beam and column yielding has occurred and straightening may be desirable for aesthetic reasons. | Brace and gusset are severely damaged with significant loss in stiffness and resistance, and both likely require replacement. Yielding and local buckling of beams and columns may be repaired by heat straightening, stiffeners or reinforcement, if there is no cracking or tearing. If cracking or tearing has initiated more substantial repair is needed |  |  | NO | NO | NO |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | YES | YES |  |  | 0% | 60% | 40% |  |  | 0 | 0.5 | 0.5 |  |  | None | Not Given | By User | By User | Not Given | none | none | none |  |  | No | 2011-08-24 DS3 beta changed from 0.5 to 0.30 to avoid negative probability. 2016-08-17 time consequence adjusted to avoid decreasing consequence with increasing member weight. | YES
B1033.051a | B1033.051a | Ordinary Concentric Braced Frame w compact braces, Chevron Brace, Brace w < 40 PLF | Costing on a per bay basis, braces may be HSS, WF, or Angle. Costing does not include fireproofing removal or reapplication cost. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 53 | EA 1 | YES | NO | Buckling of the brace has begun but does not exceed the depth of the brace. Initial yielding of the gusset has begun. Yielding has initiated in framing at gusset plates but no buckling has occurred. Residual deformation of the brace has occurred but is barely noticeable to the naked eye and does not exceed half the brace depth. Residual drift is slight. | Brace has buckled but residual displacement does not exceed two times brace depth. Brace has not fractured. Gusset plate exhibits extensive yielding. Yielding extends well into the members. | Brace has fractured. Gusset plate has torn, possibly completely free of framing. Local buckling of flanges and web of framing members. Bolt fractures in beam-column connections. |  |  | 1 | 1 | 1 |  |  | 0.00159 | 0.01 | 0.0178 |  |  | 0.66 | 0.15 | 0.43 |  |  | 0.25 | 0.25 | 0.25 |  |  | 0.7 | 0.3 | 0.3 |  |  | NO | YES | Not Rated | Marginal | average | Superior | Brace damage is largely aesthetic. Heat straightening may be desirable but replacement would be for aesthetic reasons. Gusset has minor loss of strength and stiffness and straightening or repair may be desirable aesthetic reasons. | Replace brace. Gusset plate must be replaced 50% of the time. Heat straightening of deformed beams and columns may be required. | Replace brace. Gusset plate must be replaced 90% of the time. Replacement of portions (deformed flanges, webs) of permanently deformed beams and columns likely required. |  |  | NO | NO | NO |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | YES | YES |  |  | 0% | 40% | 20% |  |  | 0 | 0.5 | 0.5 |  |  | None | Not Given | By User | By User | Not Given | none | none | none |  |  | No | 2011-08-24 DS3 beta changed from 0.5 to 0.30 to avoid negative probability. 2016-08-17 time consequence adjusted to avoid decreasing consequence with increasing member weight. | YES
B1033.051b | B1033.051b | Ordinary Concentric Braced Frame w compact braces, Chevron Brace, Brace w, 41 PLF < w < 99 PLF | Costing on a per bay basis, braces may be HSS, WF, or Angle. Costing does not include fireproofing removal or reapplication cost. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 54 | EA 1 | YES | NO | Buckling of the brace has begun but does not exceed the depth of the brace. Initial yielding of the gusset has begun. Yielding has initiated in framing at gusset plates but no buckling has occurred. Residual deformation of the brace has occurred but is barely noticeable to the naked eye and does not exceed half the brace depth. Residual drift is slight. | Brace has buckled but residual displacement does not exceed two times brace depth. Brace has not fractured. Gusset plate exhibits extensive yielding. Yielding extends well into the members. | Brace has fractured. Gusset plate has torn, possibly completely free of framing. Local buckling of flanges and web of framing members. Bolt fractures in beam-column connections. |  |  | 1 | 1 | 1 |  |  | 0.00159 | 0.01 | 0.0178 |  |  | 0.66 | 0.15 | 0.43 |  |  | 0.25 | 0.25 | 0.25 |  |  | 0.7 | 0.3 | 0.3 |  |  | NO | YES | Not Rated | Marginal | average | Superior | Brace damage is largely aesthetic. Heat straightening may be desirable but replacement would be for aesthetic reasons. Gusset has minor loss of strength and stiffness and straightening or repair may be desirable aesthetic reasons. | Replace brace. Gusset plate must be replaced 50% of the time. Heat straightening of deformed beams and columns may be required. | Replace brace. Gusset plate must be replaced 90% of the time. Replacement of portions (deformed flanges, webs) of permanently deformed beams and columns likely required. |  |  | NO | NO | NO |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | YES | YES |  |  | 0% | 40% | 20% |  |  | 0 | 0.5 | 0.5 |  |  | None | Not Given | By User | By User | Not Given | none | none | none |  |  | No | 2011-08-24 DS3 beta changed from 0.5 to 0.30 to avoid negative probability. 2016-08-17 time consequence adjusted to avoid decreasing consequence with increasing member weight. | YES
B1033.051c | B1033.051c | Ordinary Concentric Braced Frame w compact braces, Chevron Brace, Brace w > 100 PLF | Costing on a per bay basis, braces may be HSS, WF, or Angle. Costing does not include fireproofing removal or reapplication cost. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 55 | EA 1 | YES | NO | Buckling of the brace has begun but does not exceed the depth of the brace. Initial yielding of the gusset has begun. Yielding has initiated in framing at gusset plates but no buckling has occurred. Residual deformation of the brace has occurred but is barely noticeable to the naked eye and does not exceed half the brace depth. Residual drift is slight. | Brace has buckled but residual displacement does not exceed two times brace depth. Brace has not fractured. Gusset plate exhibits extensive yielding. Yielding extends well into the members. | Brace has fractured. Gusset plate has torn, possibly completely free of framing. Local buckling of flanges and web of framing members. Bolt fractures in beam-column connections. |  |  | 1 | 1 | 1 |  |  | 0.00159 | 0.01 | 0.0178 |  |  | 0.66 | 0.15 | 0.43 |  |  | 0.25 | 0.25 | 0.25 |  |  | 0.7 | 0.3 | 0.3 |  |  | NO | YES | Not Rated | Marginal | average | Superior | Brace damage is largely aesthetic. Heat straightening may be desirable but replacement would be for aesthetic reasons. Gusset has minor loss of strength and stiffness and straightening or repair may be desirable aesthetic reasons. | Replace brace. Gusset plate must be replaced 50% of the time. Heat straightening of deformed beams and columns may be required. | Replace brace. Gusset plate must be replaced 90% of the time. Replacement of portions (deformed flanges, webs) of permanently deformed beams and columns likely required. |  |  | NO | NO | NO |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | YES | YES |  |  | 0% | 40% | 20% |  |  | 0 | 0.5 | 0.5 |  |  | None | Not Given | By User | By User | Not Given | none | none | none |  |  | No | 2011-08-24 DS3 beta changed from 0.5 to 0.30 to avoid negative probability. 2016-08-17 time consequence adjusted to avoid decreasing consequence with increasing member weight. | YES
B1033.052a | B1033.052a | Ordinary Concentric Braced Frame w compact braces, Single Diagonal Brace, Brace w < 40 PLF | Costing on a per bay basis, braces may be HSS, WF, or Angle. Costing does not include fireproofing removal or reapplication cost. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 56 | EA 1 | YES | NO | Buckling of the brace has begun but does not exceed the depth of the brace. Initial yielding of the gusset has begun. Yielding has initiated in framing at gusset plates but no buckling has occurred. Residual deformation of the brace has occurred but is barely noticeable to the naked eye and does not exceed half the brace depth. Residual drift is slight. | Brace has buckled but residual displacement does not exceed two times brace depth. Brace has not fractured. Gusset plate exhibits extensive yielding. Yielding extends well into the members. | Brace has fractured. Gusset plate has torn, possibly completely free of framing. Local buckling of flanges and web of framing members. Bolt fractures in beam-column connections. |  |  | 1 | 1 | 1 |  |  | 0.00159 | 0.01 | 0.0178 |  |  | 0.66 | 0.15 | 0.43 |  |  | 0.25 | 0.25 | 0.25 |  |  | 0.7 | 0.3 | 0.3 |  |  | NO | YES | Not Rated | Marginal | average | Superior | Brace damage is largely aesthetic. Heat straightening may be desirable but replacement would be for aesthetic reasons. Gusset has minor loss of strength and stiffness and straightening or repair may be desirable aesthetic reasons. | Replace brace. Gusset plate must be replaced 50% of the time. Heat straightening of deformed beams and columns may be required. | Replace brace. Gusset plate must be replaced 90% of the time. Replacement of portions (deformed flanges, webs) of permanently deformed beams and columns likely required. |  |  | NO | NO | NO |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | YES | YES |  |  | 0% | 40% | 20% |  |  | 0 | 0.5 | 0.5 |  |  | None | Not Given | By User | By User | Not Given | none | none | none |  |  | No | 2011-08-24 DS3 beta changed from 0.5 to 0.30 to avoid negative probability. 2016-08-17 time consequence adjusted to avoid decreasing consequence with increasing member weight. | YES
B1033.052b | B1033.052b | Ordinary Concentric Braced Frame w compact braces, Single Diagonal Brace, Brace w, 41 PLF < w < 99 PLF | Costing on a per bay basis, braces may be HSS, WF, or Angle. Costing does not include fireproofing removal or reapplication cost. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 57 | EA 1 | YES | NO | Buckling of the brace has begun but does not exceed the depth of the brace. Initial yielding of the gusset has begun. Yielding has initiated in framing at gusset plates but no buckling has occurred. Residual deformation of the brace has occurred but is barely noticeable to the naked eye and does not exceed half the brace depth. Residual drift is slight. | Brace has buckled but residual displacement does not exceed two times brace depth. Brace has not fractured. Gusset plate exhibits extensive yielding. Yielding extends well into the members. | Brace has fractured. Gusset plate has torn, possibly completely free of framing. Local buckling of flanges and web of framing members. Bolt fractures in beam-column connections. |  |  | 1 | 1 | 1 |  |  | 0.00159 | 0.01 | 0.0178 |  |  | 0.66 | 0.15 | 0.43 |  |  | 0.25 | 0.25 | 0.25 |  |  | 0.7 | 0.3 | 0.3 |  |  | NO | YES | Not Rated | Marginal | average | Superior | Brace damage is largely aesthetic. Heat straightening may be desirable but replacement would be for aesthetic reasons. Gusset has minor loss of strength and stiffness and straightening or repair may be desirable aesthetic reasons. | Replace brace. Gusset plate must be replaced 50% of the time. Heat straightening of deformed beams and columns may be required. | Replace brace. Gusset plate must be replaced 90% of the time. Replacement of portions (deformed flanges, webs) of permanently deformed beams and columns likely required. |  |  | NO | NO | NO |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | YES | YES |  |  | 0% | 40% | 20% |  |  | 0 | 0.5 | 0.5 |  |  | None | Not Given | By User | By User | Not Given | none | none | none |  |  | No | 2011-08-24 DS3 beta changed from 0.5 to 0.30 to avoid negative probability. 2016-08-17 time consequence adjusted to avoid decreasing consequence with increasing member weight. | YES
B1033.052c | B1033.052c | Ordinary Concentric Braced Frame w compact braces, Single Diagonal Brace, Brace w > 100 PLF | Costing on a per bay basis, braces may be HSS, WF, or Angle. Costing does not include fireproofing removal or reapplication cost. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 58 | EA 1 | YES | NO | Buckling of the brace has begun but does not exceed the depth of the brace. Initial yielding of the gusset has begun. Yielding has initiated in framing at gusset plates but no buckling has occurred. Residual deformation of the brace has occurred but is barely noticeable to the naked eye and does not exceed half the brace depth. Residual drift is slight. | Brace has buckled but residual displacement does not exceed two times brace depth. Brace has not fractured. Gusset plate exhibits extensive yielding. Yielding extends well into the members. | Brace has fractured. Gusset plate has torn, possibly completely free of framing. Local buckling of flanges and web of framing members. Bolt fractures in beam-column connections. |  |  | 1 | 1 | 1 |  |  | 0.00159 | 0.01 | 0.0178 |  |  | 0.66 | 0.15 | 0.43 |  |  | 0.25 | 0.25 | 0.25 |  |  | 0.7 | 0.3 | 0.3 |  |  | NO | YES | Not Rated | Marginal | average | Superior | Brace damage is largely aesthetic. Heat straightening may be desirable but replacement would be for aesthetic reasons. Gusset has minor loss of strength and stiffness and straightening or repair may be desirable aesthetic reasons. | Replace brace. Gusset plate must be replaced 50% of the time. Heat straightening of deformed beams and columns may be required. | Replace brace. Gusset plate must be replaced 90% of the time. Replacement of portions (deformed flanges, webs) of permanently deformed beams and columns likely required. |  |  | NO | NO | NO |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | YES | YES |  |  | 0% | 40% | 20% |  |  | 0 | 0.5 | 0.5 |  |  | None | Not Given | By User | By User | Not Given | none | none | none |  |  | No | 2011-08-24 DS3 beta changed from 0.5 to 0.30 to avoid negative probability. 2016-08-17 time consequence adjusted to avoid decreasing consequence with increasing member weight. | YES
B1033.053a | B1033.053a | Ordinary Concentric Braced Frame w compact braces, X Brace, Brace w < 40 PLF | Costing on a per bay basis, braces may be HSS, WF, or Angle. Costing does not include fireproofing removal or reapplication cost. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 59 | EA 1 | YES | NO | Buckling of the brace has begun but does not exceed the depth of the brace. Initial yielding of the gusset has begun. Yielding has initiated in framing at gusset plates but no buckling has occurred. Residual deformation of the brace has occurred but is barely noticeable to the naked eye and does not exceed half the brace depth. Residual drift is slight. | Brace has buckled but residual displacement does not exceed two times brace depth. Brace has not fractured. Gusset plate exhibits extensive yielding. Yielding extends well into the members. | Brace has fractured. Gusset plate has torn, possibly completely free of framing. Local buckling of flanges and web of framing members. Bolt fractures in beam-column connections. |  |  | 1 | 1 | 1 |  |  | 0.00159 | 0.01 | 0.0178 |  |  | 0.66 | 0.15 | 0.43 |  |  | 0.25 | 0.25 | 0.25 |  |  | 0.7 | 0.3 | 0.3 |  |  | NO | YES | Not Rated | Marginal | average | Superior | Brace damage is largely aesthetic. Heat straightening may be desirable but replacement would be for aesthetic reasons. Gusset has minor loss of strength and stiffness and straightening or repair may be desirable aesthetic reasons. | Replace brace. Gusset plate must be replaced 50% of the time. Heat straightening of deformed beams and columns may be required. | Replace brace. Gusset plate must be replaced 90% of the time. Replacement of portions (deformed flanges, webs) of permanently deformed beams and columns likely required. |  |  | NO | NO | NO |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | YES | YES |  |  | 0% | 40% | 20% |  |  | 0 | 0.5 | 0.5 |  |  | None | Not Given | By User | By User | Not Given | none | none | none |  |  | No | 2011-08-24 DS3 beta changed from 0.5 to 0.30 to avoid negative probability. 2016-08-17 time consequence adjusted to avoid decreasing consequence with increasing member weight. | YES
B1033.053b | B1033.053b | Ordinary Concentric Braced Frame w compact braces, X Brace, Brace w, 41 PLF < w < 99 PLF | Costing on a per bay basis, braces may be HSS, WF, or Angle. Costing does not include fireproofing removal or reapplication cost. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 60 | EA 1 | YES | NO | Buckling of the brace has begun but does not exceed the depth of the brace. Initial yielding of the gusset has begun. Yielding has initiated in framing at gusset plates but no buckling has occurred. Residual deformation of the brace has occurred but is barely noticeable to the naked eye and does not exceed half the brace depth. Residual drift is slight. | Brace has buckled but residual displacement does not exceed two times brace depth. Brace has not fractured. Gusset plate exhibits extensive yielding. Yielding extends well into the members. | Brace has fractured. Gusset plate has torn, possibly completely free of framing. Local buckling of flanges and web of framing members. Bolt fractures in beam-column connections. |  |  | 1 | 1 | 1 |  |  | 0.00159 | 0.01 | 0.0178 |  |  | 0.66 | 0.15 | 0.43 |  |  | 0.25 | 0.25 | 0.25 |  |  | 0.7 | 0.3 | 0.3 |  |  | NO | YES | Not Rated | Marginal | average | Superior | Brace damage is largely aesthetic. Heat straightening may be desirable but replacement would be for aesthetic reasons. Gusset has minor loss of strength and stiffness and straightening or repair may be desirable aesthetic reasons. | Replace brace. Gusset plate must be replaced 50% of the time. Heat straightening of deformed beams and columns may be required. | Replace brace. Gusset plate must be replaced 90% of the time. Replacement of portions (deformed flanges, webs) of permanently deformed beams and columns likely required. |  |  | NO | NO | NO |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | YES | YES |  |  | 0% | 40% | 20% |  |  | 0 | 0.5 | 0.5 |  |  | None | Not Given | By User | By User | Not Given | none | none | none |  |  | No | 2011-08-24 DS3 beta changed from 0.5 to 0.30 to avoid negative probability. 2016-08-17 time consequence adjusted to avoid decreasing consequence with increasing member weight. | YES
B1033.053c | B1033.053c | Ordinary Concentric Braced Frame w compact braces, X Brace, Brace w > 100 PLF | Costing on a per bay basis, braces may be HSS, WF, or Angle. Costing does not include fireproofing removal or reapplication cost. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 61 | EA 1 | YES | NO | Buckling of the brace has begun but does not exceed the depth of the brace. Initial yielding of the gusset has begun. Yielding has initiated in framing at gusset plates but no buckling has occurred. Residual deformation of the brace has occurred but is barely noticeable to the naked eye and does not exceed half the brace depth. Residual drift is slight. | Brace has buckled but residual displacement does not exceed two times brace depth. Brace has not fractured. Gusset plate exhibits extensive yielding. Yielding extends well into the members. | Brace has fractured. Gusset plate has torn, possibly completely free of framing. Local buckling of flanges and web of framing members. Bolt fractures in beam-column connections. |  |  | 1 | 1 | 1 |  |  | 0.00159 | 0.01 | 0.0178 |  |  | 0.66 | 0.15 | 0.43 |  |  | 0.25 | 0.25 | 0.25 |  |  | 0.7 | 0.3 | 0.3 |  |  | NO | YES | Not Rated | Marginal | average | Superior | Brace damage is largely aesthetic. Heat straightening may be desirable but replacement would be for aesthetic reasons. Gusset has minor loss of strength and stiffness and straightening or repair may be desirable aesthetic reasons. | Replace brace. Gusset plate must be replaced 50% of the time. Heat straightening of deformed beams and columns may be required. | Replace brace. Gusset plate must be replaced 90% of the time. Replacement of portions (deformed flanges, webs) of permanently deformed beams and columns likely required. |  |  | NO | NO | NO |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | YES | YES |  |  | 0% | 40% | 20% |  |  | 0 | 0.5 | 0.5 |  |  | None | Not Given | By User | By User | Not Given | none | none | none |  |  | No | 2011-08-24 DS3 beta changed from 0.5 to 0.30 to avoid negative probability. 2016-08-17 time consequence adjusted to avoid decreasing consequence with increasing member weight. | YES
B1033.061a | B1033.061a | Ordinary Concentric Braced Frame, braces design to ductile slenderness limits, Chevron Brace, Brace w < 40 PLF | Costing on a per bay basis, equivalent to AISC OCBF criteria. Braces may be HSS, WF, or Angle. Costing does not include fireproofing removal or reapplication cost. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 62 | EA 1 | YES | NO | Buckling of brace in excess of the brace depth. Initiation of yielding and out-of-plane deformation of the gusset. Initiation of cracking of welds of gusset. Initiation of yielding in beams and columns adjacent to gusset. | Buckling of brace in excess of 2 time brace depth. Yielding and out-of-plane deformation of gusset. Cracking and tearing of welds and gussets adjacent to welds but crack length is less than critical for fracture. Significant yielding and local buckling in beams and columns adjacent to gusset. | Fracture of brace or gusset. Buckling of gusset. Severe yielding of beams and columns adjacent to the gusset with possibility of local buckling and cracking in the yielded areas. Nearly total loss of lateral resistance. |  |  | 1 | 1 | 1 |  |  | 0.00159 | 0.01 | 0.01776 |  |  | 0.65 | 0.15 | 0.4 |  |  | 0.25 | 0.25 | 0.25 |  |  | 0.7 | 0.3 | 0.3 |  |  | NO | YES | Average | Average | Average | Average | Brace damage is largely aesthetic. Heat straightening may be desirable but replacement would be for aesthetic reasons. Gusset has minor loss of strength and stiffness and straightening or repair may be desirable aesthetic reasons. | Brace has lost significant axial capacity, and replacement of braces is likely required. The gusset plate may have significant deformation and replacement may also be needed. Local beam and column yielding has occurred and straightening may be desirable for aesthetic reasons. | Brace and gusset are severely damaged with significant loss in stiffness and resistance, and both likely require replacement. Yielding and local buckling of beams and columns may be repaired by heat straightening, stiffeners or reinforcement, if there is no cracking or tearing. If cracking or tearing has initiated more substantial repair is needed |  |  | NO | NO | NO |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | YES | YES | YES |  |  | 60% | 40% | 20% |  |  | 0.5 | 0.5 | 0.5 |  |  | None | Not Given | By User | By User | Not Given | none | none | none |  |  | No | 2011-08-24 DS3 beta changed from 0.5 to 0.30 to avoid negative probability. 2016-08-17 time consequence adjusted to avoid decreasing consequence with increasing member weight. | YES
B1033.061b | B1033.061b | Ordinary Concentric Braced Frame, braces design to ductile slenderness limits, Chevron Brace, Brace 41 PLF < w < 99 PLF | Costing on a per bay basis, equivalent to AISC OCBF criteria. Braces may be HSS, WF, or Angle. Costing does not include fireproofing removal or reapplication cost. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 63 | EA 1 | YES | NO | Buckling of brace in excess of the brace depth. Initiation of yielding and out-of-plane deformation of the gusset. Initiation of cracking of welds of gusset. Initiation of yielding in beams and columns adjacent to gusset. | Buckling of brace in excess of 2 time brace depth. Yielding and out-of-plane deformation of gusset. Cracking and tearing of welds and gussets adjacent to welds but crack length is less than critical for fracture. Significant yielding and local buckling in beams and columns adjacent to gusset. | Fracture of brace or gusset. Buckling of gusset. Severe yielding of beams and columns adjacent to the gusset with possibility of local buckling and cracking in the yielded areas. Nearly total loss of lateral resistance. |  |  | 1 | 1 | 1 |  |  | 0.00159 | 0.01 | 0.01776 |  |  | 0.65 | 0.15 | 0.4 |  |  | 0.25 | 0.25 | 0.25 |  |  | 0.7 | 0.3 | 0.3 |  |  | NO | YES | Average | Average | Average | Average | Brace damage is largely aesthetic. Heat straightening may be desirable but replacement would be for aesthetic reasons. Gusset has minor loss of strength and stiffness and straightening or repair may be desirable aesthetic reasons. | Brace has lost significant axial capacity, and replacement of braces is likely required. The gusset plate may have significant deformation and replacement may also be needed. Local beam and column yielding has occurred and straightening may be desirable for aesthetic reasons. | Brace and gusset are severely damaged with significant loss in stiffness and resistance, and both likely require replacement. Yielding and local buckling of beams and columns may be repaired by heat straightening, stiffeners or reinforcement, if there is no cracking or tearing. If cracking or tearing has initiated more substantial repair is needed |  |  | NO | NO | NO |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | YES | YES | YES |  |  | 60% | 40% | 20% |  |  | 0.5 | 0.5 | 0.5 |  |  | None | Not Given | By User | By User | Not Given | none | none | none |  |  | No | 2011-08-24 DS3 beta changed from 0.5 to 0.30 to avoid negative probability. 2016-08-17 time consequence adjusted to avoid decreasing consequence with increasing member weight. | YES
B1033.061c | B1033.061c | Ordinary Concentric Braced Frame, braces design to ductile slenderness limits, Chevron Brace, Brace w > 100 PLF | Costing on a per bay basis, equivalent to AISC OCBF criteria. Braces may be HSS, WF, or Angle. Costing does not include fireproofing removal or reapplication cost. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 64 | EA 1 | YES | NO | Buckling of brace in excess of the brace depth. Initiation of yielding and out-of-plane deformation of the gusset. Initiation of cracking of welds of gusset. Initiation of yielding in beams and columns adjacent to gusset. | Buckling of brace in excess of 2 time brace depth. Yielding and out-of-plane deformation of gusset. Cracking and tearing of welds and gussets adjacent to welds but crack length is less than critical for fracture. Significant yielding and local buckling in beams and columns adjacent to gusset. | Fracture of brace or gusset. Buckling of gusset. Severe yielding of beams and columns adjacent to the gusset with possibility of local buckling and cracking in the yielded areas. Nearly total loss of lateral resistance. |  |  | 1 | 1 | 1 |  |  | 0.00159 | 0.01 | 0.01776 |  |  | 0.65 | 0.15 | 0.4 |  |  | 0.25 | 0.25 | 0.25 |  |  | 0.7 | 0.3 | 0.3 |  |  | NO | YES | Average | Average | Average | Average | Brace damage is largely aesthetic. Heat straightening may be desirable but replacement would be for aesthetic reasons. Gusset has minor loss of strength and stiffness and straightening or repair may be desirable aesthetic reasons. | Brace has lost significant axial capacity, and replacement of braces is likely required. The gusset plate may have significant deformation and replacement may also be needed. Local beam and column yielding has occurred and straightening may be desirable for aesthetic reasons. | Brace and gusset are severely damaged with significant loss in stiffness and resistance, and both likely require replacement. Yielding and local buckling of beams and columns may be repaired by heat straightening, stiffeners or reinforcement, if there is no cracking or tearing. If cracking or tearing has initiated more substantial repair is needed |  |  | NO | NO | NO |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | YES | YES | YES |  |  | 60% | 40% | 20% |  |  | 0.5 | 0.5 | 0.5 |  |  | None | Not Given | By User | By User | Not Given | none | none | none |  |  | No | 2011-08-24 DS3 beta changed from 0.5 to 0.30 to avoid negative probability. 2016-08-17 time consequence adjusted to avoid decreasing consequence with increasing member weight. | YES
B1033.062a | B1033.062a | Ordinary Concentric Braced Frame, braces design to ductile slenderness limits, Single Diagonal Brace, Brace w < 40 PLF | Costing on a per bay basis, equivalent to AISC OCBF criteria. Braces may be HSS, WF, or Angle. Costing does not include fireproofing removal or reapplication cost. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 65 | EA 1 | YES | NO | Buckling of brace in excess of the brace depth. Initiation of yielding and out-of-plane deformation of the gusset. Initiation of cracking of welds of gusset. Initiation of yielding in beams and columns adjacent to gusset. | Buckling of brace in excess of 2 time brace depth. Yielding and out-of-plane deformation of gusset. Cracking and tearing of welds and gussets adjacent to welds but crack length is less than critical for fracture. Significant yielding and local buckling in beams and columns adjacent to gusset. | Fracture of brace or gusset. Buckling of gusset. Severe yielding of beams and columns adjacent to the gusset with possibility of local buckling and cracking in the yielded areas. Nearly total loss of lateral resistance. |  |  | 1 | 1 | 1 |  |  | 0.00159 | 0.01 | 0.01776 |  |  | 0.65 | 0.15 | 0.4 |  |  | 0.25 | 0.25 | 0.25 |  |  | 0.7 | 0.3 | 0.3 |  |  | NO | YES | Average | Average | Average | Average | Brace damage is largely aesthetic. Heat straightening may be desirable but replacement would be for aesthetic reasons. Gusset has minor loss of strength and stiffness and straightening or repair may be desirable aesthetic reasons. | Brace has lost significant axial capacity, and replacement of braces is likely required. The gusset plate may have significant deformation and replacement may also be needed. Local beam and column yielding has occurred and straightening may be desirable for aesthetic reasons. | Brace and gusset are severely damaged with significant loss in stiffness and resistance, and both likely require replacement. Yielding and local buckling of beams and columns may be repaired by heat straightening, stiffeners or reinforcement, if there is no cracking or tearing. If cracking or tearing has initiated more substantial repair is needed |  |  | NO | NO | NO |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | YES | YES | YES |  |  | 60% | 40% | 20% |  |  | 0.5 | 0.5 | 0.5 |  |  | None | Not Given | By User | By User | Not Given | none | none | none |  |  | No | 2011-08-24 DS3 beta changed from 0.5 to 0.30 to avoid negative probability. 2016-08-17 time consequence adjusted to avoid decreasing consequence with increasing member weight. | YES
B1033.062b | B1033.062b | Ordinary Concentric Braced Frame, braces design to ductile slenderness limits, Single Diagonal Brace, Brace 41 PLF < w < 99 PLF | Costing on a per bay basis, equivalent to AISC OCBF criteria. Braces may be HSS, WF, or Angle. Costing does not include fireproofing removal or reapplication cost. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 66 | EA 1 | YES | NO | Buckling of brace in excess of the brace depth. Initiation of yielding and out-of-plane deformation of the gusset. Initiation of cracking of welds of gusset. Initiation of yielding in beams and columns adjacent to gusset. | Buckling of brace in excess of 2 time brace depth. Yielding and out-of-plane deformation of gusset. Cracking and tearing of welds and gussets adjacent to welds but crack length is less than critical for fracture. Significant yielding and local buckling in beams and columns adjacent to gusset. | Fracture of brace or gusset. Buckling of gusset. Severe yielding of beams and columns adjacent to the gusset with possibility of local buckling and cracking in the yielded areas. Nearly total loss of lateral resistance. |  |  | 1 | 1 | 1 |  |  | 0.00159 | 0.01 | 0.01776 |  |  | 0.65 | 0.15 | 0.4 |  |  | 0.25 | 0.25 | 0.25 |  |  | 0.7 | 0.3 | 0.3 |  |  | NO | YES | Average | Average | Average | Average | Brace damage is largely aesthetic. Heat straightening may be desirable but replacement would be for aesthetic reasons. Gusset has minor loss of strength and stiffness and straightening or repair may be desirable aesthetic reasons. | Brace has lost significant axial capacity, and replacement of braces is likely required. The gusset plate may have significant deformation and replacement may also be needed. Local beam and column yielding has occurred and straightening may be desirable for aesthetic reasons. | Brace and gusset are severely damaged with significant loss in stiffness and resistance, and both likely require replacement. Yielding and local buckling of beams and columns may be repaired by heat straightening, stiffeners or reinforcement, if there is no cracking or tearing. If cracking or tearing has initiated more substantial repair is needed |  |  | NO | NO | NO |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | YES | YES | YES |  |  | 60% | 40% | 20% |  |  | 0.5 | 0.5 | 0.5 |  |  | None | Not Given | By User | By User | Not Given | none | none | none |  |  | No | 2011-08-24 DS3 beta changed from 0.5 to 0.30 to avoid negative probability. | YES
B1033.062c | B1033.062c | Ordinary Concentric Braced Frame, braces design to ductile slenderness limits, Single Diagonal Brace, Brace w > 100 PLF | Costing on a per bay basis, equivalent to AISC OCBF criteria. Braces may be HSS, WF, or Angle. Costing does not include fireproofing removal or reapplication cost. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 67 | EA 1 | YES | NO | Buckling of brace in excess of the brace depth. Initiation of yielding and out-of-plane deformation of the gusset. Initiation of cracking of welds of gusset. Initiation of yielding in beams and columns adjacent to gusset. | Buckling of brace in excess of 2 time brace depth. Yielding and out-of-plane deformation of gusset. Cracking and tearing of welds and gussets adjacent to welds but crack length is less than critical for fracture. Significant yielding and local buckling in beams and columns adjacent to gusset. | Fracture of brace or gusset. Buckling of gusset. Severe yielding of beams and columns adjacent to the gusset with possibility of local buckling and cracking in the yielded areas. Nearly total loss of lateral resistance. |  |  | 1 | 1 | 1 |  |  | 0.00159 | 0.01 | 0.01776 |  |  | 0.65 | 0.15 | 0.4 |  |  | 0.25 | 0.25 | 0.25 |  |  | 0.7 | 0.3 | 0.3 |  |  | NO | YES | Average | Average | Average | Average | Brace damage is largely aesthetic. Heat straightening may be desirable but replacement would be for aesthetic reasons. Gusset has minor loss of strength and stiffness and straightening or repair may be desirable aesthetic reasons. | Brace has lost significant axial capacity, and replacement of braces is likely required. The gusset plate may have significant deformation and replacement may also be needed. Local beam and column yielding has occurred and straightening may be desirable for aesthetic reasons. | Brace and gusset are severely damaged with significant loss in stiffness and resistance, and both likely require replacement. Yielding and local buckling of beams and columns may be repaired by heat straightening, stiffeners or reinforcement, if there is no cracking or tearing. If cracking or tearing has initiated more substantial repair is needed |  |  | NO | NO | NO |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | YES | YES | YES |  |  | 60% | 40% | 20% |  |  | 0.5 | 0.5 | 0.5 |  |  | None | Not Given | By User | By User | Not Given | none | none | none |  |  | No | 2011-08-24 DS3 beta changed from 0.5 to 0.30 to avoid negative probability. | YES
B1033.063a | B1033.063a | Ordinary Concentric Braced Frame, braces design to ductile slenderness limits, X Brace, Brace w < 40 PLF | Costing on a per bay basis, equivalent to AISC OCBF criteria. Braces may be HSS, WF, or Angle. Costing does not include fireproofing removal or reapplication cost. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 68 | EA 1 | YES | NO | Buckling of brace in excess of the brace depth. Initiation of yielding and out-of-plane deformation of the gusset. Initiation of cracking of welds of gusset. Initiation of yielding in beams and columns adjacent to gusset. | Buckling of brace in excess of 2 time brace depth. Yielding and out-of-plane deformation of gusset. Cracking and tearing of welds and gussets adjacent to welds but crack length is less than critical for fracture. Significant yielding and local buckling in beams and columns adjacent to gusset. | Fracture of brace or gusset. Buckling of gusset. Severe yielding of beams and columns adjacent to the gusset with possibility of local buckling and cracking in the yielded areas. Nearly total loss of lateral resistance. |  |  | 1 | 1 | 1 |  |  | 0.00159 | 0.01 | 0.01776 |  |  | 0.65 | 0.15 | 0.4 |  |  | 0.25 | 0.25 | 0.25 |  |  | 0.7 | 0.3 | 0.3 |  |  | NO | YES | Average | Average | Average | Average | Brace damage is largely aesthetic. Heat straightening may be desirable but replacement would be for aesthetic reasons. Gusset has minor loss of strength and stiffness and straightening or repair may be desirable aesthetic reasons. | Brace has lost significant axial capacity, and replacement of braces is likely required. The gusset plate may have significant deformation and replacement may also be needed. Local beam and column yielding has occurred and straightening may be desirable for aesthetic reasons. | Brace and gusset are severely damaged with significant loss in stiffness and resistance, and both likely require replacement. Yielding and local buckling of beams and columns may be repaired by heat straightening, stiffeners or reinforcement, if there is no cracking or tearing. If cracking or tearing has initiated more substantial repair is needed |  |  | NO | NO | NO |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | YES | YES | YES |  |  | 60% | 40% | 20% |  |  | 0.5 | 0.5 | 0.5 |  |  | None | Not Given | By User | By User | Not Given | none | none | none |  |  | No | 2011-08-24 DS3 beta changed from 0.5 to 0.30 to avoid negative probability. | YES
B1033.063b | B1033.063b | Ordinary Concentric Braced Frame, braces design to ductile slenderness limits, X Brace, Brace 41 PLF < w < 99 PLF | Costing on a per bay basis, equivalent to AISC OCBF criteria. Braces may be HSS, WF, or Angle. Costing does not include fireproofing removal or reapplication cost. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 69 | EA 1 | YES | NO | Buckling of brace in excess of the brace depth. Initiation of yielding and out-of-plane deformation of the gusset. Initiation of cracking of welds of gusset. Initiation of yielding in beams and columns adjacent to gusset. | Buckling of brace in excess of 2 time brace depth. Yielding and out-of-plane deformation of gusset. Cracking and tearing of welds and gussets adjacent to welds but crack length is less than critical for fracture. Significant yielding and local buckling in beams and columns adjacent to gusset. | Fracture of brace or gusset. Buckling of gusset. Severe yielding of beams and columns adjacent to the gusset with possibility of local buckling and cracking in the yielded areas. Nearly total loss of lateral resistance. |  |  | 1 | 1 | 1 |  |  | 0.00159 | 0.01 | 0.01776 |  |  | 0.65 | 0.15 | 0.4 |  |  | 0.25 | 0.25 | 0.25 |  |  | 0.7 | 0.3 | 0.3 |  |  | NO | YES | Average | Average | Average | Average | Brace damage is largely aesthetic. Heat straightening may be desirable but replacement would be for aesthetic reasons. Gusset has minor loss of strength and stiffness and straightening or repair may be desirable aesthetic reasons. | Brace has lost significant axial capacity, and replacement of braces is likely required. The gusset plate may have significant deformation and replacement may also be needed. Local beam and column yielding has occurred and straightening may be desirable for aesthetic reasons. | Brace and gusset are severely damaged with significant loss in stiffness and resistance, and both likely require replacement. Yielding and local buckling of beams and columns may be repaired by heat straightening, stiffeners or reinforcement, if there is no cracking or tearing. If cracking or tearing has initiated more substantial repair is needed |  |  | NO | NO | NO |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | YES | YES | YES |  |  | 60% | 40% | 20% |  |  | 0.5 | 0.5 | 0.5 |  |  | None | Not Given | By User | By User | Not Given | none | none | none |  |  | No | 2011-08-24 DS3 beta changed from 0.5 to 0.30 to avoid negative probability. | YES
B1033.063c | B1033.063c | Ordinary Concentric Braced Frame, braces design to ductile slenderness limits, X Brace, Brace w > 100 PLF | Costing on a per bay basis, equivalent to AISC OCBF criteria. Braces may be HSS, WF, or Angle. Costing does not include fireproofing removal or reapplication cost. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 70 | EA 1 | YES | NO | Buckling of brace in excess of the brace depth. Initiation of yielding and out-of-plane deformation of the gusset. Initiation of cracking of welds of gusset. Initiation of yielding in beams and columns adjacent to gusset. | Buckling of brace in excess of 2 time brace depth. Yielding and out-of-plane deformation of gusset. Cracking and tearing of welds and gussets adjacent to welds but crack length is less than critical for fracture. Significant yielding and local buckling in beams and columns adjacent to gusset. | Fracture of brace or gusset. Buckling of gusset. Severe yielding of beams and columns adjacent to the gusset with possibility of local buckling and cracking in the yielded areas. Nearly total loss of lateral resistance. |  |  | 1 | 1 | 1 |  |  | 0.00159 | 0.01 | 0.01776 |  |  | 0.65 | 0.15 | 0.4 |  |  | 0.25 | 0.25 | 0.25 |  |  | 0.7 | 0.3 | 0.3 |  |  | NO | YES | Average | Average | Average | Average | Brace damage is largely aesthetic. Heat straightening may be desirable but replacement would be for aesthetic reasons. Gusset has minor loss of strength and stiffness and straightening or repair may be desirable aesthetic reasons. | Brace has lost significant axial capacity, and replacement of braces is likely required. The gusset plate may have significant deformation and replacement may also be needed. Local beam and column yielding has occurred and straightening may be desirable for aesthetic reasons. | Brace and gusset are severely damaged with significant loss in stiffness and resistance, and both likely require replacement. Yielding and local buckling of beams and columns may be repaired by heat straightening, stiffeners or reinforcement, if there is no cracking or tearing. If cracking or tearing has initiated more substantial repair is needed |  |  | NO | NO | NO |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | YES | YES | YES |  |  | 60% | 40% | 20% |  |  | 0.5 | 0.5 | 0.5 |  |  | None | Not Given | By User | By User | Not Given | none | none | none |  |  | No | 2011-08-24 DS3 beta changed from 0.5 to 0.30 to avoid negative probability. | YES
B1033.071a | B1033.071a | Braced frame, design for factored loads, no additional seismic detailing, Chevron Brace, Brace w < 40 PLF | Costing on a per bay basis, equivalent to current AISC R=3. Braces may be HSS, WF, or Angle. Costing does not include fireproofing removal or reapplication cost. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 1 | DS1 |  |  |  |  | Sequential |  |  |  |  | Seq(DS1) | 71 | EA 1 | YES | NO | Fracture of brace or gusset. Buckling of gusset. Substantial loss of lateral resistance. |  |  |  |  | 1 |  |  |  |  | 0.0042 |  |  |  |  | Not Specified |  |  |  |  | 0.25 |  |  |  |  | 0.25 |  |  |  |  | NO | YES | Not Rated | Average | Average | Superior | Brace and gusset are severely damaged with significant loss in stiffness and resistance, and both likely require replacement. Yielding and local buckling of beams and columns may be repaired by heat straightening, stiffeners or reinforcement, if there is no cracking or tearing. If cracking or tearing has initiated more substantial repair is needed. |  |  |  |  | NO |  |  |  |  | NO |  |  |  |  | Not Applicable |  |  |  |  | 0% | 0 | [8 empty] | 0% | 0 | [8 empty] | YES |  |  |  |  | 20% |  |  |  |  | 0.5 |  |  |  |  | Performance data has 1 damage state where as the cost data has 3 damage states. The performance data listed in DS1 appears to correspond to the cost data currently shown in DS3… Please confirm if two additional damage state performances should be added or if only one cost damage state should be included. | Not Given | By User | By User | Not Given | none |  |  |  |  | No | 2016-08-17 time consequence adjusted to avoid decreasing consequence with increasing member weight. | YES
B1033.071b | B1033.071b | Braced frame, design for factored loads, no additional seismic detailing, Chevron Brace, 41 PLF < w < 99 PLF | Costing on a per bay basis, equivalent to current AISC R=3. Braces may be HSS, WF, or Angle. Costing does not include fireproofing removal or reapplication cost. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 1 | DS1 |  |  |  |  | Sequential |  |  |  |  | Seq(DS1) | 72 | EA 1 | YES | NO | Fracture of brace or gusset. Buckling of gusset. Substantial loss of lateral resistance. |  |  |  |  | 1 |  |  |  |  | 0.0042 |  |  |  |  | Not Specified |  |  |  |  | 0.25 |  |  |  |  | 0.25 |  |  |  |  | NO | YES | Not Rated | Average | Average | Superior | Brace and gusset are severely damaged with significant loss in stiffness and resistance, and both likely require replacement. Yielding and local buckling of beams and columns may be repaired by heat straightening, stiffeners or reinforcement, if there is no cracking or tearing. If cracking or tearing has initiated more substantial repair is needed. |  |  |  |  | NO |  |  |  |  | NO |  |  |  |  | Not Applicable |  |  |  |  | 0% | 0 | [8 empty] | 0% | 0 | [8 empty] | YES |  |  |  |  | 20% |  |  |  |  | 0.5 |  |  |  |  | Performance data has 1 damage state where as the cost data has 3 damage states. The performance data listed in DS1 appears to correspond to the cost data currently shown in DS3… Please confirm if two additional damage state performances should be added or if only one cost damage state should be included. | Not Given | By User | By User | Not Given | none |  |  |  |  | No | 2016-08-17 time consequence adjusted to avoid decreasing consequence with increasing member weight. | YES
B1033.071c | B1033.071c | Braced frame, design for factored loads, no additional seismic detailing, Chevron Brace, Brace w > 100 PLF | Costing on a per bay basis, equivalent to current AISC R=3. Braces may be HSS, WF, or Angle. Costing does not include fireproofing removal or reapplication cost. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 1 | DS1 |  |  |  |  | Sequential |  |  |  |  | Seq(DS1) | 73 | EA 1 | YES | NO | Fracture of brace or gusset. Buckling of gusset. Substantial loss of lateral resistance. |  |  |  |  | 1 |  |  |  |  | 0.0042 |  |  |  |  | Not Specified |  |  |  |  | 0.25 |  |  |  |  | 0.25 |  |  |  |  | NO | YES | Not Rated | Average | Average | Superior | Brace and gusset are severely damaged with significant loss in stiffness and resistance, and both likely require replacement. Yielding and local buckling of beams and columns may be repaired by heat straightening, stiffeners or reinforcement, if there is no cracking or tearing. If cracking or tearing has initiated more substantial repair is needed. |  |  |  |  | NO |  |  |  |  | NO |  |  |  |  | Not Applicable |  |  |  |  | 0% | 0 | [8 empty] | 0% | 0 | [8 empty] | YES |  |  |  |  | 20% |  |  |  |  | 0.5 |  |  |  |  | Performance data has 1 damage state where as the cost data has 3 damage states. The performance data listed in DS1 appears to correspond to the cost data currently shown in DS3… Please confirm if two additional damage state performances should be added or if only one cost damage state should be included. | Not Given | By User | By User | Not Given | none |  |  |  |  | No | 2016-08-17 time consequence adjusted to avoid decreasing consequence with increasing member weight. | YES
B1033.072a | B1033.072a | Braced frame, design for factored loads, no additional seismic detailing, Single Diagonal Brace, Brace w < 40 PLF | Costing on a per bay basis, equivalent to current AISC R=3. Braces may be HSS, WF, or Angle. Costing does not include fireproofing removal or reapplication cost. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 1 | DS1 |  |  |  |  | Sequential |  |  |  |  | Seq(DS1) | 74 | EA 1 | YES | NO | Fracture of brace or gusset. Buckling of gusset. Substantial loss of lateral resistance. |  |  |  |  | 1 |  |  |  |  | 0.0042 |  |  |  |  | Not Specified |  |  |  |  | 0.25 |  |  |  |  | 0.25 |  |  |  |  | NO | YES | Not Rated | Average | Average | Superior | Brace and gusset are severely damaged with significant loss in stiffness and resistance, and both likely require replacement. Yielding and local buckling of beams and columns may be repaired by heat straightening, stiffeners or reinforcement, if there is no cracking or tearing. If cracking or tearing has initiated more substantial repair is needed. |  |  |  |  | NO |  |  |  |  | NO |  |  |  |  | Not Applicable |  |  |  |  | 0% | 0 | [8 empty] | 0% | 0 | [8 empty] | YES |  |  |  |  | 20% |  |  |  |  | 0.5 |  |  |  |  | Performance data has 1 damage state where as the cost data has 3 damage states. The performance data listed in DS1 appears to correspond to the cost data currently shown in DS3… Please confirm if two additional damage state performances should be added or if only one cost damage state should be included. | Not Given | By User | By User | Not Given | none |  |  |  |  | No | 2016-08-17 time consequence adjusted to avoid decreasing consequence with increasing member weight. | YES
B1033.072b | B1033.072b | Braced frame, design for factored loads, no additional seismic detailing, Single Diagonal Brace, 41 PLF < w < 99 PLF | Costing on a per bay basis, equivalent to current AISC R=3. Braces may be HSS, WF, or Angle. Costing does not include fireproofing removal or reapplication cost. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 1 | DS1 |  |  |  |  | Sequential |  |  |  |  | Seq(DS1) | 75 | EA 1 | YES | NO | Fracture of brace or gusset. Buckling of gusset. Substantial loss of lateral resistance. |  |  |  |  | 1 |  |  |  |  | 0.0042 |  |  |  |  | Not Specified |  |  |  |  | 0.25 |  |  |  |  | 0.25 |  |  |  |  | NO | YES | Not Rated | Average | Average | Superior | Brace and gusset are severely damaged with significant loss in stiffness and resistance, and both likely require replacement. Yielding and local buckling of beams and columns may be repaired by heat straightening, stiffeners or reinforcement, if there is no cracking or tearing. If cracking or tearing has initiated more substantial repair is needed. |  |  |  |  | NO |  |  |  |  | NO |  |  |  |  | Not Applicable |  |  |  |  | 0% | 0 | [8 empty] | 0% | 0 | [8 empty] | YES |  |  |  |  | 20% |  |  |  |  | 0.5 |  |  |  |  | Performance data has 1 damage state where as the cost data has 3 damage states. The performance data listed in DS1 appears to correspond to the cost data currently shown in DS3… Please confirm if two additional damage state performances should be added or if only one cost damage state should be included. | Not Given | By User | By User | Not Given | none |  |  |  |  | No | 2016-08-17 time consequence adjusted to avoid decreasing consequence with increasing member weight. | YES
B1033.072c | B1033.072c | Braced frame, design for factored loads, no additional seismic detailing, Single Diagonal Brace, Brace w > 100 PLF | Costing on a per bay basis, equivalent to current AISC R=3. Braces may be HSS, WF, or Angle. Costing does not include fireproofing removal or reapplication cost. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 1 | DS1 |  |  |  |  | Sequential |  |  |  |  | Seq(DS1) | 76 | EA 1 | YES | NO | Fracture of brace or gusset. Buckling of gusset. Substantial loss of lateral resistance. |  |  |  |  | 1 |  |  |  |  | 0.0042 |  |  |  |  | Not Specified |  |  |  |  | 0.25 |  |  |  |  | 0.25 |  |  |  |  | NO | YES | Not Rated | Average | Average | Superior | Brace and gusset are severely damaged with significant loss in stiffness and resistance, and both likely require replacement. Yielding and local buckling of beams and columns may be repaired by heat straightening, stiffeners or reinforcement, if there is no cracking or tearing. If cracking or tearing has initiated more substantial repair is needed. |  |  |  |  | NO |  |  |  |  | NO |  |  |  |  | Not Applicable |  |  |  |  | 0% | 0 | [8 empty] | 0% | 0 | [8 empty] | YES |  |  |  |  | 20% |  |  |  |  | 0.5 |  |  |  |  | Performance data has 1 damage state where as the cost data has 3 damage states. The performance data listed in DS1 appears to correspond to the cost data currently shown in DS3… Please confirm if two additional damage state performances should be added or if only one cost damage state should be included. | Not Given | By User | By User | Not Given | none |  |  |  |  | No | 2016-08-17 time consequence adjusted to avoid decreasing consequence with increasing member weight. | YES
B1033.073a | B1033.073a | Braced frame, design for factored loads, no additional seismic detailing, X Brace, Brace w < 40 PLF | Costing on a per bay basis, equivalent to current AISC R=3. Braces may be HSS, WF, or Angle. Costing does not include fireproofing removal or reapplication cost. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 1 | DS1 |  |  |  |  | Sequential |  |  |  |  | Seq(DS1) | 77 | EA 1 | YES | NO | Fracture of brace or gusset. Buckling of gusset. Substantial loss of lateral resistance. |  |  |  |  | 1 |  |  |  |  | 0.0042 |  |  |  |  | Not Specified |  |  |  |  | 0.25 |  |  |  |  | 0.25 |  |  |  |  | NO | YES | Not Rated | Average | Average | Superior | Brace and gusset are severely damaged with significant loss in stiffness and resistance, and both likely require replacement. Yielding and local buckling of beams and columns may be repaired by heat straightening, stiffeners or reinforcement, if there is no cracking or tearing. If cracking or tearing has initiated more substantial repair is needed. |  |  |  |  | NO |  |  |  |  | NO |  |  |  |  | Not Applicable |  |  |  |  | 0% | 0 | [8 empty] | 0% | 0 | [8 empty] | YES |  |  |  |  | 20% |  |  |  |  | 0.5 |  |  |  |  | Performance data has 1 damage state where as the cost data has 3 damage states. The performance data listed in DS1 appears to correspond to the cost data currently shown in DS3… Please confirm if two additional damage state performances should be added or if only one cost damage state should be included. | Not Given | By User | By User | Not Given | none |  |  |  |  | No | 2016-08-17 time consequence adjusted to avoid decreasing consequence with increasing member weight. | YES
B1033.073b | B1033.073b | Braced frame, design for factored loads, no additional seismic detailing, X Brace, Brace 41 PLF < w < 99 PLF | Costing on a per bay basis, equivalent to current AISC R=3. Braces may be HSS, WF, or Angle. Costing does not include fireproofing removal or reapplication cost. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 1 | DS1 |  |  |  |  | Sequential |  |  |  |  | Seq(DS1) | 78 | EA 1 | YES | NO | Fracture of brace or gusset. Buckling of gusset. Substantial loss of lateral resistance. |  |  |  |  | 1 |  |  |  |  | 0.0042 |  |  |  |  | Not Specified |  |  |  |  | 0.25 |  |  |  |  | 0.25 |  |  |  |  | NO | YES | Not Rated | Average | Average | Superior | Brace and gusset are severely damaged with significant loss in stiffness and resistance, and both likely require replacement. Yielding and local buckling of beams and columns may be repaired by heat straightening, stiffeners or reinforcement, if there is no cracking or tearing. If cracking or tearing has initiated more substantial repair is needed. |  |  |  |  | NO |  |  |  |  | NO |  |  |  |  | Not Applicable |  |  |  |  | 0% | 0 | [8 empty] | 0% | 0 | [8 empty] | YES |  |  |  |  | 20% |  |  |  |  | 0.5 |  |  |  |  | Performance data has 1 damage state where as the cost data has 3 damage states. The performance data listed in DS1 appears to correspond to the cost data currently shown in DS3… Please confirm if two additional damage state performances should be added or if only one cost damage state should be included. | Not Given | By User | By User | Not Given | none |  |  |  |  | No | 2016-08-17 time consequence adjusted to avoid decreasing consequence with increasing member weight. | YES
B1033.073c | B1033.073c | Braced frame, design for factored loads, no additional seismic detailing, X Brace, Brace w > 100 PLF | Costing on a per bay basis, equivalent to current AISC R=3. Braces may be HSS, WF, or Angle. Costing does not include fireproofing removal or reapplication cost. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 1 | DS1 |  |  |  |  | Sequential |  |  |  |  | Seq(DS1) | 79 | EA 1 | YES | NO | Fracture of brace or gusset. Buckling of gusset. Substantial loss of lateral resistance. |  |  |  |  | 1 |  |  |  |  | 0.0042 |  |  |  |  | Not Specified |  |  |  |  | 0.25 |  |  |  |  | 0.25 |  |  |  |  | NO | YES | Not Rated | Average | Average | Superior | Brace and gusset are severely damaged with significant loss in stiffness and resistance, and both likely require replacement. Yielding and local buckling of beams and columns may be repaired by heat straightening, stiffeners or reinforcement, if there is no cracking or tearing. If cracking or tearing has initiated more substantial repair is needed. |  |  |  |  | NO |  |  |  |  | NO |  |  |  |  | Not Applicable |  |  |  |  | 0% | 0 | [8 empty] | 0% | 0 | [8 empty] | YES |  |  |  |  | 20% |  |  |  |  | 0.5 |  |  |  |  | Performance data has 1 damage state where as the cost data has 3 damage states. The performance data listed in DS1 appears to correspond to the cost data currently shown in DS3… Please confirm if two additional damage state performances should be added or if only one cost damage state should be included. | Not Given | By User | By User | Not Given | none |  |  |  |  | No | 2016-08-17 time consequence adjusted to avoid decreasing consequence with increasing member weight. | YES
B1033.101a | B1033.101a | Steel Buckling Restrained Brace (BRB), Chevron Brace, Weight of brace < 40 plf. | None | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 1 | DS1 |  |  |  |  | Sequential |  |  |  |  | Seq(DS1) | 80 | EA 1 | YES | NO | Fracture of brace or gusset. Buckling of gusset. Severe yielding of beams and columns adjacent to the gusset with possibility of local buckling and cracking in the yielded areas. Severe loss of lateral resistance. |  |  |  |  | 1 |  |  |  |  | 0.02 |  |  |  |  | Not Specified |  |  |  |  | Not Specified |  |  |  |  | 0.4 |  |  |  |  | NO | YES | Not Rated | Not Rated | Not Rated | Not Rated | Brace and gusset are severely damaged with significant loss in stiffness and resistance, and both likely require replacement. Yielding and local buckling of beams and columns may be repaired by heat straightening, stiffeners or reinforcement, if there is no cracking or tearing. If cracking or tearing has initiated more substantial repair is needed. |  |  |  |  | NO |  |  |  |  | NO |  |  |  |  | Not Applicable |  |  |  |  | 0% | 0 | [8 empty] | 0% | 0 | [8 empty] | NO |  |  |  |  | 0% |  |  |  |  | 0 |  |  |  |  | None | Not Given | By User | By User | John Wallace | none |  |  |  |  | No | 2016-08-17 time consequence adjusted to avoid decreasing consequence with increasing member weight. Median demand established from PEER TBI project. | YES
B1033.101b | B1033.101b | Steel Buckling Restrained Brace (BRB), Chevron brace, Weight of brace > 41 plf and < 99 plf. | None | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 1 | DS1 |  |  |  |  | Sequential |  |  |  |  | Seq(DS1) | 81 | EA 1 | YES | NO | Fracture of brace or gusset. Buckling of gusset. Severe yielding of beams and columns adjacent to the gusset with possibility of local buckling and cracking in the yielded areas. Severe loss of lateral resistance. |  |  |  |  | 1 |  |  |  |  | 0.02 |  |  |  |  | Not Specified |  |  |  |  | Not Specified |  |  |  |  | 0.4 |  |  |  |  | NO | YES | Not Rated | Not Rated | Not Rated | Not Rated | Brace and gusset are severely damaged with significant loss in stiffness and resistance, and both likely require replacement. Yielding and local buckling of beams and columns may be repaired by heat straightening, stiffeners or reinforcement, if there is no cracking or tearing. If cracking or tearing has initiated more substantial repair is needed. |  |  |  |  | NO |  |  |  |  | NO |  |  |  |  | Not Applicable |  |  |  |  | 0% | 0 | [8 empty] | 0% | 0 | [8 empty] | NO |  |  |  |  | 0% |  |  |  |  | 0 |  |  |  |  | None | Not Given | By User | By User | John Wallace | none |  |  |  |  | No | 2016-08-17 time consequence adjusted to avoid decreasing consequence with increasing member weight. Median demand established from PEER TBI project. | YES
B1033.101c | B1033.101c | Steel Buckling Restrained Brace (BRB), Chevron Brace, Weight of brace > 100 plf. | None | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 1 | DS1 |  |  |  |  | Sequential |  |  |  |  | Seq(DS1) | 82 | EA 1 | YES | NO | Fracture of brace or gusset. Buckling of gusset. Severe yielding of beams and columns adjacent to the gusset with possibility of local buckling and cracking in the yielded areas. Severe loss of lateral resistance. |  |  |  |  | 1 |  |  |  |  | 0.02 |  |  |  |  | Not Specified |  |  |  |  | Not Specified |  |  |  |  | 0.4 |  |  |  |  | NO | YES | Not Rated | Not Rated | Not Rated | Not Rated | Brace and gusset are severely damaged with significant loss in stiffness and resistance, and both likely require replacement. Yielding and local buckling of beams and columns may be repaired by heat straightening, stiffeners or reinforcement, if there is no cracking or tearing. If cracking or tearing has initiated more substantial repair is needed. |  |  |  |  | NO |  |  |  |  | NO |  |  |  |  | Not Applicable |  |  |  |  | 0% | 0 | [8 empty] | 0% | 0 | [8 empty] | NO |  |  |  |  | 0% |  |  |  |  | 0 |  |  |  |  | None | Not Given | By User | By User | John Wallace | none |  |  |  |  | No | 2016-08-17 time consequence adjusted to avoid decreasing consequence with increasing member weight. Median demand established from PEER TBI project. | YES
B1033.111a | B1033.111a | Steel Buckling Restrained Brace (BRB), Single Diagonal Brace, Weight of brace < 40 plf. | None | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 1 | DS1 |  |  |  |  | Sequential |  |  |  |  | Seq(DS1) | 83 | EA 1 | YES | NO | Fracture of brace or gusset. Buckling of gusset. Severe yielding of beams and columns adjacent to the gusset with possibility of local buckling and cracking in the yielded areas. Severe loss of lateral resistance. |  |  |  |  | 1 |  |  |  |  | 0.02 |  |  |  |  | Not Specified |  |  |  |  | Not Specified |  |  |  |  | 0.4 |  |  |  |  | NO | YES | Not Rated | Not Rated | Not Rated | Not Rated | Brace and gusset are severely damaged with significant loss in stiffness and resistance, and both likely require replacement. Yielding and local buckling of beams and columns may be repaired by heat straightening, stiffeners or reinforcement, if there is no cracking or tearing. If cracking or tearing has initiated more substantial repair is needed. |  |  |  |  | NO |  |  |  |  | NO |  |  |  |  | Not Applicable |  |  |  |  | 0% | 0 | [8 empty] | 0% | 0 | [8 empty] | NO |  |  |  |  | 0% |  |  |  |  | 0 |  |  |  |  | None | Not Given | By User | By User | John Wallace | none |  |  |  |  | No | 2016-08-17 time consequence adjusted to avoid decreasing consequence with increasing member weight. Median demand established from PEER TBI project. | YES
B1033.111b | B1033.111b | Steel Buckling Restrained Brace (BRB), Single Diagonal brace, Weight of brace > 41 plf and < 99 plf. | None | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 1 | DS1 |  |  |  |  | Sequential |  |  |  |  | Seq(DS1) | 84 | EA 1 | YES | NO | Fracture of brace or gusset. Buckling of gusset. Severe yielding of beams and columns adjacent to the gusset with possibility of local buckling and cracking in the yielded areas. Severe loss of lateral resistance. |  |  |  |  | 1 |  |  |  |  | 0.02 |  |  |  |  | Not Specified |  |  |  |  | Not Specified |  |  |  |  | 0.4 |  |  |  |  | NO | YES | Not Rated | Not Rated | Not Rated | Not Rated | Brace and gusset are severely damaged with significant loss in stiffness and resistance, and both likely require replacement. Yielding and local buckling of beams and columns may be repaired by heat straightening, stiffeners or reinforcement, if there is no cracking or tearing. If cracking or tearing has initiated more substantial repair is needed. |  |  |  |  | NO |  |  |  |  | NO |  |  |  |  | Not Applicable |  |  |  |  | 0% | 0 | [8 empty] | 0% | 0 | [8 empty] | NO |  |  |  |  | 0% |  |  |  |  | 0 |  |  |  |  | None | Not Given | By User | By User | John Wallace | none |  |  |  |  | No | 2016-08-17 time consequence adjusted to avoid decreasing consequence with increasing member weight. Median demand established from PEER TBI project. | YES
B1033.111c | B1033.111c | Steel Buckling Restrained Brace (BRB), Single Diagonal Brace, Weight of brace > 100 plf. | None | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 1 | DS1 |  |  |  |  | Sequential |  |  |  |  | Seq(DS1) | 85 | EA 1 | YES | NO | Fracture of brace or gusset. Buckling of gusset. Severe yielding of beams and columns adjacent to the gusset with possibility of local buckling and cracking in the yielded areas. Severe loss of lateral resistance. |  |  |  |  | 1 |  |  |  |  | 0.02 |  |  |  |  | Not Specified |  |  |  |  | Not Specified |  |  |  |  | 0.4 |  |  |  |  | NO | YES | Not Rated | Not Rated | Not Rated | Not Rated | Brace and gusset are severely damaged with significant loss in stiffness and resistance, and both likely require replacement. Yielding and local buckling of beams and columns may be repaired by heat straightening, stiffeners or reinforcement, if there is no cracking or tearing. If cracking or tearing has initiated more substantial repair is needed. |  |  |  |  | NO |  |  |  |  | NO |  |  |  |  | Not Applicable |  |  |  |  | 0% | 0 | [8 empty] | 0% | 0 | [8 empty] | NO |  |  |  |  | 0% |  |  |  |  | 0 |  |  |  |  | None | Not Given | By User | By User | John Wallace | none |  |  |  |  | No | 2016-08-17 time consequence adjusted to avoid decreasing consequence with increasing member weight. Median demand established from PEER TBI project. | YES
B1035.001 | B1035.001 | Post-Northridge RBS connection with welded web, beam one side of column only, beam depth <= W27 | Costing is on a per bay basis. Costing does not include fireproofing removal or reapplication cost. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 86 | EA 1 | YES | NO | Local beam flange and web buckling. | DS1 plus lateral-torsional distortion of beam in hinge region. | Low-cycle fatigue fracture in buckled region of RBS. |  |  | 1 | 1 | 1 |  |  | 0.03 | 0.04 | 0.05 |  |  | Not Specified | Not Specified | Not Specified |  |  | 0.3 | 0.3 | 0.3 |  |  | 0.3 | 0.3 | 0.3 |  |  | NO | YES | Superior | Average | Superior | Superior | The likely repair state is heat straightening of the buckled flanges and web. Repair and replace partitions at connection. | Repair will necessitate removal and replacement of distorted and or fractured portion of beam. Repair and replace partitions at connection. | Repair will necessitate removal and replacement of distorted and/or fractured portion of beam. Repair and replace partitions at connection. |  |  | NO | NO | NO |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | YES | YES |  |  | 0% | 50% | 50% |  |  | 0 | 0.5 | 0.5 |  |  | None | Not Given | By User | By User | Greg Deierlein | none | none | none |  |  | No | None | YES
B1035.002 | B1035.002 | Post-Northridge RBS connection with welded web, beam one side of column only, beam depth >= W30 | Costing is on a per bay basis. Costing does not include fireproofing removal or reapplication cost. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 87 | EA 1 | YES | NO | Local beam flange and web buckling. | DS1 plus lateral-torsional distortion of beam in hinge region. | Low-cycle fatigue fracture in buckled region of RBS. |  |  | 1 | 1 | 1 |  |  | 0.03 | 0.04 | 0.05 |  |  | Not Specified | Not Specified | Not Specified |  |  | 0.3 | 0.3 | 0.3 |  |  | 0.3 | 0.3 | 0.3 |  |  | NO | YES | Superior | Average | Superior | Superior | The likely repair state is heat straightening of the buckled flanges and web. Repair and replace partitions at connection. | Repair will necessitate removal and replacement of distorted and or fractured portion of beam. Repair and replace partitions at connection. | Repair will necessitate removal and replacement of distorted and/or fractured portion of beam. Repair and replace partitions at connection. |  |  | NO | NO | NO |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | YES | YES |  |  | 0% | 50% | 50% |  |  | 0 | 0.5 | 0.5 |  |  | None | Not Given | By User | By User | Greg Deierlein | none | none | none |  |  | No | None | YES
B1035.011 | B1035.011 | Post-Northridge RBS connection with welded web, beams both sides of column, beam depth <= W27 | Costing is on a per bay basis. Costing does not include fireproofing removal or reapplication cost. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 88 | EA 1 | YES | NO | Local beam flange and web buckling. | DS1 plus lateral-torsional distortion of beam in hinge region. | Low-cycle fatigue fracture in buckled region of RBS. |  |  | 1 | 1 | 1 |  |  | 0.03 | 0.04 | 0.05 |  |  | Not Specified | Not Specified | Not Specified |  |  | 0.3 | 0.3 | 0.3 |  |  | 0.3 | 0.3 | 0.3 |  |  | NO | YES | Superior | Average | Superior | Superior | The likely repair state is heat straightening of the buckled flanges and web. Repair and replace partitions at connection. | Repair will necessitate removal and replacement of distorted and or fractured portion of beam. Repair and replace partitions at connection. | Repair will necessitate removal and replacement of distorted and/or fractured portion of beam. Repair and replace partitions at connection. |  |  | NO | NO | NO |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | YES | YES |  |  | 0% | 50% | 50% |  |  | 0 | 0.5 | 0.5 |  |  | None | Not Given | By User | By User | Greg Deierlein | none | none | none |  |  | No | None | YES
B1035.012 | B1035.012 | Post-Northridge RBS connection with welded web, beams both sides of column, beam depth >= W30 | Costing is on a per bay basis. Costing does not include fireproofing removal or reapplication cost. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 89 | EA 1 | YES | NO | Local beam flange and web buckling. | DS1 plus lateral-torsional distortion of beam in hinge region. | Low-cycle fatigue fracture in buckled region of RBS. |  |  | 1 | 1 | 1 |  |  | 0.03 | 0.04 | 0.05 |  |  | Not Specified | Not Specified | Not Specified |  |  | 0.3 | 0.3 | 0.3 |  |  | 0.3 | 0.3 | 0.3 |  |  | NO | YES | Superior | Average | Superior | Superior | The likely repair state is heat straightening of the buckled flanges and web. Repair and replace partitions at connection. | Repair will necessitate removal and replacement of distorted and or fractured portion of beam. Repair and replace partitions at connection. | Repair will necessitate removal and replacement of distorted and/or fractured portion of beam. Repair and replace partitions at connection. |  |  | NO | NO | NO |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | YES | YES |  |  | 0% | 50% | 50% |  |  | 0 | 0.5 | 0.5 |  |  | None | Not Given | By User | By User | Greg Deierlein | none | none | none |  |  | No | None | YES
B1035.021 | B1035.021 | Post-Northridge welded steel moment connection other than RBS, beam one side, beam depth <= W27 | Costing is on a per bay basis. Costing does not include fireproofing removal or reapplication cost. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 90 | EA 1 | YES | NO | Local beam flange and web buckling. | DS1 plus lateral-torsional distortion of beam in hinge region. | Low-cycle fatigue fracture in buckled region of RBS. |  |  | 1 | 1 | 1 |  |  | 0.03 | 0.04 | 0.05 |  |  | Not Specified | Not Specified | Not Specified |  |  | 0.3 | 0.3 | 0.3 |  |  | 0.3 | 0.3 | 0.3 |  |  | NO | YES | Superior | Average | Superior | Superior | The likely repair state is heat straightening of the buckled flanges and web. Repair and replace partitions at connection. | Repair will necessitate removal and replacement of distorted and or fractured portion of beam. Repair and replace partitions at connection. | Repair will necessitate removal and replacement of distorted and/or fractured portion of beam. Repair and replace partitions at connection. |  |  | NO | NO | NO |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | YES | YES |  |  | 0% | 50% | 50% |  |  | 0 | 0.5 | 0.5 |  |  | None | Not Given | By User | By User | Greg Deierlein | none | none | none |  |  | No | None | YES
B1035.022 | B1035.022 | Post-Northridge welded steel moment connection other than RBS, beam one side, beam depth >= W30 | Costing is on a per bay basis. Costing does not include fireproofing removal or reapplication cost. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 91 | EA 1 | YES | NO | Local beam flange and web buckling. | DS1 plus lateral-torsional distortion of beam in hinge region. | Low-cycle fatigue fracture in buckled region of RBS. |  |  | 1 | 1 | 1 |  |  | 0.03 | 0.04 | 0.05 |  |  | Not Specified | Not Specified | Not Specified |  |  | 0.3 | 0.3 | 0.3 |  |  | 0.3 | 0.3 | 0.3 |  |  | NO | YES | Superior | Average | Superior | Superior | The likely repair state is heat straightening of the buckled flanges and web. Repair and replace partitions at connection. | Repair will necessitate removal and replacement of distorted and or fractured portion of beam. Repair and replace partitions at connection. | Repair will necessitate removal and replacement of distorted and/or fractured portion of beam. Repair and replace partitions at connection. |  |  | NO | NO | NO |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | YES | YES |  |  | 0% | 50% | 50% |  |  | 0 | 0.5 | 0.5 |  |  | None | Not Given | By User | By User | Greg Deierlein | none | none | none |  |  | No | None | YES
B1035.031 | B1035.031 | Post-Northridge welded steel moment connection other than RBS, beams both sides, beam depth <= W27 | Costing is on a per bay basis. Costing does not include fireproofing removal or reapplication cost. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 92 | EA 1 | YES | NO | Local beam flange and web buckling. | DS1 plus lateral-torsional distortion of beam in hinge region. | Low-cycle fatigue fracture in buckled region of RBS. |  |  | 1 | 1 | 1 |  |  | 0.03 | 0.04 | 0.05 |  |  | Not Specified | Not Specified | Not Specified |  |  | 0.3 | 0.3 | 0.3 |  |  | 0.3 | 0.3 | 0.3 |  |  | NO | YES | Superior | Average | Superior | Superior | The likely repair state is heat straightening of the buckled flanges and web. Repair and replace partitions at connection. | Repair will necessitate removal and replacement of distorted and or fractured portion of beam. Repair and replace partitions at connection. | Repair will necessitate removal and replacement of distorted and/or fractured portion of beam. Repair and replace partitions at connection. |  |  | NO | NO | NO |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | YES | YES |  |  | 0% | 50% | 50% |  |  | 0 | 0.5 | 0.5 |  |  | None | Not Given | By User | By User | Greg Deierlein | none | none | none |  |  | No | None | YES
B1035.032 | B1035.032 | Post-Northridge welded steel moment connection other than RBS, beams both sides, beam depth >= W30 | Costing is on a per bay basis. Costing does not include fireproofing removal or reapplication cost. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 93 | EA 1 | YES | NO | Local beam flange and web buckling. | DS1 plus lateral-torsional distortion of beam in hinge region. | Low-cycle fatigue fracture in buckled region of RBS. |  |  | 1 | 1 | 1 |  |  | 0.03 | 0.04 | 0.05 |  |  | Not Specified | Not Specified | Not Specified |  |  | 0.3 | 0.3 | 0.3 |  |  | 0.3 | 0.3 | 0.3 |  |  | NO | YES | Superior | Average | Superior | Superior | The likely repair state is heat straightening of the buckled flanges and web. Repair and replace partitions at connection. | Repair will necessitate removal and replacement of distorted and or fractured portion of beam. Repair and replace partitions at connection. | Repair will necessitate removal and replacement of distorted and/or fractured portion of beam. Repair and replace partitions at connection. |  |  | NO | NO | NO |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | YES | YES |  |  | 0% | 50% | 50% |  |  | 0 | 0.5 | 0.5 |  |  | None | Not Given | By User | By User | Greg Deierlein | none | none | none |  |  | No | None | YES
B1035.041 | B1035.041 | Pre-Northridge WUF-B beam-column joint, beam one side of column, beam depth <= W27 | Costing is on a per bay basis. Costing does not include fireproofing removal or reapplication cost. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 5 | DS1 | DS2 | DS3 | DS4 | DS5 | Mutually Exclusive | Mutually Exclusive | Mutually Exclusive | Mutually Exclusive | Sequential | Seq(MutEx(DS1,DS2),MutEx(DS3,DS4),DS5) | 94 | EA 1 | YES | NO | Fracture of lower beam flange weld and failure of web bolts (shear tab connection), with fractures confined to the weld region. | Similar to DS1, except that fracture propagates into column flanges. | Fracture of upper beam flange weld, without DS1 type damage. Fracture is confined to beam flange region. | Similar to DS3, except that fracture propagates into column flanges. | Fracture initiating at weld access hole and propagating through beam flange, possibly accompanied by local buckling deformations of web and flange. | 0.75 | 0.25 | 0.75 | 0.25 | 1 | 0.017 | 0.017 | 0.025 | 0.025 | 0.03 | Not Specified | Not Specified | Not Specified | Not Specified | Not Specified | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | NO | YES | Average | Average | Superior | Superior | Repair will typically require gouging out and re-welding of the beam flange weld, repair of shear tab, and replacing shear bolts. Repair and replace partitions at connection. | In addition to column measures for DS1, repairs to column will be necessary. Cover plate, patch, or replace damaged column flange at connection. | Repairs will be similar to those required for DS1, except that access to weld will likely require removal and replacement of a portion of the floor slab above the weld. | In addition to column measures for DS3, repairs to column will be necessary that will involve replacing a portion of the column flange. | Repair is similar to that for DS1 except that a portion of the beam web and flange may need to be heat straightened or replaced. | NO | NO | NO | NO | NO | NO | NO | NO | NO | NO | Not Applicable | Not Applicable | Not Applicable | Not Applicable | Not Applicable | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | YES | YES | YES | YES | YES | 50% | 50% | 50% | 50% | 50% | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | None | Not Given | By User | By User | Greg Deierlein | B1035.041-DS1-1.JPG | B1035.041-DS2-1.JPG | none | none | none | No | None | YES
B1035.042 | B1035.042 | Pre-Northridge WUF-B beam-column joint, beam one side of column, beam depth >= W30 | Costing is on a per bay basis. Costing does not include fireproofing removal or reapplication cost. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 5 | DS1 | DS2 | DS3 | DS4 | DS5 | Mutually Exclusive | Mutually Exclusive | Mutually Exclusive | Mutually Exclusive | Sequential | Seq(MutEx(DS1,DS2),MutEx(DS3,DS4),DS5) | 95 | EA 1 | YES | NO | Fracture of lower beam flange weld and failure of web bolts (shear tab connection), with fractures confined to the weld region. | Similar to DS1, except that fracture propagates into column flanges. | Fracture of upper beam flange weld, without DS1 type damage. Fracture is confined to beam flange region. | Similar to DS3, except that fracture propagates into column flanges. | Fracture initiating at weld access hole and propagating through beam flange, possibly accompanied by local buckling deformations of web and flange. | 0.75 | 0.25 | 0.75 | 0.25 | 1 | 0.017 | 0.017 | 0.025 | 0.025 | 0.03 | Not Specified | Not Specified | Not Specified | Not Specified | Not Specified | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | NO | YES | Average | Average | Superior | Superior | Repair will typically require gouging out and re-welding of the beam flange weld, repair of shear tab, and replacing shear bolts. Repair and replace partitions at connection. | In addition to column measures for DS1, repairs to column will be necessary. Cover plate, patch, or replace damaged column flange at connection. | Repairs will be similar to those required for DS1, except that access to weld will likely require removal and replacement of a portion of the floor slab above the weld. | In addition to column measures for DS3, repairs to column will be necessary that will involve replacing a portion of the column flange. | Repair is similar to that for DS1 except that a portion of the beam web and flange may need to be heat straightened or replaced. | NO | NO | NO | NO | NO | NO | NO | NO | NO | NO | Not Applicable | Not Applicable | Not Applicable | Not Applicable | Not Applicable | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | YES | YES | YES | YES | YES | 50% | 50% | 50% | 50% | 50% | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | None | Not Given | By User | By User | Greg Deierlein | B1035.041-DS1-1.JPG | B1035.041-DS2-1.JPG | none | none | none | No | None | YES
B1035.051 | B1035.051 | Pre-Northridge WUF-B beam-column joint, beam both sides of column, beam depth <= W27 | Costing is on a per bay basis. Costing does not include fireproofing removal or reapplication cost. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 5 | DS1 | DS2 | DS3 | DS4 | DS5 | Mutually Exclusive | Mutually Exclusive | Mutually Exclusive | Mutually Exclusive | Sequential | Seq(MutEx(DS1,DS2),MutEx(DS3,DS4),DS5) | 96 | EA 1 | YES | NO | Fracture of lower beam flange weld and failure of web bolts (shear tab connection), with fractures confined to the weld region. | Similar to DS1, except that fracture propagates into column flanges. | Fracture of upper beam flange weld, without DS1 type damage. Fracture is confined to beam flange region. | Similar to DS3, except that fracture propagates into column flanges. | Fracture initiating at weld access hole and propagating through beam flange, possibly accompanied by local buckling deformations of web and flange. | 0.75 | 0.25 | 0.75 | 0.25 | 1 | 0.017 | 0.017 | 0.025 | 0.025 | 0.03 | Not Specified | Not Specified | Not Specified | Not Specified | Not Specified | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | NO | YES | Average | Average | Superior | Superior | Repair will typically require gouging out and re-welding of the beam flange weld, repair of shear tab, and replacing shear bolts. Repair and replace partitions at connection. | In addition to column measures for DS1, repairs to column will be necessary. Cover plate, patch, or replace damaged column flange at connection. | Repairs will be similar to those required for DS1, except that access to weld will likely require removal and replacement of a portion of the floor slab above the weld. | In addition to column measures for DS3, repairs to column will be necessary that will involve replacing a portion of the column flange. | Repair is similar to that for DS1 except that a portion of the beam web and flange may need to be heat straightened or replaced. | NO | NO | NO | NO | NO | NO | NO | NO | NO | NO | Not Applicable | Not Applicable | Not Applicable | Not Applicable | Not Applicable | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | YES | YES | YES | YES | YES | 50% | 50% | 50% | 50% | 50% | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | None | Not Given | By User | By User | Greg Deierlein | B1035.041-DS1-1.JPG | B1035.041-DS2-1.JPG | none | none | none | No | None | YES
B1035.052 | B1035.052 | Pre-Northridge WUF-B beam-column joint, beam both sides of column, beam depth >= W30 | Costing is on a per bay basis. Costing does not include fireproofing removal or reapplication cost. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 5 | DS1 | DS2 | DS3 | DS4 | DS5 | Mutually Exclusive | Mutually Exclusive | Mutually Exclusive | Mutually Exclusive | Sequential | Seq(MutEx(DS1,DS2),MutEx(DS3,DS4),DS5) | 97 | EA 1 | YES | NO | Fracture of lower beam flange weld and failure of web bolts (shear tab connection), with fractures confined to the weld region. | Similar to DS1, except that fracture propagates into column flanges. | Fracture of upper beam flange weld, without DS1 type damage. Fracture is confined to beam flange region. | Similar to DS3, except that fracture propagates into column flanges. | Fracture initiating at weld access hole and propagating through beam flange, possibly accompanied by local buckling deformations of web and flange. | 0.75 | 0.25 | 0.75 | 0.25 | 1 | 0.017 | 0.017 | 0.025 | 0.025 | 0.03 | Not Specified | Not Specified | Not Specified | Not Specified | Not Specified | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | NO | YES | Average | Average | Superior | Superior | Repair will typically require gouging out and re-welding of the beam flange weld, repair of shear tab, and replacing shear bolts. Repair and replace partitions at connection. | In addition to column measures for DS1, repairs to column will be necessary. Cover plate, patch, or replace damaged column flange at connection. | Repairs will be similar to those required for DS1, except that access to weld will likely require removal and replacement of a portion of the floor slab above the weld. | In addition to column measures for DS3, repairs to column will be necessary that will involve replacing a portion of the column flange. | Repair is similar to that for DS1 except that a portion of the beam web and flange may need to be heat straightened or replaced. | NO | NO | NO | NO | NO | NO | NO | NO | NO | NO | Not Applicable | Not Applicable | Not Applicable | Not Applicable | Not Applicable | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | YES | YES | YES | YES | YES | 50% | 50% | 50% | 50% | 50% | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | None | Not Given | By User | By User | Greg Deierlein | B1035.041-DS1-1.JPG | B1035.041-DS2-1.JPG | none | none | none | No | None | YES
B1035.061a | B1035.061a | EBF Shear Link, no floor beams, link w < 100 PLF | Costing is on a per connection basis. Costing does not include fireproofing removal or reapplication cost. | Not Specified | Not Specified | Each | Each | Link Rotation Angle | Radians | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 98 | EA 1 | YES | NO | Damage to concrete slab above the link beam. | Web local buckling, flange local buckling. | Initiation of fracture in the link beam and link flange. |  |  | 1 | 1 | 1 |  |  | 0.04 | 0.06 | 0.08 |  |  | Not Specified | Not Specified | Not Specified |  |  | Not Specified | Not Specified | Not Specified |  |  | 0.3 | 0.3 | 0.3 |  |  | NO | YES | Superior | Superior | Superior | Superior | Replace concrete slab and finishes in 400 SF at EBF link. | Heat straightening of buckled elements. | Replace EBF link. |  |  | NO | NO | NO |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | YES | YES |  |  | 0% | 50% | 25% |  |  | 0 | 0.5 | 0.5 |  |  | None | Not Given | By User | By User | Not Given | B1035.061-DS1-1.JPG | B1035.061-DS2-1.JPG | B1035.061-DS3-1.JPG |  |  | No | None | YES
B1035.061b | B1035.061b | EBF Shear Link, no floor beams, link w < 200 PLF | Costing is on a per connection basis. Costing does not include fireproofing removal or reapplication cost. | Not Specified | Not Specified | Each | Each | Link Rotation Angle | Radians | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 99 | EA 1 | YES | NO | Damage to concrete slab above the link beam. | Web local buckling, flange local buckling. | Initiation of fracture in the link beam and link flange. |  |  | 1 | 1 | 1 |  |  | 0.04 | 0.06 | 0.08 |  |  | Not Specified | Not Specified | Not Specified |  |  | Not Specified | Not Specified | Not Specified |  |  | 0.3 | 0.3 | 0.3 |  |  | NO | YES | Superior | Superior | Superior | Superior | Replace concrete slab and finishes in 400 SF at EBF link. | Heat straightening of buckled elements. | Replace EBF link. |  |  | NO | NO | NO |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | YES | YES |  |  | 0% | 50% | 25% |  |  | 0 | 0.5 | 0.5 |  |  | None | Not Given | By User | By User | Not Given | B1035.061-DS1-1.JPG | B1035.061-DS2-1.JPG | B1035.061-DS3-1.JPG |  |  | No | None | YES
B1035.062a | B1035.062a | EBF Shear Link, with floor beams, link w < 100 PLF | Costing is on a per connection basis. Costing does not include fireproofing removal or reapplication cost. | Not Specified | Not Specified | Each | Each | Link Rotation Angle | Radians | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 100 | EA 1 | YES | NO | Damage to concrete slab above the link beam. | Web local buckling, flange local buckling. | Initiation of fracture in the link beam and link flange. |  |  | 1 | 1 | 1 |  |  | 0.04 | 0.06 | 0.08 |  |  | Not Specified | Not Specified | Not Specified |  |  | Not Specified | Not Specified | Not Specified |  |  | 0.3 | 0.3 | 0.3 |  |  | NO | YES | Superior | Superior | Superior | Superior | Replace concrete slab and finishes in 400 SF at EBF link. | Heat straightening of buckled elements. | Replace EBF link. |  |  | NO | NO | NO |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | YES | YES |  |  | 0% | 50% | 25% |  |  | 0 | 0.5 | 0.5 |  |  | None | Not Given | By User | By User | Not Given | B1035.061-DS1-1.JPG | B1035.061-DS2-1.JPG | B1035.061-DS3-1.JPG |  |  | No | None | YES
B1035.062b | B1035.062b | EBF Shear Link, with floor beams, link w < 200 PLF | Costing is on a per connection basis. Costing does not include fireproofing removal or reapplication cost. | Not Specified | Not Specified | Each | Each | Link Rotation Angle | Radians | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 101 | EA 1 | YES | NO | Damage to concrete slab above the link beam. | Web local buckling, flange local buckling. | Initiation of fracture in the link beam and link flange. |  |  | 1 | 1 | 1 |  |  | 0.04 | 0.06 | 0.08 |  |  | Not Specified | Not Specified | Not Specified |  |  | Not Specified | Not Specified | Not Specified |  |  | 0.3 | 0.3 | 0.3 |  |  | NO | YES | Superior | Superior | Superior | Superior | Replace concrete slab and finishes in 400 SF at EBF link. | Heat straightening of buckled elements. | Replace EBF link. |  |  | NO | NO | NO |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | YES | YES |  |  | 0% | 50% | 25% |  |  | 0 | 0.5 | 0.5 |  |  | None | Not Given | By User | By User | Not Given | B1035.061-DS1-1.JPG | B1035.061-DS2-1.JPG | B1035.061-DS3-1.JPG |  |  | No | None | YES
B1041.001a | B1041.001a | ACI 318 SMF , Conc Col & Bm = 24" x 24", Beam one side | ACI318 Concrete SMF, ductile response. Meets the requirements of ACI318 SMF. Costing is on a per joint basis. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 4 | DS1 | DS2 | DS3 | DS4 |  | Sequential | Sequential | Mutually Exclusive | Mutually Exclusive |  | Seq(DS1,DS2,MutEx(DS3,DS4)) | 102 | EA 1 | YES | NO | Beams or joints exhibit residual crack widths > 0.06 in. No significant spalling. No fracture or buckling of reinforcing. | Beams or joints exhibit residual crack widths > 0.06 in. Spalling of cover concrete exposes beam and joint transverse reinforcement but not longitudinal reinforcement. No fracture or buckling of reinforcing. | Beams or joints exhibit residual crack widths > 0.06 in. Spalling of cover concrete exposes a significant length of beam longitudinal reinforcement. Crushing of core concrete may occur. Fracture or buckling of reinforcing requiring replacement may occur. | Beams or joints exhibit residual crack widths > 0.06 in. Spalling of cover concrete exposes beam and joint transverse reinforcement but not longitudinal reinforcement. No fracture or buckling of reinforcing. |  | 1 | 1 | 0.8 | 0.2 |  | 0.02 | 0.0275 | 0.05 | 0.05 |  | Not Specified | 0.28 | 0.15 | 0.28 |  | 0.4 | 0.1 | 0.25 | 0.1 |  | 0.4 | 0.3 | 0.3 | 0.3 |  | NO | YES | Average | Average | Superior | Superior | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 8 feet either side of damaged area. Clean area adjacent to the damaged concrete. Prepare spalled concrete and adjacent cracks, as necessary, to be patched and to receive the epoxy injection. Patch concrete with grout. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems as necessary. | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 15 feet either side of damaged area. Shore damaged member(s) a min one level below (more levels may be required). Remove damaged concrete at least 1 inch beyond the exposed reinforcing steel. Place concrete forms. Place concrete. Remove forms. Remove shores after one week. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary). | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 15 feet either side of damaged component. Shore damaged member(s) a minimum of one level below (more levels may be required). Remove damaged component. Place and splice (as necessary) new reinforcing steel to existing, undamaged reinforcing. Place concrete forms. Place concrete. Remove forms. Remove shores after one week. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary). | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 15 feet either side of damaged area. Shore damaged member(s) a min one level below (more levels may be required). Remove damaged concrete at least 1 inch beyond the exposed reinforcing steel. Place concrete forms. Place concrete. Remove forms. Remove shores after one week. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary). |  | NO | NO | NO | NO |  | NO | NO | NO | NO |  | Not Applicable | Not Applicable | Not Applicable | Not Applicable |  | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 |  |  | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 |  |  | NO | NO | YES | NO |  | 0% | 0% | 20% | 0% |  | 0 | 0 | 0.5 | 0 |  | Note: DS4 is a copy of DS2 to create a mutually exclusive compliment to DS3. | Not Given | By User | By User | Laura Lowes | B1041.001a-DS1-1.JPG | B1041.001a-DS2-1.JPG | B1041.001a-DS3-1.JPG | B1041.001a-DS2-1.JPG |  | No | None | YES
B1041.001b | B1041.001b | ACI 318 SMF , Conc Col & Bm = 24" x 24", Beam both sides | ACI318 Concrete SMF, ductile response. Meets the requirements of ACI318 SMF. Costing is on a per joint basis. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 4 | DS1 | DS2 | DS3 | DS4 |  | Sequential | Sequential | Mutually Exclusive | Mutually Exclusive |  | Seq(DS1,DS2,MutEx(DS3,DS4)) | 103 | EA 1 | YES | NO | Beams or joints exhibit residual crack widths > 0.06 in. No significant spalling. No fracture or buckling of reinforcing. | Beams or joints exhibit residual crack widths > 0.06 in. Spalling of cover concrete exposes beam and joint transverse reinforcement but not longitudinal reinforcement. No fracture or buckling of reinforcing. | Beams or joints exhibit residual crack widths > 0.06 in. Spalling of cover concrete exposes a significant length of beam longitudinal reinforcement. Crushing of core concrete may occur. Fracture or buckling of reinforcing requiring replacement may occur. | Beams or joints exhibit residual crack widths > 0.06 in. Spalling of cover concrete exposes beam and joint transverse reinforcement but not longitudinal reinforcement. No fracture or buckling of reinforcing. |  | 1 | 1 | 0.8 | 0.2 |  | 0.02 | 0.0275 | 0.05 | 0.05 |  | Not Specified | 0.28 | 0.15 | 0.28 |  | 0.4 | 0.1 | 0.25 | 0.1 |  | 0.4 | 0.3 | 0.3 | 0.3 |  | NO | YES | Average | Average | Superior | Superior | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 8 feet either side of damaged area. Clean area adjacent to the damaged concrete. Prepare spalled concrete and adjacent cracks, as necessary, to be patched and to receive the epoxy injection. Patch concrete with grout. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems as necessary. | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 15 feet either side of damaged area. Shore damaged member(s) a min one level below (more levels may be required). Remove damaged concrete at least 1 inch beyond the exposed reinforcing steel. Place concrete forms. Place concrete. Remove forms. Remove shores after one week. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary). | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 15 feet either side of damaged component. Shore damaged member(s) a minimum of one level below (more levels may be required). Remove damaged component. Place and splice (as necessary) new reinforcing steel to existing, undamaged reinforcing. Place concrete forms. Place concrete. Remove forms. Remove shores after one week. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary). | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 15 feet either side of damaged area. Shore damaged member(s) a min one level below (more levels may be required). Remove damaged concrete at least 1 inch beyond the exposed reinforcing steel. Place concrete forms. Place concrete. Remove forms. Remove shores after one week. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary). |  | NO | NO | NO | NO |  | NO | NO | NO | NO |  | Not Applicable | Not Applicable | Not Applicable | Not Applicable |  | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 |  |  | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 |  |  | NO | NO | YES | NO |  | 0% | 0% | 20% | 0% |  | 0 | 0 | 0.5 | 0 |  | Note: DS4 is a copy of DS2 to create a mutually exclusive compliment to DS3. | Not Given | By User | By User | Laura Lowes | B1041.001a-DS1-1.JPG | B1041.001a-DS2-1.JPG | B1041.001a-DS3-1.JPG | B1041.001a-DS2-1.JPG |  | No | None | YES
B1041.002a | B1041.002a | ACI 318 SMF , Conc Col & Bm = 24" x 36", Beam one side | ACI318 Concrete SMF, ductile response. Meets the requirements of ACI318 SMF. Costing is on a per joint basis. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 4 | DS1 | DS2 | DS3 | DS4 |  | Sequential | Sequential | Mutually Exclusive | Mutually Exclusive |  | Seq(DS1,DS2,MutEx(DS3,DS4)) | 104 | EA 1 | YES | NO | Beams or joints exhibit residual crack widths > 0.06 in. No significant spalling. No fracture or buckling of reinforcing. | Beams or joints exhibit residual crack widths > 0.06 in. Spalling of cover concrete exposes beam and joint transverse reinforcement but not longitudinal reinforcement. No fracture or buckling of reinforcing. | Beams or joints exhibit residual crack widths > 0.06 in. Spalling of cover concrete exposes a significant length of beam longitudinal reinforcement. Crushing of core concrete may occur. Fracture or buckling of reinforcing requiring replacement may occur. | Beams or joints exhibit residual crack widths > 0.06 in. Spalling of cover concrete exposes beam and joint transverse reinforcement but not longitudinal reinforcement. No fracture or buckling of reinforcing. |  | 1 | 1 | 0.8 | 0.2 |  | 0.02 | 0.0275 | 0.05 | 0.05 |  | Not Specified | 0.28 | 0.15 | 0.28 |  | 0.4 | 0.1 | 0.25 | 0.1 |  | 0.4 | 0.3 | 0.3 | 0.3 |  | NO | YES | Average | Average | Superior | Superior | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 8 feet either side of damaged area. Clean area adjacent to the damaged concrete. Prepare spalled concrete and adjacent cracks, as necessary, to be patched and to receive the epoxy injection. Patch concrete with grout. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems as necessary. | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 15 feet either side of damaged area. Shore damaged member(s) a min one level below (more levels may be required). Remove damaged concrete at least 1 inch beyond the exposed reinforcing steel. Place concrete forms. Place concrete. Remove forms. Remove shores after one week. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary). | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 15 feet either side of damaged component. Shore damaged member(s) a minimum of one level below (more levels may be required). Remove damaged component. Place and splice (as necessary) new reinforcing steel to existing, undamaged reinforcing. Place concrete forms. Place concrete. Remove forms. Remove shores after one week. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary). | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 15 feet either side of damaged area. Shore damaged member(s) a min one level below (more levels may be required). Remove damaged concrete at least 1 inch beyond the exposed reinforcing steel. Place concrete forms. Place concrete. Remove forms. Remove shores after one week. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary). |  | NO | NO | NO | NO |  | NO | NO | NO | NO |  | Not Applicable | Not Applicable | Not Applicable | Not Applicable |  | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 |  |  | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 |  |  | NO | NO | YES | NO |  | 0% | 0% | 20% | 0% |  | 0 | 0 | 0.5 | 0 |  | Note: DS4 is a copy of DS2 to create a mutually exclusive compliment to DS3. | Not Given | By User | By User | Laura Lowes | B1041.001a-DS1-1.JPG | B1041.001a-DS2-1.JPG | B1041.001a-DS3-1.JPG | B1041.001a-DS2-1.JPG |  | No | None | YES
B1041.002b | B1041.002b | ACI 318 SMF , Conc Col & Bm = 24" x 36", Beam both sides | ACI318 Concrete SMF, ductile response. Meets the requirements of ACI318 SMF. Costing is on a per joint basis. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 4 | DS1 | DS2 | DS3 | DS4 |  | Sequential | Sequential | Mutually Exclusive | Mutually Exclusive |  | Seq(DS1,DS2,MutEx(DS3,DS4)) | 105 | EA 1 | YES | NO | Beams or joints exhibit residual crack widths > 0.06 in. No significant spalling. No fracture or buckling of reinforcing. | Beams or joints exhibit residual crack widths > 0.06 in. Spalling of cover concrete exposes beam and joint transverse reinforcement but not longitudinal reinforcement. No fracture or buckling of reinforcing. | Beams or joints exhibit residual crack widths > 0.06 in. Spalling of cover concrete exposes a significant length of beam longitudinal reinforcement. Crushing of core concrete may occur. Fracture or buckling of reinforcing requiring replacement may occur. | Beams or joints exhibit residual crack widths > 0.06 in. Spalling of cover concrete exposes beam and joint transverse reinforcement but not longitudinal reinforcement. No fracture or buckling of reinforcing. |  | 1 | 1 | 0.8 | 0.2 |  | 0.02 | 0.0275 | 0.05 | 0.05 |  | Not Specified | 0.28 | 0.15 | 0.28 |  | 0.4 | 0.1 | 0.25 | 0.1 |  | 0.4 | 0.3 | 0.3 | 0.3 |  | NO | YES | Average | Average | Superior | Superior | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 8 feet either side of damaged area. Clean area adjacent to the damaged concrete. Prepare spalled concrete and adjacent cracks, as necessary, to be patched and to receive the epoxy injection. Patch concrete with grout. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems as necessary. | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 15 feet either side of damaged area. Shore damaged member(s) a min one level below (more levels may be required). Remove damaged concrete at least 1 inch beyond the exposed reinforcing steel. Place concrete forms. Place concrete. Remove forms. Remove shores after one week. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary). | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 15 feet either side of damaged component. Shore damaged member(s) a minimum of one level below (more levels may be required). Remove damaged component. Place and splice (as necessary) new reinforcing steel to existing, undamaged reinforcing. Place concrete forms. Place concrete. Remove forms. Remove shores after one week. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary). | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 15 feet either side of damaged area. Shore damaged member(s) a min one level below (more levels may be required). Remove damaged concrete at least 1 inch beyond the exposed reinforcing steel. Place concrete forms. Place concrete. Remove forms. Remove shores after one week. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary). |  | NO | NO | NO | NO |  | NO | NO | NO | NO |  | Not Applicable | Not Applicable | Not Applicable | Not Applicable |  | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 |  |  | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 |  |  | NO | NO | YES | NO |  | 0% | 0% | 20% | 0% |  | 0 | 0 | 0.5 | 0 |  | Note: DS4 is a copy of DS2 to create a mutually exclusive compliment to DS3. | Not Given | By User | By User | Laura Lowes | B1041.001a-DS1-1.JPG | B1041.001a-DS2-1.JPG | B1041.001a-DS3-1.JPG | B1041.001a-DS2-1.JPG |  | No | None | YES
B1041.003a | B1041.003a | ACI 318 SMF , Conc Col & Bm = 36" x 36", Beam one side | ACI318 Concrete SMF, ductile response. Meets the requirements of ACI318 SMF. Costing is on a per joint basis. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 4 | DS1 | DS2 | DS3 | DS4 |  | Sequential | Sequential | Mutually Exclusive | Mutually Exclusive |  | Seq(DS1,DS2,MutEx(DS3,DS4)) | 106 | EA 1 | YES | NO | Beams or joints exhibit residual crack widths > 0.06 in. No significant spalling. No fracture or buckling of reinforcing. | Beams or joints exhibit residual crack widths > 0.06 in. Spalling of cover concrete exposes beam and joint transverse reinforcement but not longitudinal reinforcement. No fracture or buckling of reinforcing. | Beams or joints exhibit residual crack widths > 0.06 in. Spalling of cover concrete exposes a significant length of beam longitudinal reinforcement. Crushing of core concrete may occur. Fracture or buckling of reinforcing requiring replacement may occur. | Beams or joints exhibit residual crack widths > 0.06 in. Spalling of cover concrete exposes beam and joint transverse reinforcement but not longitudinal reinforcement. No fracture or buckling of reinforcing. |  | 1 | 1 | 0.8 | 0.2 |  | 0.02 | 0.0275 | 0.05 | 0.05 |  | Not Specified | 0.28 | 0.15 | 0.28 |  | 0.4 | 0.1 | 0.25 | 0.1 |  | 0.4 | 0.3 | 0.3 | 0.3 |  | NO | YES | Average | Average | Superior | Superior | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 8 feet either side of damaged area. Clean area adjacent to the damaged concrete. Prepare spalled concrete and adjacent cracks, as necessary, to be patched and to receive the epoxy injection. Patch concrete with grout. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems as necessary. | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 15 feet either side of damaged area. Shore damaged member(s) a min one level below (more levels may be required). Remove damaged concrete at least 1 inch beyond the exposed reinforcing steel. Place concrete forms. Place concrete. Remove forms. Remove shores after one week. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary). | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 15 feet either side of damaged component. Shore damaged member(s) a minimum of one level below (more levels may be required). Remove damaged component. Place and splice (as necessary) new reinforcing steel to existing, undamaged reinforcing. Place concrete forms. Place concrete. Remove forms. Remove shores after one week. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary). | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 15 feet either side of damaged area. Shore damaged member(s) a min one level below (more levels may be required). Remove damaged concrete at least 1 inch beyond the exposed reinforcing steel. Place concrete forms. Place concrete. Remove forms. Remove shores after one week. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary). |  | NO | NO | NO | NO |  | NO | NO | NO | NO |  | Not Applicable | Not Applicable | Not Applicable | Not Applicable |  | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 |  |  | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 |  |  | NO | NO | YES | NO |  | 0% | 0% | 20% | 0% |  | 0 | 0 | 0.5 | 0 |  | Note: DS4 is a copy of DS2 to create a mutually exclusive compliment to DS3. | Not Given | By User | By User | Laura Lowes | B1041.001a-DS1-1.JPG | B1041.001a-DS2-1.JPG | B1041.001a-DS3-1.JPG | B1041.001a-DS2-1.JPG |  | No | None | YES
B1041.003b | B1041.003b | ACI 318 SMF , Conc Col & Bm = 36" x 36", Beam both sides | ACI318 Concrete SMF, ductile response. Meets the requirements of ACI318 SMF. Costing is on a per joint basis. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 4 | DS1 | DS2 | DS3 | DS4 |  | Sequential | Sequential | Mutually Exclusive | Mutually Exclusive |  | Seq(DS1,DS2,MutEx(DS3,DS4)) | 107 | EA 1 | YES | NO | Beams or joints exhibit residual crack widths > 0.06 in. No significant spalling. No fracture or buckling of reinforcing. | Beams or joints exhibit residual crack widths > 0.06 in. Spalling of cover concrete exposes beam and joint transverse reinforcement but not longitudinal reinforcement. No fracture or buckling of reinforcing. | Beams or joints exhibit residual crack widths > 0.06 in. Spalling of cover concrete exposes a significant length of beam longitudinal reinforcement. Crushing of core concrete may occur. Fracture or buckling of reinforcing requiring replacement may occur. | Beams or joints exhibit residual crack widths > 0.06 in. Spalling of cover concrete exposes beam and joint transverse reinforcement but not longitudinal reinforcement. No fracture or buckling of reinforcing. |  | 1 | 1 | 0.8 | 0.2 |  | 0.02 | 0.0275 | 0.05 | 0.05 |  | Not Specified | 0.28 | 0.15 | 0.28 |  | 0.4 | 0.1 | 0.25 | 0.1 |  | 0.4 | 0.3 | 0.3 | 0.3 |  | NO | YES | Average | Average | Superior | Superior | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 8 feet either side of damaged area. Clean area adjacent to the damaged concrete. Prepare spalled concrete and adjacent cracks, as necessary, to be patched and to receive the epoxy injection. Patch concrete with grout. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems as necessary. | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 15 feet either side of damaged area. Shore damaged member(s) a min one level below (more levels may be required). Remove damaged concrete at least 1 inch beyond the exposed reinforcing steel. Place concrete forms. Place concrete. Remove forms. Remove shores after one week. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary). | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 15 feet either side of damaged component. Shore damaged member(s) a minimum of one level below (more levels may be required). Remove damaged component. Place and splice (as necessary) new reinforcing steel to existing, undamaged reinforcing. Place concrete forms. Place concrete. Remove forms. Remove shores after one week. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary). | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 15 feet either side of damaged area. Shore damaged member(s) a min one level below (more levels may be required). Remove damaged concrete at least 1 inch beyond the exposed reinforcing steel. Place concrete forms. Place concrete. Remove forms. Remove shores after one week. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary). |  | NO | NO | NO | NO |  | NO | NO | NO | NO |  | Not Applicable | Not Applicable | Not Applicable | Not Applicable |  | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 |  |  | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 |  |  | NO | NO | YES | NO |  | 0% | 0% | 20% | 0% |  | 0 | 0 | 0.5 | 0 |  | Note: DS4 is a copy of DS2 to create a mutually exclusive compliment to DS3. | Not Given | By User | By User | Laura Lowes | B1041.001a-DS1-1.JPG | B1041.001a-DS2-1.JPG | B1041.001a-DS3-1.JPG | B1041.001a-DS2-1.JPG |  | No | None | YES
B1041.011a | B1041.011a | MF with SMF-conforming beam and column flexural and confinement reinforcement but weak joints , Conc Col & Bm = 24" x 24", Beam one side | Non-conforming SMF, joint shear damage, beam flexural response. Meets the following requirements: (1) Sum Mcol / Sum Mbeam > 1.2, (2) Column Pu < 0.6f'cAg, (3) Column flexural response with HIGH ductility, (4) Beam compliant transverse reinforcing with low beam V/bwd(f'c)^0.5, (5) Joints with compliant transverse reinforcing details with spacing < d(column)/2 and Joint V/Vn < 1.2. Costing is on a per joint basis. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 4 | DS1 | DS2 | DS3 | DS4 |  | Sequential | Sequential | Mutually Exclusive | Mutually Exclusive |  | Seq(DS1,DS2,MutEx(DS3,DS4)) | 108 | EA 1 | YES | NO | Beams or joints exhibit residual crack widths > 0.06 in. No significant spalling. No fracture or buckling of reinforcing. | Beams or joints exhibit residual crack widths > 0.06 in. Spalling of cover concrete exposes beam and joint transverse reinforcement but not longitudinal reinforcement. No fracture or buckling of reinforcing. | Beams or joints exhibit residual crack widths > 0.06 in. Spalling of cover concrete exposes a significant length of beam longitudinal reinforcement. Crushing of core concrete may occur. Fracture or buckling of reinforcing requiring replacement may occur. | Beams or joints exhibit residual crack widths > 0.06 in. Spalling of cover concrete exposes beam and joint transverse reinforcement but not longitudinal reinforcement. No fracture or buckling of reinforcing. |  | 1 | 1 | 0.5 | 0.5 |  | 0.02 | 0.025 | 0.04 | 0.04 |  | 0.07 | 0.3 | 0.2 | 0.3 |  | 0.4 | 0.1 | 0.25 | 0.1 |  | 0.4 | 0.3 | 0.3 | 0.3 |  | NO | YES | Average | Average | Superior | Superior | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 8 feet either side of damaged area. Clean area adjacent to the damaged concrete. Prepare spalled concrete and adjacent cracks, as necessary, to be patched and to receive the epoxy injection. Patch concrete with grout. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems as necessary. | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 15 feet either side of damaged area. Shore damaged member(s) a min one level below (more levels may be required). Remove damaged concrete at least 1 inch beyond the exposed reinforcing steel. Place concrete forms. Place concrete. Remove forms. Remove shores after one week. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary). | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 15 feet either side of damaged component. Shore damaged member(s) a minimum of one level below (more levels may be required). Remove damaged component. Place and splice (as necessary) new reinforcing steel to existing, undamaged reinforcing. Place concrete forms. Place concrete. Remove forms. Remove shores after one week. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary). | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 15 feet either side of damaged area. Shore damaged member(s) a min one level below (more levels may be required). Remove damaged concrete at least 1 inch beyond the exposed reinforcing steel. Place concrete forms. Place concrete. Remove forms. Remove shores after one week. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary). |  | NO | NO | NO | NO |  | NO | NO | NO | NO |  | Not Applicable | Not Applicable | Not Applicable | Not Applicable |  | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 |  |  | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 |  |  | NO | NO | YES | NO |  | 0% | 0% | 20% | 0% |  | 0 | 0 | 0.5 | 0 |  | Note: DS4 is a copy of DS2 to create a mutually exclusive compliment to DS3. | Not Given | By User | By User | Laura Lowes | B1041.001a-DS1-1.JPG | B1041.001a-DS2-1.JPG | B1041.001a-DS3-1.JPG | B1041.001a-DS2-1.JPG |  | No | None | YES
B1041.011b | B1041.011b | MF with SMF-conforming beam and column flexural and confinement reinforcement but weak joints , Conc Col & Bm = 24" x 24", Beam both sides | Non-conforming SMF, joint shear damage, beam flexural response. Meets the following requirements: (1) Sum Mcol / Sum Mbeam > 1.2, (2) Column Pu < 0.6f'cAg, (3) Column flexural response with HIGH ductility, (4) Beam compliant transverse reinforcing with low beam V/bwd(f'c)^0.5, (5) Joints with compliant transverse reinforcing details with spacing < d(column)/2 and Joint V/Vn < 1.2. Costing is on a per joint basis. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 4 | DS1 | DS2 | DS3 | DS4 |  | Sequential | Sequential | Mutually Exclusive | Mutually Exclusive |  | Seq(DS1,DS2,MutEx(DS3,DS4)) | 109 | EA 1 | YES | NO | Beams or joints exhibit residual crack widths > 0.06 in. No significant spalling. No fracture or buckling of reinforcing. | Beams or joints exhibit residual crack widths > 0.06 in. Spalling of cover concrete exposes beam and joint transverse reinforcement but not longitudinal reinforcement. No fracture or buckling of reinforcing. | Beams or joints exhibit residual crack widths > 0.06 in. Spalling of cover concrete exposes a significant length of beam longitudinal reinforcement. Crushing of core concrete may occur. Fracture or buckling of reinforcing requiring replacement may occur. | Beams or joints exhibit residual crack widths > 0.06 in. Spalling of cover concrete exposes beam and joint transverse reinforcement but not longitudinal reinforcement. No fracture or buckling of reinforcing. |  | 1 | 1 | 0.5 | 0.5 |  | 0.02 | 0.025 | 0.04 | 0.04 |  | 0.07 | 0.3 | 0.2 | 0.3 |  | 0.4 | 0.1 | 0.25 | 0.1 |  | 0.4 | 0.3 | 0.3 | 0.3 |  | NO | YES | Average | Average | Superior | Superior | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 8 feet either side of damaged area. Clean area adjacent to the damaged concrete. Prepare spalled concrete and adjacent cracks, as necessary, to be patched and to receive the epoxy injection. Patch concrete with grout. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems as necessary. | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 15 feet either side of damaged area. Shore damaged member(s) a min one level below (more levels may be required). Remove damaged concrete at least 1 inch beyond the exposed reinforcing steel. Place concrete forms. Place concrete. Remove forms. Remove shores after one week. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary). | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 15 feet either side of damaged component. Shore damaged member(s) a minimum of one level below (more levels may be required). Remove damaged component. Place and splice (as necessary) new reinforcing steel to existing, undamaged reinforcing. Place concrete forms. Place concrete. Remove forms. Remove shores after one week. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary). | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 15 feet either side of damaged area. Shore damaged member(s) a min one level below (more levels may be required). Remove damaged concrete at least 1 inch beyond the exposed reinforcing steel. Place concrete forms. Place concrete. Remove forms. Remove shores after one week. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary). |  | NO | NO | NO | NO |  | NO | NO | NO | NO |  | Not Applicable | Not Applicable | Not Applicable | Not Applicable |  | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 |  |  | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 |  |  | NO | NO | YES | NO |  | 0% | 0% | 20% | 0% |  | 0 | 0 | 0.5 | 0 |  | Note: DS4 is a copy of DS2 to create a mutually exclusive compliment to DS3. | Not Given | By User | By User | Laura Lowes | B1041.001a-DS1-1.JPG | B1041.001a-DS2-1.JPG | B1041.001a-DS3-1.JPG | B1041.001a-DS2-1.JPG |  | No | None | YES
B1041.012a | B1041.012a | MF with SMF-conforming beam and column flexural and confinement reinforcement but weak joints , Conc Col & Bm = 24" x 36", Beam one side | Non-conforming SMF, joint shear damage, beam flexural response. Meets the following requirements: (1) Sum Mcol / Sum Mbeam > 1.2, (2) Column Pu < 0.6f'cAg, (3) Column flexural response with HIGH ductility, (4) Beam compliant transverse reinforcing with low beam V/bwd(f'c)^0.5, (5) Joints with compliant transverse reinforcing details with spacing < d(column)/2 and Joint V/Vn < 1.2. Costing is on a per joint basis. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 4 | DS1 | DS2 | DS3 | DS4 |  | Sequential | Sequential | Mutually Exclusive | Mutually Exclusive |  | Seq(DS1,DS2,MutEx(DS3,DS4)) | 110 | EA 1 | YES | NO | Beams or joints exhibit residual crack widths > 0.06 in. No significant spalling. No fracture or buckling of reinforcing. | Beams or joints exhibit residual crack widths > 0.06 in. Spalling of cover concrete exposes beam and joint transverse reinforcement but not longitudinal reinforcement. No fracture or buckling of reinforcing. | Beams or joints exhibit residual crack widths > 0.06 in. Spalling of cover concrete exposes a significant length of beam longitudinal reinforcement. Crushing of core concrete may occur. Fracture or buckling of reinforcing requiring replacement may occur. | Beams or joints exhibit residual crack widths > 0.06 in. Spalling of cover concrete exposes beam and joint transverse reinforcement but not longitudinal reinforcement. No fracture or buckling of reinforcing. |  | 1 | 1 | 0.5 | 0.5 |  | 0.02 | 0.025 | 0.04 | 0.04 |  | 0.07 | 0.3 | 0.2 | 0.3 |  | 0.4 | 0.1 | 0.25 | 0.1 |  | 0.4 | 0.3 | 0.3 | 0.3 |  | NO | YES | Average | Average | Superior | Superior | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 8 feet either side of damaged area. Clean area adjacent to the damaged concrete. Prepare spalled concrete and adjacent cracks, as necessary, to be patched and to receive the epoxy injection. Patch concrete with grout. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems as necessary. | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 15 feet either side of damaged area. Shore damaged member(s) a min one level below (more levels may be required). Remove damaged concrete at least 1 inch beyond the exposed reinforcing steel. Place concrete forms. Place concrete. Remove forms. Remove shores after one week. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary). | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 15 feet either side of damaged component. Shore damaged member(s) a minimum of one level below (more levels may be required). Remove damaged component. Place and splice (as necessary) new reinforcing steel to existing, undamaged reinforcing. Place concrete forms. Place concrete. Remove forms. Remove shores after one week. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary). | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 15 feet either side of damaged area. Shore damaged member(s) a min one level below (more levels may be required). Remove damaged concrete at least 1 inch beyond the exposed reinforcing steel. Place concrete forms. Place concrete. Remove forms. Remove shores after one week. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary). |  | NO | NO | NO | NO |  | NO | NO | NO | NO |  | Not Applicable | Not Applicable | Not Applicable | Not Applicable |  | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 |  |  | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 |  |  | NO | NO | YES | NO |  | 0% | 0% | 20% | 0% |  | 0 | 0 | 0.5 | 0 |  | Note: DS4 is a copy of DS2 to create a mutually exclusive compliment to DS3. | Not Given | By User | By User | Laura Lowes | B1041.001a-DS1-1.JPG | B1041.001a-DS2-1.JPG | B1041.001a-DS3-1.JPG | B1041.001a-DS2-1.JPG |  | No | None | YES
B1041.012b | B1041.012b | MF with SMF-conforming beam and column flexural and confinement reinforcement but weak joints , Conc Col & Bm = 24" x 36", Beam both sides | Non-conforming SMF, joint shear damage, beam flexural response. Meets the following requirements: (1) Sum Mcol / Sum Mbeam > 1.2, (2) Column Pu < 0.6f'cAg, (3) Column flexural response with HIGH ductility, (4) Beam compliant transverse reinforcing with low beam V/bwd(f'c)^0.5, (5) Joints with compliant transverse reinforcing details with spacing < d(column)/2 and Joint V/Vn < 1.2. Costing is on a per joint basis. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 4 | DS1 | DS2 | DS3 | DS4 |  | Sequential | Sequential | Mutually Exclusive | Mutually Exclusive |  | Seq(DS1,DS2,MutEx(DS3,DS4)) | 111 | EA 1 | YES | NO | Beams or joints exhibit residual crack widths > 0.06 in. No significant spalling. No fracture or buckling of reinforcing. | Beams or joints exhibit residual crack widths > 0.06 in. Spalling of cover concrete exposes beam and joint transverse reinforcement but not longitudinal reinforcement. No fracture or buckling of reinforcing. | Beams or joints exhibit residual crack widths > 0.06 in. Spalling of cover concrete exposes a significant length of beam longitudinal reinforcement. Crushing of core concrete may occur. Fracture or buckling of reinforcing requiring replacement may occur. | Beams or joints exhibit residual crack widths > 0.06 in. Spalling of cover concrete exposes beam and joint transverse reinforcement but not longitudinal reinforcement. No fracture or buckling of reinforcing. |  | 1 | 1 | 0.5 | 0.5 |  | 0.02 | 0.025 | 0.04 | 0.04 |  | 0.07 | 0.3 | 0.2 | 0.3 |  | 0.4 | 0.1 | 0.25 | 0.1 |  | 0.4 | 0.3 | 0.3 | 0.3 |  | NO | YES | Average | Average | Superior | Superior | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 8 feet either side of damaged area. Clean area adjacent to the damaged concrete. Prepare spalled concrete and adjacent cracks, as necessary, to be patched and to receive the epoxy injection. Patch concrete with grout. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems as necessary. | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 15 feet either side of damaged area. Shore damaged member(s) a min one level below (more levels may be required). Remove damaged concrete at least 1 inch beyond the exposed reinforcing steel. Place concrete forms. Place concrete. Remove forms. Remove shores after one week. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary). | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 15 feet either side of damaged component. Shore damaged member(s) a minimum of one level below (more levels may be required). Remove damaged component. Place and splice (as necessary) new reinforcing steel to existing, undamaged reinforcing. Place concrete forms. Place concrete. Remove forms. Remove shores after one week. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary). | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 15 feet either side of damaged area. Shore damaged member(s) a min one level below (more levels may be required). Remove damaged concrete at least 1 inch beyond the exposed reinforcing steel. Place concrete forms. Place concrete. Remove forms. Remove shores after one week. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary). |  | NO | NO | NO | NO |  | NO | NO | NO | NO |  | Not Applicable | Not Applicable | Not Applicable | Not Applicable |  | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 |  |  | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 |  |  | NO | NO | YES | NO |  | 0% | 0% | 20% | 0% |  | 0 | 0 | 0.5 | 0 |  | Note: DS4 is a copy of DS2 to create a mutually exclusive compliment to DS3. | Not Given | By User | By User | Laura Lowes | B1041.001a-DS1-1.JPG | B1041.001a-DS2-1.JPG | B1041.001a-DS3-1.JPG | B1041.001a-DS2-1.JPG |  | No | None | YES
B1041.013a | B1041.013a | MF with SMF-conforming beam and column flexural and confinement reinforcement but weak joints , Conc Col & Bm = 36" x 36", Beam one side | Non-conforming SMF, joint shear damage, beam flexural response. Meets the following requirements: (1) Sum Mcol / Sum Mbeam > 1.2, (2) Column Pu < 0.6f'cAg, (3) Column flexural response with HIGH ductility, (4) Beam compliant transverse reinforcing with low beam V/bwd(f'c)^0.5, (5) Joints with compliant transverse reinforcing details with spacing < d(column)/2 and Joint V/Vn < 1.2. Costing is on a per joint basis. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 4 | DS1 | DS2 | DS3 | DS4 |  | Sequential | Sequential | Mutually Exclusive | Mutually Exclusive |  | Seq(DS1,DS2,MutEx(DS3,DS4)) | 112 | EA 1 | YES | NO | Beams or joints exhibit residual crack widths > 0.06 in. No significant spalling. No fracture or buckling of reinforcing. | Beams or joints exhibit residual crack widths > 0.06 in. Spalling of cover concrete exposes beam and joint transverse reinforcement but not longitudinal reinforcement. No fracture or buckling of reinforcing. | Beams or joints exhibit residual crack widths > 0.06 in. Spalling of cover concrete exposes a significant length of beam longitudinal reinforcement. Crushing of core concrete may occur. Fracture or buckling of reinforcing requiring replacement may occur. | Beams or joints exhibit residual crack widths > 0.06 in. Spalling of cover concrete exposes beam and joint transverse reinforcement but not longitudinal reinforcement. No fracture or buckling of reinforcing. |  | 1 | 1 | 0.5 | 0.5 |  | 0.02 | 0.025 | 0.04 | 0.04 |  | 0.07 | 0.3 | 0.2 | 0.3 |  | 0.4 | 0.1 | 0.25 | 0.1 |  | 0.4 | 0.3 | 0.3 | 0.3 |  | NO | YES | Average | Average | Superior | Superior | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 8 feet either side of damaged area. Clean area adjacent to the damaged concrete. Prepare spalled concrete and adjacent cracks, as necessary, to be patched and to receive the epoxy injection. Patch concrete with grout. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems as necessary. | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 15 feet either side of damaged area. Shore damaged member(s) a min one level below (more levels may be required). Remove damaged concrete at least 1 inch beyond the exposed reinforcing steel. Place concrete forms. Place concrete. Remove forms. Remove shores after one week. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary). | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 15 feet either side of damaged component. Shore damaged member(s) a minimum of one level below (more levels may be required). Remove damaged component. Place and splice (as necessary) new reinforcing steel to existing, undamaged reinforcing. Place concrete forms. Place concrete. Remove forms. Remove shores after one week. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary). | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 15 feet either side of damaged area. Shore damaged member(s) a min one level below (more levels may be required). Remove damaged concrete at least 1 inch beyond the exposed reinforcing steel. Place concrete forms. Place concrete. Remove forms. Remove shores after one week. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary). |  | NO | NO | NO | NO |  | NO | NO | NO | NO |  | Not Applicable | Not Applicable | Not Applicable | Not Applicable |  | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 |  |  | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 |  |  | NO | NO | YES | NO |  | 0% | 0% | 20% | 0% |  | 0 | 0 | 0.5 | 0 |  | Note: DS4 is a copy of DS2 to create a mutually exclusive compliment to DS3. | Not Given | By User | By User | Laura Lowes | B1041.001a-DS1-1.JPG | B1041.001a-DS2-1.JPG | B1041.001a-DS3-1.JPG | B1041.001a-DS2-1.JPG |  | No | None | YES
B1041.013b | B1041.013b | MF with SMF-conforming beam and column flexural and confinement reinforcement but weak joints , Conc Col & Bm = 36" x 36", Beam both sides | Non-conforming SMF, joint shear damage, beam flexural response. Meets the following requirements: (1) Sum Mcol / Sum Mbeam > 1.2, (2) Column Pu < 0.6f'cAg, (3) Column flexural response with HIGH ductility, (4) Beam compliant transverse reinforcing with low beam V/bwd(f'c)^0.5, (5) Joints with compliant transverse reinforcing details with spacing < d(column)/2 and Joint V/Vn < 1.2. Costing is on a per joint basis. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 4 | DS1 | DS2 | DS3 | DS4 |  | Sequential | Sequential | Mutually Exclusive | Mutually Exclusive |  | Seq(DS1,DS2,MutEx(DS3,DS4)) | 113 | EA 1 | YES | NO | Beams or joints exhibit residual crack widths > 0.06 in. No significant spalling. No fracture or buckling of reinforcing. | Beams or joints exhibit residual crack widths > 0.06 in. Spalling of cover concrete exposes beam and joint transverse reinforcement but not longitudinal reinforcement. No fracture or buckling of reinforcing. | Beams or joints exhibit residual crack widths > 0.06 in. Spalling of cover concrete exposes a significant length of beam longitudinal reinforcement. Crushing of core concrete may occur. Fracture or buckling of reinforcing requiring replacement may occur. | Beams or joints exhibit residual crack widths > 0.06 in. Spalling of cover concrete exposes beam and joint transverse reinforcement but not longitudinal reinforcement. No fracture or buckling of reinforcing. |  | 1 | 1 | 0.5 | 0.5 |  | 0.02 | 0.025 | 0.04 | 0.04 |  | 0.07 | 0.3 | 0.2 | 0.3 |  | 0.4 | 0.1 | 0.25 | 0.1 |  | 0.4 | 0.3 | 0.3 | 0.3 |  | NO | YES | Average | Average | Superior | Superior | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 8 feet either side of damaged area. Clean area adjacent to the damaged concrete. Prepare spalled concrete and adjacent cracks, as necessary, to be patched and to receive the epoxy injection. Patch concrete with grout. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems as necessary. | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 15 feet either side of damaged area. Shore damaged member(s) a min one level below (more levels may be required). Remove damaged concrete at least 1 inch beyond the exposed reinforcing steel. Place concrete forms. Place concrete. Remove forms. Remove shores after one week. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary). | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 15 feet either side of damaged component. Shore damaged member(s) a minimum of one level below (more levels may be required). Remove damaged component. Place and splice (as necessary) new reinforcing steel to existing, undamaged reinforcing. Place concrete forms. Place concrete. Remove forms. Remove shores after one week. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary). | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 15 feet either side of damaged area. Shore damaged member(s) a min one level below (more levels may be required). Remove damaged concrete at least 1 inch beyond the exposed reinforcing steel. Place concrete forms. Place concrete. Remove forms. Remove shores after one week. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary). |  | NO | NO | NO | NO |  | NO | NO | NO | NO |  | Not Applicable | Not Applicable | Not Applicable | Not Applicable |  | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 |  |  | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 |  |  | NO | NO | YES | NO |  | 0% | 0% | 20% | 0% |  | 0 | 0 | 0.5 | 0 |  | Note: DS4 is a copy of DS2 to create a mutually exclusive compliment to DS3. | Not Given | By User | By User | Laura Lowes | B1041.001a-DS1-1.JPG | B1041.001a-DS2-1.JPG | B1041.001a-DS3-1.JPG | B1041.001a-DS2-1.JPG |  | No | None | YES
B1041.021a | B1041.021a | ACI 318 IMF, Conc Col & Bm = 24" x 24", Beam one side | ACI318 IMF, joint shear damage or failure, beam or column flexure-shear response. Meets the following requirements: (1) Column Pu < 0.3Agf'c Costing is on a per joint basis. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 4 | DS1 | DS2 | DS3 | DS4 |  | Sequential | Sequential | Mutually Exclusive | Mutually Exclusive |  | Seq(DS1,DS2,MutEx(DS3,DS4)) | 114 | EA 1 | YES | NO | Beams or joints exhibit residual crack widths > 0.06 in. No significant spalling. No fracture or buckling of reinforcing. | Beams or joints exhibit residual crack widths > 0.06 in. Spalling of cover concrete exposes beam and joint transverse reinforcement but not longitudinal reinforcement. No fracture or buckling of reinforcing. | Beams or joints exhibit residual crack widths > 0.06 in. Spalling of cover concrete exposes a significant length of beam longitudinal reinforcement. Crushing of core concrete may occur. Fracture or buckling of reinforcing requiring replacement may occur. | Beams or joints exhibit residual crack widths > 0.06 in. Spalling of cover concrete exposes beam and joint transverse reinforcement but not longitudinal reinforcement. No fracture or buckling of reinforcing. |  | 1 | 1 | 0.4 | 0.6 |  | 0.02 | 0.025 | 0.035 | 0.035 |  | 0.06 | 0.3 | 0.2 | 0.3 |  | 0.4 | 0.1 | 0.1 | 0.1 |  | 0.4 | 0.3 | 0.3 | 0.3 |  | NO | YES | Average | Average | Superior | Superior | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 8 feet either side of damaged area. Clean area adjacent to the damaged concrete. Prepare spalled concrete and adjacent cracks, as necessary, to be patched and to receive the epoxy injection. Patch concrete with grout. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems as necessary. | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 15 feet either side of damaged area. Shore damaged member(s) a min one level below (more levels may be required). Remove damaged concrete at least 1 inch beyond the exposed reinforcing steel. Place concrete forms. Place concrete. Remove forms. Remove shores after one week. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary). | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 15 feet either side of damaged component. Shore damaged member(s) a minimum of one level below (more levels may be required). Remove damaged component. Place and splice (as necessary) new reinforcing steel to existing, undamaged reinforcing. Place concrete forms. Place concrete. Remove forms. Remove shores after one week. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary). | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 15 feet either side of damaged area. Shore damaged member(s) a min one level below (more levels may be required). Remove damaged concrete at least 1 inch beyond the exposed reinforcing steel. Place concrete forms. Place concrete. Remove forms. Remove shores after one week. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary). |  | NO | NO | NO | NO |  | NO | NO | NO | NO |  | Not Applicable | Not Applicable | Not Applicable | Not Applicable |  | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 |  |  | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 |  |  | NO | NO | YES | NO |  | 0% | 0% | 20% | 0% |  | 0 | 0 | 0.5 | 0 |  | Note: DS4 is a copy of DS2 to create a mutually exclusive compliment to DS3. | Not Given | By User | By User | Laura Lowes | B1041.001a-DS1-1.JPG | B1041.001a-DS2-1.JPG | B1041.001a-DS3-1.JPG | B1041.001a-DS2-1.JPG |  | No | 2011-08-24 Changed DS4 beta from 0.4 to 0.3 to avoid negative probability. | YES
B1041.021b | B1041.021b | ACI 318 IMF, Conc Col & Bm = 24" x 24", Beam both sides | ACI318 IMF, joint shear damage or failure, beam or column flexure-shear response. Meets the following requirements: (1) Column Pu < 0.3Agf'c Costing is on a per joint basis. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 4 | DS1 | DS2 | DS3 | DS4 |  | Sequential | Sequential | Mutually Exclusive | Mutually Exclusive |  | Seq(DS1,DS2,MutEx(DS3,DS4)) | 115 | EA 1 | YES | NO | Beams or joints exhibit residual crack widths > 0.06 in. No significant spalling. No fracture or buckling of reinforcing. | Beams or joints exhibit residual crack widths > 0.06 in. Spalling of cover concrete exposes beam and joint transverse reinforcement but not longitudinal reinforcement. No fracture or buckling of reinforcing. | Beams or joints exhibit residual crack widths > 0.06 in. Spalling of cover concrete exposes a significant length of beam longitudinal reinforcement. Crushing of core concrete may occur. Fracture or buckling of reinforcing requiring replacement may occur. | Beams or joints exhibit residual crack widths > 0.06 in. Spalling of cover concrete exposes beam and joint transverse reinforcement but not longitudinal reinforcement. No fracture or buckling of reinforcing. |  | 1 | 1 | 0.4 | 0.6 |  | 0.02 | 0.025 | 0.035 | 0.035 |  | 0.06 | 0.3 | 0.2 | 0.3 |  | 0.4 | 0.1 | 0.1 | 0.1 |  | 0.4 | 0.3 | 0.3 | 0.3 |  | NO | YES | Average | Average | Superior | Superior | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 8 feet either side of damaged area. Clean area adjacent to the damaged concrete. Prepare spalled concrete and adjacent cracks, as necessary, to be patched and to receive the epoxy injection. Patch concrete with grout. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems as necessary. | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 15 feet either side of damaged area. Shore damaged member(s) a min one level below (more levels may be required). Remove damaged concrete at least 1 inch beyond the exposed reinforcing steel. Place concrete forms. Place concrete. Remove forms. Remove shores after one week. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary). | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 15 feet either side of damaged component. Shore damaged member(s) a minimum of one level below (more levels may be required). Remove damaged component. Place and splice (as necessary) new reinforcing steel to existing, undamaged reinforcing. Place concrete forms. Place concrete. Remove forms. Remove shores after one week. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary). | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 15 feet either side of damaged area. Shore damaged member(s) a min one level below (more levels may be required). Remove damaged concrete at least 1 inch beyond the exposed reinforcing steel. Place concrete forms. Place concrete. Remove forms. Remove shores after one week. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary). |  | NO | NO | NO | NO |  | NO | NO | NO | NO |  | Not Applicable | Not Applicable | Not Applicable | Not Applicable |  | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 |  |  | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 |  |  | NO | NO | YES | NO |  | 0% | 0% | 20% | 0% |  | 0 | 0 | 0.5 | 0 |  | Note: DS4 is a copy of DS2 to create a mutually exclusive compliment to DS3. | Not Given | By User | By User | Laura Lowes | B1041.001a-DS1-1.JPG | B1041.001a-DS2-1.JPG | B1041.001a-DS3-1.JPG | B1041.001a-DS2-1.JPG |  | No | 2011-08-24 Changed DS4 beta from 0.4 to 0.3 to avoid negative probability. | YES
B1041.022a | B1041.022a | ACI 318 IMF, Conc Col & Bm = 24" x 36", Beam one side | ACI318 IMF, joint shear damage or failure, beam or column flexure-shear response. Meets the following requirements: (1) Column Pu < 0.3Agf'c Costing is on a per joint basis. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 4 | DS1 | DS2 | DS3 | DS4 |  | Sequential | Sequential | Mutually Exclusive | Mutually Exclusive |  | Seq(DS1,DS2,MutEx(DS3,DS4)) | 116 | EA 1 | YES | NO | Beams or joints exhibit residual crack widths > 0.06 in. No significant spalling. No fracture or buckling of reinforcing. | Beams or joints exhibit residual crack widths > 0.06 in. Spalling of cover concrete exposes beam and joint transverse reinforcement but not longitudinal reinforcement. No fracture or buckling of reinforcing. | Beams or joints exhibit residual crack widths > 0.06 in. Spalling of cover concrete exposes a significant length of beam longitudinal reinforcement. Crushing of core concrete may occur. Fracture or buckling of reinforcing requiring replacement may occur. | Beams or joints exhibit residual crack widths > 0.06 in. Spalling of cover concrete exposes beam and joint transverse reinforcement but not longitudinal reinforcement. No fracture or buckling of reinforcing. |  | 1 | 1 | 0.4 | 0.6 |  | 0.02 | 0.025 | 0.035 | 0.035 |  | 0.06 | 0.3 | 0.2 | 0.3 |  | 0.4 | 0.1 | 0.1 | 0.1 |  | 0.4 | 0.3 | 0.3 | 0.3 |  | NO | YES | Average | Average | Superior | Superior | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 8 feet either side of damaged area. Clean area adjacent to the damaged concrete. Prepare spalled concrete and adjacent cracks, as necessary, to be patched and to receive the epoxy injection. Patch concrete with grout. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems as necessary. | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 15 feet either side of damaged area. Shore damaged member(s) a min one level below (more levels may be required). Remove damaged concrete at least 1 inch beyond the exposed reinforcing steel. Place concrete forms. Place concrete. Remove forms. Remove shores after one week. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary). | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 15 feet either side of damaged component. Shore damaged member(s) a minimum of one level below (more levels may be required). Remove damaged component. Place and splice (as necessary) new reinforcing steel to existing, undamaged reinforcing. Place concrete forms. Place concrete. Remove forms. Remove shores after one week. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary). | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 15 feet either side of damaged area. Shore damaged member(s) a min one level below (more levels may be required). Remove damaged concrete at least 1 inch beyond the exposed reinforcing steel. Place concrete forms. Place concrete. Remove forms. Remove shores after one week. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary). |  | NO | NO | NO | NO |  | NO | NO | NO | NO |  | Not Applicable | Not Applicable | Not Applicable | Not Applicable |  | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 |  |  | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 |  |  | NO | NO | YES | NO |  | 0% | 0% | 20% | 0% |  | 0 | 0 | 0.5 | 0 |  | Note: DS4 is a copy of DS2 to create a mutually exclusive compliment to DS3. | Not Given | By User | By User | Laura Lowes | B1041.001a-DS1-1.JPG | B1041.001a-DS2-1.JPG | B1041.001a-DS3-1.JPG | B1041.001a-DS2-1.JPG |  | No | 2011-08-24 Changed DS4 beta from 0.4 to 0.3 to avoid negative probability. | YES
B1041.022b | B1041.022b | ACI 318 IMF, Conc Col & Bm = 24" x 36", Beam both sides | ACI318 IMF, joint shear damage or failure, beam or column flexure-shear response. Meets the following requirements: (1) Column Pu < 0.3Agf'c Costing is on a per joint basis. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 4 | DS1 | DS2 | DS3 | DS4 |  | Sequential | Sequential | Mutually Exclusive | Mutually Exclusive |  | Seq(DS1,DS2,MutEx(DS3,DS4)) | 117 | EA 1 | YES | NO | Beams or joints exhibit residual crack widths > 0.06 in. No significant spalling. No fracture or buckling of reinforcing. | Beams or joints exhibit residual crack widths > 0.06 in. Spalling of cover concrete exposes beam and joint transverse reinforcement but not longitudinal reinforcement. No fracture or buckling of reinforcing. | Beams or joints exhibit residual crack widths > 0.06 in. Spalling of cover concrete exposes a significant length of beam longitudinal reinforcement. Crushing of core concrete may occur. Fracture or buckling of reinforcing requiring replacement may occur. | Beams or joints exhibit residual crack widths > 0.06 in. Spalling of cover concrete exposes beam and joint transverse reinforcement but not longitudinal reinforcement. No fracture or buckling of reinforcing. |  | 1 | 1 | 0.4 | 0.6 |  | 0.02 | 0.025 | 0.035 | 0.035 |  | 0.06 | 0.3 | 0.2 | 0.3 |  | 0.4 | 0.1 | 0.1 | 0.1 |  | 0.4 | 0.3 | 0.3 | 0.3 |  | NO | YES | Average | Average | Superior | Superior | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 8 feet either side of damaged area. Clean area adjacent to the damaged concrete. Prepare spalled concrete and adjacent cracks, as necessary, to be patched and to receive the epoxy injection. Patch concrete with grout. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems as necessary. | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 15 feet either side of damaged area. Shore damaged member(s) a min one level below (more levels may be required). Remove damaged concrete at least 1 inch beyond the exposed reinforcing steel. Place concrete forms. Place concrete. Remove forms. Remove shores after one week. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary). | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 15 feet either side of damaged component. Shore damaged member(s) a minimum of one level below (more levels may be required). Remove damaged component. Place and splice (as necessary) new reinforcing steel to existing, undamaged reinforcing. Place concrete forms. Place concrete. Remove forms. Remove shores after one week. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary). | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 15 feet either side of damaged area. Shore damaged member(s) a min one level below (more levels may be required). Remove damaged concrete at least 1 inch beyond the exposed reinforcing steel. Place concrete forms. Place concrete. Remove forms. Remove shores after one week. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary). |  | NO | NO | NO | NO |  | NO | NO | NO | NO |  | Not Applicable | Not Applicable | Not Applicable | Not Applicable |  | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 |  |  | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 |  |  | NO | NO | YES | NO |  | 0% | 0% | 20% | 0% |  | 0 | 0 | 0.5 | 0 |  | Note: DS4 is a copy of DS2 to create a mutually exclusive compliment to DS3. | Not Given | By User | By User | Laura Lowes | B1041.001a-DS1-1.JPG | B1041.001a-DS2-1.JPG | B1041.001a-DS3-1.JPG | B1041.001a-DS2-1.JPG |  | No | 2011-08-24 Changed DS4 beta from 0.4 to 0.3 to avoid negative probability. | YES
B1041.023a | B1041.023a | ACI 318 IMF, Conc Col & Bm = 36" x 36", Beam one side | ACI318 IMF, joint shear damage or failure, beam or column flexure-shear response. Meets the following requirements: (1) Column Pu < 0.3Agf'c Costing is on a per joint basis. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 4 | DS1 | DS2 | DS3 | DS4 |  | Sequential | Sequential | Mutually Exclusive | Mutually Exclusive |  | Seq(DS1,DS2,MutEx(DS3,DS4)) | 118 | EA 1 | YES | NO | Beams or joints exhibit residual crack widths > 0.06 in. No significant spalling. No fracture or buckling of reinforcing. | Beams or joints exhibit residual crack widths > 0.06 in. Spalling of cover concrete exposes beam and joint transverse reinforcement but not longitudinal reinforcement. No fracture or buckling of reinforcing. | Beams or joints exhibit residual crack widths > 0.06 in. Spalling of cover concrete exposes a significant length of beam longitudinal reinforcement. Crushing of core concrete may occur. Fracture or buckling of reinforcing requiring replacement may occur. | Beams or joints exhibit residual crack widths > 0.06 in. Spalling of cover concrete exposes beam and joint transverse reinforcement but not longitudinal reinforcement. No fracture or buckling of reinforcing. |  | 1 | 1 | 0.4 | 0.6 |  | 0.02 | 0.025 | 0.035 | 0.035 |  | 0.06 | 0.3 | 0.2 | 0.3 |  | 0.4 | 0.1 | 0.1 | 0.1 |  | 0.4 | 0.3 | 0.3 | 0.3 |  | NO | YES | Average | Average | Superior | Superior | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 8 feet either side of damaged area. Clean area adjacent to the damaged concrete. Prepare spalled concrete and adjacent cracks, as necessary, to be patched and to receive the epoxy injection. Patch concrete with grout. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems as necessary. | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 15 feet either side of damaged area. Shore damaged member(s) a min one level below (more levels may be required). Remove damaged concrete at least 1 inch beyond the exposed reinforcing steel. Place concrete forms. Place concrete. Remove forms. Remove shores after one week. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary). | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 15 feet either side of damaged component. Shore damaged member(s) a minimum of one level below (more levels may be required). Remove damaged component. Place and splice (as necessary) new reinforcing steel to existing, undamaged reinforcing. Place concrete forms. Place concrete. Remove forms. Remove shores after one week. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary). | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 15 feet either side of damaged area. Shore damaged member(s) a min one level below (more levels may be required). Remove damaged concrete at least 1 inch beyond the exposed reinforcing steel. Place concrete forms. Place concrete. Remove forms. Remove shores after one week. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary). |  | NO | NO | NO | NO |  | NO | NO | NO | NO |  | Not Applicable | Not Applicable | Not Applicable | Not Applicable |  | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 |  |  | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 |  |  | NO | NO | YES | NO |  | 0% | 0% | 20% | 0% |  | 0 | 0 | 0.5 | 0 |  | Note: DS4 is a copy of DS2 to create a mutually exclusive compliment to DS3. | Not Given | By User | By User | Laura Lowes | B1041.001a-DS1-1.JPG | B1041.001a-DS2-1.JPG | B1041.001a-DS3-1.JPG | B1041.001a-DS2-1.JPG |  | No | 2011-08-24 Changed DS4 beta from 0.4 to 0.3 to avoid negative probability. | YES
B1041.023b | B1041.023b | ACI 318 IMF, Conc Col & Bm = 36" x 36", Beam both sides | ACI318 IMF, joint shear damage or failure, beam or column flexure-shear response. Meets the following requirements: (1) Column Pu < 0.3Agf'c Costing is on a per joint basis. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 4 | DS1 | DS2 | DS3 | DS4 |  | Sequential | Sequential | Mutually Exclusive | Mutually Exclusive |  | Seq(DS1,DS2,MutEx(DS3,DS4)) | 119 | EA 1 | YES | NO | Beams or joints exhibit residual crack widths > 0.06 in. No significant spalling. No fracture or buckling of reinforcing. | Beams or joints exhibit residual crack widths > 0.06 in. Spalling of cover concrete exposes beam and joint transverse reinforcement but not longitudinal reinforcement. No fracture or buckling of reinforcing. | Beams or joints exhibit residual crack widths > 0.06 in. Spalling of cover concrete exposes a significant length of beam longitudinal reinforcement. Crushing of core concrete may occur. Fracture or buckling of reinforcing requiring replacement may occur. | Beams or joints exhibit residual crack widths > 0.06 in. Spalling of cover concrete exposes beam and joint transverse reinforcement but not longitudinal reinforcement. No fracture or buckling of reinforcing. |  | 1 | 1 | 0.4 | 0.6 |  | 0.02 | 0.025 | 0.035 | 0.035 |  | 0.06 | 0.3 | 0.2 | 0.3 |  | 0.4 | 0.1 | 0.1 | 0.1 |  | 0.4 | 0.3 | 0.3 | 0.3 |  | NO | YES | Average | Average | Superior | Superior | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 8 feet either side of damaged area. Clean area adjacent to the damaged concrete. Prepare spalled concrete and adjacent cracks, as necessary, to be patched and to receive the epoxy injection. Patch concrete with grout. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems as necessary. | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 15 feet either side of damaged area. Shore damaged member(s) a min one level below (more levels may be required). Remove damaged concrete at least 1 inch beyond the exposed reinforcing steel. Place concrete forms. Place concrete. Remove forms. Remove shores after one week. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary). | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 15 feet either side of damaged component. Shore damaged member(s) a minimum of one level below (more levels may be required). Remove damaged component. Place and splice (as necessary) new reinforcing steel to existing, undamaged reinforcing. Place concrete forms. Place concrete. Remove forms. Remove shores after one week. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary). | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 15 feet either side of damaged area. Shore damaged member(s) a min one level below (more levels may be required). Remove damaged concrete at least 1 inch beyond the exposed reinforcing steel. Place concrete forms. Place concrete. Remove forms. Remove shores after one week. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary). |  | NO | NO | NO | NO |  | NO | NO | NO | NO |  | Not Applicable | Not Applicable | Not Applicable | Not Applicable |  | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 |  |  | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 |  |  | NO | NO | YES | NO |  | 0% | 0% | 20% | 0% |  | 0 | 0 | 0.5 | 0 |  | Note: DS4 is a copy of DS2 to create a mutually exclusive compliment to DS3. | Not Given | By User | By User | Laura Lowes | B1041.001a-DS1-1.JPG | B1041.001a-DS2-1.JPG | B1041.001a-DS3-1.JPG | B1041.001a-DS2-1.JPG |  | No | 2011-08-24 Changed DS4 beta from 0.4 to 0.3 to avoid negative probability. | YES
B1041.031a | B1041.031a | ACI 318 OMF with weak joints and beam flexural response, Conc Col & Bm = 24" x 24", Beam one side | ACI318 OMF, joint shear failure, beam flexural response. Meets the following requirements: (1) Sum Mcol / Sum Mbeam > 1.2, (2) Beam Vn > Veq, (3) Column Vn > Veq. Costing is on a per joint basis. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 120 | EA 1 | YES | NO | Beams or joints exhibit residual crack widths > 0.06 in. No significant spalling. No fracture or buckling of reinforcing. | Beams or joints exhibit residual crack widths > 0.06 in. Spalling of cover concrete exposes beam and joint transverse reinforcement but not longitudinal reinforcement. No fracture or buckling of reinforcing. | Beams or joints exhibit residual crack widths > 0.06 in. Spalling of cover concrete exposes a significant length of beam longitudinal reinforcement. Crushing of core concrete may occur. Fracture or buckling of reinforcing requiring replacement may occur. |  |  | 1 | 1 | 1 |  |  | 0.0175 | 0.0225 | 0.0322 |  |  | 0.2 | 0.27 | 0.32 |  |  | 0.3 | 0.13 | 0.15 |  |  | 0.4 | 0.4 | 0.4 |  |  | NO | YES | Average | Average | Superior | Superior | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 8 feet either side of damaged area. Clean area adjacent to the damaged concrete. Prepare spalled concrete and adjacent cracks, as necessary, to be patched and to receive the epoxy injection. Patch concrete with grout. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems as necessary. | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 15 feet either side of damaged area. Shore damaged member(s) a min one level below (more levels may be required). Remove damaged concrete at least 1 inch beyond the exposed reinforcing steel. Place concrete forms. Place concrete. Remove forms. Remove shores after one week. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary). | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 15 feet either side of damaged component. Shore damaged member(s) a minimum of one level below (more levels may be required). Remove damaged component. Place and splice (as necessary) new reinforcing steel to existing, undamaged reinforcing. Place concrete forms. Place concrete. Remove forms. Remove shores after one week. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary). |  |  | NO | NO | NO |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | NO | YES |  |  | 0% | 0% | 20% |  |  | 0 | 0 | 0.5 |  |  | None | Not Given | By User | By User | Laura Lowes | B1041.031a-DS1-1.JPG | B1041.031a-DS2-1.JPG | B1041.031a-DS3-1.JPG |  |  | No | 2011-08-24 Changed DS2 beta from 0.3 to 0.4 to avoid negative probability beyond 1% story drift. | YES
B1041.031b | B1041.031b | ACI 318 OMF with weak joints and beam flexural response, Conc Col & Bm = 24" x 24", Beam both sides | ACI318 OMF, joint shear failure, beam flexural response. Meets the following requirements: (1) Sum Mcol / Sum Mbeam > 1.2, (2) Beam Vn > Veq, (3) Column Vn > Veq. Costing is on a per joint basis. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 121 | EA 1 | YES | NO | Beams or joints exhibit residual crack widths > 0.06 in. No significant spalling. No fracture or buckling of reinforcing. | Beams or joints exhibit residual crack widths > 0.06 in. Spalling of cover concrete exposes beam and joint transverse reinforcement but not longitudinal reinforcement. No fracture or buckling of reinforcing. | Beams or joints exhibit residual crack widths > 0.06 in. Spalling of cover concrete exposes a significant length of beam longitudinal reinforcement. Crushing of core concrete may occur. Fracture or buckling of reinforcing requiring replacement may occur. |  |  | 1 | 1 | 1 |  |  | 0.0175 | 0.0225 | 0.0322 |  |  | 0.2 | 0.27 | 0.32 |  |  | 0.3 | 0.13 | 0.15 |  |  | 0.4 | 0.4 | 0.4 |  |  | NO | YES | Average | Average | Superior | Superior | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 8 feet either side of damaged area. Clean area adjacent to the damaged concrete. Prepare spalled concrete and adjacent cracks, as necessary, to be patched and to receive the epoxy injection. Patch concrete with grout. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems as necessary. | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 15 feet either side of damaged area. Shore damaged member(s) a min one level below (more levels may be required). Remove damaged concrete at least 1 inch beyond the exposed reinforcing steel. Place concrete forms. Place concrete. Remove forms. Remove shores after one week. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary). | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 15 feet either side of damaged component. Shore damaged member(s) a minimum of one level below (more levels may be required). Remove damaged component. Place and splice (as necessary) new reinforcing steel to existing, undamaged reinforcing. Place concrete forms. Place concrete. Remove forms. Remove shores after one week. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary). |  |  | NO | NO | NO |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | NO | YES |  |  | 0% | 0% | 20% |  |  | 0 | 0 | 0.5 |  |  | None | Not Given | By User | By User | Laura Lowes | B1041.031a-DS1-1.JPG | B1041.031a-DS2-1.JPG | B1041.031a-DS3-1.JPG |  |  | No | 2011-08-24 Changed DS2 beta from 0.3 to 0.4 to avoid negative probability beyond 1% story drift. | YES
B1041.032a | B1041.032a | ACI 318 OMF with weak joints and beam flexural response, Conc Col & Bm = 24" x 36", Beam one side | ACI318 OMF, joint shear failure, beam flexural response. Meets the following requirements: (1) Sum Mcol / Sum Mbeam > 1.2, (2) Beam Vn > Veq, (3) Column Vn > Veq. Costing is on a per joint basis. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 122 | EA 1 | YES | NO | Beams or joints exhibit residual crack widths > 0.06 in. No significant spalling. No fracture or buckling of reinforcing. | Beams or joints exhibit residual crack widths > 0.06 in. Spalling of cover concrete exposes beam and joint transverse reinforcement but not longitudinal reinforcement. No fracture or buckling of reinforcing. | Beams or joints exhibit residual crack widths > 0.06 in. Spalling of cover concrete exposes a significant length of beam longitudinal reinforcement. Crushing of core concrete may occur. Fracture or buckling of reinforcing requiring replacement may occur. |  |  | 1 | 1 | 1 |  |  | 0.0175 | 0.0225 | 0.0322 |  |  | 0.2 | 0.27 | 0.32 |  |  | 0.3 | 0.13 | 0.15 |  |  | 0.4 | 0.4 | 0.4 |  |  | NO | YES | Average | Average | Superior | Superior | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 8 feet either side of damaged area. Clean area adjacent to the damaged concrete. Prepare spalled concrete and adjacent cracks, as necessary, to be patched and to receive the epoxy injection. Patch concrete with grout. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems as necessary. | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 15 feet either side of damaged area. Shore damaged member(s) a min one level below (more levels may be required). Remove damaged concrete at least 1 inch beyond the exposed reinforcing steel. Place concrete forms. Place concrete. Remove forms. Remove shores after one week. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary). | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 15 feet either side of damaged component. Shore damaged member(s) a minimum of one level below (more levels may be required). Remove damaged component. Place and splice (as necessary) new reinforcing steel to existing, undamaged reinforcing. Place concrete forms. Place concrete. Remove forms. Remove shores after one week. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary). |  |  | NO | NO | NO |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | NO | YES |  |  | 0% | 0% | 20% |  |  | 0 | 0 | 0.5 |  |  | None | Not Given | By User | By User | Laura Lowes | B1041.031a-DS1-1.JPG | B1041.031a-DS2-1.JPG | B1041.031a-DS3-1.JPG |  |  | No | 2011-08-24 Changed DS2 beta from 0.3 to 0.4 to avoid negative probability beyond 1% story drift. | YES
B1041.032b | B1041.032b | ACI 318 OMF with weak joints and beam flexural response, Conc Col & Bm = 24" x 36", Beam both sides | ACI318 OMF, joint shear failure, beam flexural response. Meets the following requirements: (1) Sum Mcol / Sum Mbeam > 1.2, (2) Beam Vn > Veq, (3) Column Vn > Veq. Costing is on a per joint basis. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 123 | EA 1 | YES | NO | Beams or joints exhibit residual crack widths > 0.06 in. No significant spalling. No fracture or buckling of reinforcing. | Beams or joints exhibit residual crack widths > 0.06 in. Spalling of cover concrete exposes beam and joint transverse reinforcement but not longitudinal reinforcement. No fracture or buckling of reinforcing. | Beams or joints exhibit residual crack widths > 0.06 in. Spalling of cover concrete exposes a significant length of beam longitudinal reinforcement. Crushing of core concrete may occur. Fracture or buckling of reinforcing requiring replacement may occur. |  |  | 1 | 1 | 1 |  |  | 0.0175 | 0.0225 | 0.0322 |  |  | 0.2 | 0.27 | 0.32 |  |  | 0.3 | 0.13 | 0.15 |  |  | 0.4 | 0.4 | 0.4 |  |  | NO | YES | Average | Average | Superior | Superior | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 8 feet either side of damaged area. Clean area adjacent to the damaged concrete. Prepare spalled concrete and adjacent cracks, as necessary, to be patched and to receive the epoxy injection. Patch concrete with grout. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems as necessary. | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 15 feet either side of damaged area. Shore damaged member(s) a min one level below (more levels may be required). Remove damaged concrete at least 1 inch beyond the exposed reinforcing steel. Place concrete forms. Place concrete. Remove forms. Remove shores after one week. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary). | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 15 feet either side of damaged component. Shore damaged member(s) a minimum of one level below (more levels may be required). Remove damaged component. Place and splice (as necessary) new reinforcing steel to existing, undamaged reinforcing. Place concrete forms. Place concrete. Remove forms. Remove shores after one week. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary). |  |  | NO | NO | NO |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | NO | YES |  |  | 0% | 0% | 20% |  |  | 0 | 0 | 0.5 |  |  | None | Not Given | By User | By User | Laura Lowes | B1041.031a-DS1-1.JPG | B1041.031a-DS2-1.JPG | B1041.031a-DS3-1.JPG |  |  | No | 2011-08-24 Changed DS2 beta from 0.3 to 0.4 to avoid negative probability beyond 1% story drift. | YES
B1041.033a | B1041.033a | ACI 318 OMF with weak joints and beam flexural response, Conc Col & Bm = 36" x 36", Beam one side | ACI318 OMF, joint shear failure, beam flexural response. Meets the following requirements: (1) Sum Mcol / Sum Mbeam > 1.2, (2) Beam Vn > Veq, (3) Column Vn > Veq. Costing is on a per joint basis. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 124 | EA 1 | YES | NO | Beams or joints exhibit residual crack widths > 0.06 in. No significant spalling. No fracture or buckling of reinforcing. | Beams or joints exhibit residual crack widths > 0.06 in. Spalling of cover concrete exposes beam and joint transverse reinforcement but not longitudinal reinforcement. No fracture or buckling of reinforcing. | Beams or joints exhibit residual crack widths > 0.06 in. Spalling of cover concrete exposes a significant length of beam longitudinal reinforcement. Crushing of core concrete may occur. Fracture or buckling of reinforcing requiring replacement may occur. |  |  | 1 | 1 | 1 |  |  | 0.0175 | 0.0225 | 0.0322 |  |  | 0.2 | 0.27 | 0.32 |  |  | 0.3 | 0.13 | 0.15 |  |  | 0.4 | 0.4 | 0.4 |  |  | NO | YES | Average | Average | Superior | Superior | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 8 feet either side of damaged area. Clean area adjacent to the damaged concrete. Prepare spalled concrete and adjacent cracks, as necessary, to be patched and to receive the epoxy injection. Patch concrete with grout. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems as necessary. | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 15 feet either side of damaged area. Shore damaged member(s) a min one level below (more levels may be required). Remove damaged concrete at least 1 inch beyond the exposed reinforcing steel. Place concrete forms. Place concrete. Remove forms. Remove shores after one week. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary). | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 15 feet either side of damaged component. Shore damaged member(s) a minimum of one level below (more levels may be required). Remove damaged component. Place and splice (as necessary) new reinforcing steel to existing, undamaged reinforcing. Place concrete forms. Place concrete. Remove forms. Remove shores after one week. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary). |  |  | NO | NO | NO |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | NO | YES |  |  | 0% | 0% | 20% |  |  | 0 | 0 | 0.5 |  |  | None | Not Given | By User | By User | Laura Lowes | B1041.031a-DS1-1.JPG | B1041.031a-DS2-1.JPG | B1041.031a-DS3-1.JPG |  |  | No | 2011-08-24 Changed DS2 beta from 0.3 to 0.4 to avoid negative probability beyond 1% story drift. | YES
B1041.033b | B1041.033b | ACI 318 OMF with weak joints and beam flexural response, Conc Col & Bm = 36" x 36", Beam both sides | ACI318 OMF, joint shear failure, beam flexural response. Meets the following requirements: (1) Sum Mcol / Sum Mbeam > 1.2, (2) Beam Vn > Veq, (3) Column Vn > Veq. Costing is on a per joint basis. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 125 | EA 1 | YES | NO | Beams or joints exhibit residual crack widths > 0.06 in. No significant spalling. No fracture or buckling of reinforcing. | Beams or joints exhibit residual crack widths > 0.06 in. Spalling of cover concrete exposes beam and joint transverse reinforcement but not longitudinal reinforcement. No fracture or buckling of reinforcing. | Beams or joints exhibit residual crack widths > 0.06 in. Spalling of cover concrete exposes a significant length of beam longitudinal reinforcement. Crushing of core concrete may occur. Fracture or buckling of reinforcing requiring replacement may occur. |  |  | 1 | 1 | 1 |  |  | 0.0175 | 0.0225 | 0.0322 |  |  | 0.2 | 0.27 | 0.32 |  |  | 0.3 | 0.13 | 0.15 |  |  | 0.4 | 0.4 | 0.4 |  |  | NO | YES | Average | Average | Superior | Superior | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 8 feet either side of damaged area. Clean area adjacent to the damaged concrete. Prepare spalled concrete and adjacent cracks, as necessary, to be patched and to receive the epoxy injection. Patch concrete with grout. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems as necessary. | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 15 feet either side of damaged area. Shore damaged member(s) a min one level below (more levels may be required). Remove damaged concrete at least 1 inch beyond the exposed reinforcing steel. Place concrete forms. Place concrete. Remove forms. Remove shores after one week. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary). | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 15 feet either side of damaged component. Shore damaged member(s) a minimum of one level below (more levels may be required). Remove damaged component. Place and splice (as necessary) new reinforcing steel to existing, undamaged reinforcing. Place concrete forms. Place concrete. Remove forms. Remove shores after one week. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary). |  |  | NO | NO | NO |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | NO | YES |  |  | 0% | 0% | 20% |  |  | 0 | 0 | 0.5 |  |  | None | Not Given | By User | By User | Laura Lowes | B1041.031a-DS1-1.JPG | B1041.031a-DS2-1.JPG | B1041.031a-DS3-1.JPG |  |  | No | 2011-08-24 Changed DS2 beta from 0.3 to 0.4 to avoid negative probability beyond 1% story drift. | YES
B1041.041a | B1041.041a | ACI 318 OMF with weak joints and column flexural response, Conc Col & Bm = 24" x 24", Beam one side | ACI318 OMF, joint shear failure, beam flexural response. Meets the following requirements: (1) Sum Mcol / Sum Mbeam > 1.2, (2) Beam Vn > Veq, (3) Column Vn > Veq. Costing is on a per joint basis. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 126 | EA 1 | YES | NO | Concrete Cracking: beams, joints or possibly Residual concrete crack widths exceed 0.06 in. (1.5 mm). Column exhibit residual crack widths that require epoxy injection. | Concrete Spalling: slabs, beams, joints or possibly columns exhibit spalling of cover concrete that exposes transverse but not longitudinal reinforcing steel. Spalling of cover concrete possibly exposing transverse reinforcement. | Concrete Crushing: slabs, beams or joints. Spalling of beam, column or joint cover concrete exposes longitudinal reinforcement OR strength loss initiates in laboratory testing. exhibit concrete spalling that exposes longitudinal steel or crushing of core concrete. |  |  | 1 | 1 | 1 |  |  | 0.015 | 0.0175 | 0.02 |  |  | Not Specified | 0.28 | 0.18 |  |  | 0.4 | 0.15 | 0.35 |  |  | 0.4 | 0.4 | 0.4 |  |  | NO | YES | Average | Average | Superior | Superior | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 8 feet either side of damaged area. Clean area adjacent to the damaged concrete. Prepare spalled concrete and adjacent cracks, as necessary, to be patched and to receive the epoxy injection. Patch concrete with grout. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems as necessary. | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 15 feet either side of damaged area. Shore damaged member(s) a minimum of one level below (more levels may be required). Remove damaged concrete at least 1 inch beyond the exposed reinforcing steel. Place concrete forms. Place concrete. Remove forms. Remove shores after one week. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary). | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 15 feet either side of damaged component. Shore damaged member(s) a minimum of one level below (more levels may be required). Remove damaged component. Place and splice (as necessary) new reinforcing steel to existing, undamaged reinforcing. Place concrete forms. Place concrete. Remove forms. Remove shores after one week. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary). |  |  | NO | NO | NO |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | NO | YES |  |  | 0% | 0% | 20% |  |  | 0 | 0 | 0.5 |  |  | None | Not Given | By User | By User | Laura Lowes | none | none | none |  |  | No | 2011-08-24 Changed DS2 beta from 0.3 to 0.4 to avoid negative probability beyond 1% story drift. | YES
B1041.041b | B1041.041b | ACI 318 OMF with weak joints and column flexural response, Conc Col & Bm = 24" x 24", Beam both sides | ACI318 OMF, joint shear failure, beam flexural response. Meets the following requirements: (1) Sum Mcol / Sum Mbeam > 1.2, (2) Beam Vn > Veq, (3) Column Vn > Veq. Costing is on a per joint basis. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 127 | EA 1 | YES | NO | Concrete Cracking: beams, joints or possibly Residual concrete crack widths exceed 0.06 in. (1.5 mm). Column exhibit residual crack widths that require epoxy injection. | Concrete Spalling: slabs, beams, joints or possibly columns exhibit spalling of cover concrete that exposes transverse but not longitudinal reinforcing steel. Spalling of cover concrete possibly exposing transverse reinforcement. | Concrete Crushing: slabs, beams or joints. Spalling of beam, column or joint cover concrete exposes longitudinal reinforcement OR strength loss initiates in laboratory testing. exhibit concrete spalling that exposes longitudinal steel or crushing of core concrete. |  |  | 1 | 1 | 1 |  |  | 0.015 | 0.0175 | 0.02 |  |  | Not Specified | 0.28 | 0.18 |  |  | 0.4 | 0.15 | 0.35 |  |  | 0.4 | 0.4 | 0.4 |  |  | NO | YES | Average | Average | Superior | Superior | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 8 feet either side of damaged area. Clean area adjacent to the damaged concrete. Prepare spalled concrete and adjacent cracks, as necessary, to be patched and to receive the epoxy injection. Patch concrete with grout. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems as necessary. | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 15 feet either side of damaged area. Shore damaged member(s) a minimum of one level below (more levels may be required). Remove damaged concrete at least 1 inch beyond the exposed reinforcing steel. Place concrete forms. Place concrete. Remove forms. Remove shores after one week. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary). | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 15 feet either side of damaged component. Shore damaged member(s) a minimum of one level below (more levels may be required). Remove damaged component. Place and splice (as necessary) new reinforcing steel to existing, undamaged reinforcing. Place concrete forms. Place concrete. Remove forms. Remove shores after one week. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary). |  |  | NO | NO | NO |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | NO | YES |  |  | 0% | 0% | 20% |  |  | 0 | 0 | 0.5 |  |  | None | Not Given | By User | By User | Laura Lowes | none | none | none |  |  | No | 2011-08-24 Changed DS2 beta from 0.3 to 0.4 to avoid negative probability beyond 1% story drift. | YES
B1041.042a | B1041.042a | ACI 318 OMF with weak joints and column flexural response, Conc Col & Bm = 24" x 36", Beam one side | ACI318 OMF, joint shear failure, beam flexural response. Meets the following requirements: (1) Sum Mcol / Sum Mbeam > 1.2, (2) Beam Vn > Veq, (3) Column Vn > Veq. Costing is on a per joint basis. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 128 | EA 1 | YES | NO | Concrete Cracking: beams, joints or possibly Residual concrete crack widths exceed 0.06 in. (1.5 mm). Column exhibit residual crack widths that require epoxy injection. | Concrete Spalling: slabs, beams, joints or possibly columns exhibit spalling of cover concrete that exposes transverse but not longitudinal reinforcing steel. Spalling of cover concrete possibly exposing transverse reinforcement. | Concrete Crushing: slabs, beams or joints. Spalling of beam, column or joint cover concrete exposes longitudinal reinforcement OR strength loss initiates in laboratory testing. exhibit concrete spalling that exposes longitudinal steel or crushing of core concrete. |  |  | 1 | 1 | 1 |  |  | 0.015 | 0.0175 | 0.02 |  |  | Not Specified | 0.28 | 0.18 |  |  | 0.4 | 0.15 | 0.35 |  |  | 0.4 | 0.4 | 0.4 |  |  | NO | YES | Average | Average | Superior | Superior | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 8 feet either side of damaged area. Clean area adjacent to the damaged concrete. Prepare spalled concrete and adjacent cracks, as necessary, to be patched and to receive the epoxy injection. Patch concrete with grout. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems as necessary. | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 15 feet either side of damaged area. Shore damaged member(s) a minimum of one level below (more levels may be required). Remove damaged concrete at least 1 inch beyond the exposed reinforcing steel. Place concrete forms. Place concrete. Remove forms. Remove shores after one week. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary). | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 15 feet either side of damaged component. Shore damaged member(s) a minimum of one level below (more levels may be required). Remove damaged component. Place and splice (as necessary) new reinforcing steel to existing, undamaged reinforcing. Place concrete forms. Place concrete. Remove forms. Remove shores after one week. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary). |  |  | NO | NO | NO |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | NO | YES |  |  | 0% | 0% | 20% |  |  | 0 | 0 | 0.5 |  |  | None | Not Given | By User | By User | Laura Lowes | none | none | none |  |  | No | 2011-08-24 Changed DS2 beta from 0.3 to 0.4 to avoid negative probability beyond 1% story drift. | YES
B1041.042b | B1041.042b | ACI 318 OMF with weak joints and column flexural response, Conc Col & Bm = 24" x 36", Beam both sides | ACI318 OMF, joint shear failure, beam flexural response. Meets the following requirements: (1) Sum Mcol / Sum Mbeam > 1.2, (2) Beam Vn > Veq, (3) Column Vn > Veq. Costing is on a per joint basis. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 129 | EA 1 | YES | NO | Concrete Cracking: beams, joints or possibly Residual concrete crack widths exceed 0.06 in. (1.5 mm). Column exhibit residual crack widths that require epoxy injection. | Concrete Spalling: slabs, beams, joints or possibly columns exhibit spalling of cover concrete that exposes transverse but not longitudinal reinforcing steel. Spalling of cover concrete possibly exposing transverse reinforcement. | Concrete Crushing: slabs, beams or joints. Spalling of beam, column or joint cover concrete exposes longitudinal reinforcement OR strength loss initiates in laboratory testing. exhibit concrete spalling that exposes longitudinal steel or crushing of core concrete. |  |  | 1 | 1 | 1 |  |  | 0.015 | 0.0175 | 0.02 |  |  | Not Specified | 0.28 | 0.18 |  |  | 0.4 | 0.15 | 0.35 |  |  | 0.4 | 0.4 | 0.4 |  |  | NO | YES | Average | Average | Superior | Superior | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 8 feet either side of damaged area. Clean area adjacent to the damaged concrete. Prepare spalled concrete and adjacent cracks, as necessary, to be patched and to receive the epoxy injection. Patch concrete with grout. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems as necessary. | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 15 feet either side of damaged area. Shore damaged member(s) a minimum of one level below (more levels may be required). Remove damaged concrete at least 1 inch beyond the exposed reinforcing steel. Place concrete forms. Place concrete. Remove forms. Remove shores after one week. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary). | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 15 feet either side of damaged component. Shore damaged member(s) a minimum of one level below (more levels may be required). Remove damaged component. Place and splice (as necessary) new reinforcing steel to existing, undamaged reinforcing. Place concrete forms. Place concrete. Remove forms. Remove shores after one week. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary). |  |  | NO | NO | NO |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | NO | YES |  |  | 0% | 0% | 20% |  |  | 0 | 0 | 0.5 |  |  | None | Not Given | By User | By User | Laura Lowes | none | none | none |  |  | No | 2011-08-24 Changed DS2 beta from 0.3 to 0.4 to avoid negative probability beyond 1% story drift. | YES
B1041.043a | B1041.043a | ACI 318 OMF with weak joints and column flexural response, Conc Col & Bm = 36" x 36", Beam one side | ACI318 OMF, joint shear failure, beam flexural response. Meets the following requirements: (1) Sum Mcol / Sum Mbeam > 1.2, (2) Beam Vn > Veq, (3) Column Vn > Veq. Costing is on a per joint basis. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 130 | EA 1 | YES | NO | Concrete Cracking: beams, joints or possibly Residual concrete crack widths exceed 0.06 in. (1.5 mm). Column exhibit residual crack widths that require epoxy injection. | Concrete Spalling: slabs, beams, joints or possibly columns exhibit spalling of cover concrete that exposes transverse but not longitudinal reinforcing steel. Spalling of cover concrete possibly exposing transverse reinforcement. | Concrete Crushing: slabs, beams or joints. Spalling of beam, column or joint cover concrete exposes longitudinal reinforcement OR strength loss initiates in laboratory testing. exhibit concrete spalling that exposes longitudinal steel or crushing of core concrete. |  |  | 1 | 1 | 1 |  |  | 0.015 | 0.0175 | 0.02 |  |  | Not Specified | 0.28 | 0.18 |  |  | 0.4 | 0.15 | 0.35 |  |  | 0.4 | 0.4 | 0.4 |  |  | NO | YES | Average | Average | Superior | Superior | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 8 feet either side of damaged area. Clean area adjacent to the damaged concrete. Prepare spalled concrete and adjacent cracks, as necessary, to be patched and to receive the epoxy injection. Patch concrete with grout. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems as necessary. | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 15 feet either side of damaged area. Shore damaged member(s) a minimum of one level below (more levels may be required). Remove damaged concrete at least 1 inch beyond the exposed reinforcing steel. Place concrete forms. Place concrete. Remove forms. Remove shores after one week. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary). | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 15 feet either side of damaged component. Shore damaged member(s) a minimum of one level below (more levels may be required). Remove damaged component. Place and splice (as necessary) new reinforcing steel to existing, undamaged reinforcing. Place concrete forms. Place concrete. Remove forms. Remove shores after one week. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary). |  |  | NO | NO | NO |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | NO | YES |  |  | 0% | 0% | 20% |  |  | 0 | 0 | 0.5 |  |  | None | Not Given | By User | By User | Laura Lowes | none | none | none |  |  | No | 2011-08-24 Changed DS2 beta from 0.3 to 0.4 to avoid negative probability beyond 1% story drift. | YES
B1041.043b | B1041.043b | ACI 318 OMF with weak joints and column flexural response, Conc Col & Bm = 36" x 36", Beam both sides | ACI318 OMF, joint shear failure, beam flexural response. Meets the following requirements: (1) Sum Mcol / Sum Mbeam > 1.2, (2) Beam Vn > Veq, (3) Column Vn > Veq. Costing is on a per joint basis. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 131 | EA 1 | YES | NO | Concrete Cracking: beams, joints or possibly Residual concrete crack widths exceed 0.06 in. (1.5 mm). Column exhibit residual crack widths that require epoxy injection. | Concrete Spalling: slabs, beams, joints or possibly columns exhibit spalling of cover concrete that exposes transverse but not longitudinal reinforcing steel. Spalling of cover concrete possibly exposing transverse reinforcement. | Concrete Crushing: slabs, beams or joints. Spalling of beam, column or joint cover concrete exposes longitudinal reinforcement OR strength loss initiates in laboratory testing. exhibit concrete spalling that exposes longitudinal steel or crushing of core concrete. |  |  | 1 | 1 | 1 |  |  | 0.015 | 0.0175 | 0.02 |  |  | Not Specified | 0.28 | 0.18 |  |  | 0.4 | 0.15 | 0.35 |  |  | 0.4 | 0.4 | 0.4 |  |  | NO | YES | Average | Average | Superior | Superior | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 8 feet either side of damaged area. Clean area adjacent to the damaged concrete. Prepare spalled concrete and adjacent cracks, as necessary, to be patched and to receive the epoxy injection. Patch concrete with grout. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems as necessary. | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 15 feet either side of damaged area. Shore damaged member(s) a minimum of one level below (more levels may be required). Remove damaged concrete at least 1 inch beyond the exposed reinforcing steel. Place concrete forms. Place concrete. Remove forms. Remove shores after one week. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary). | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 15 feet either side of damaged component. Shore damaged member(s) a minimum of one level below (more levels may be required). Remove damaged component. Place and splice (as necessary) new reinforcing steel to existing, undamaged reinforcing. Place concrete forms. Place concrete. Remove forms. Remove shores after one week. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary). |  |  | NO | NO | NO |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | NO | YES |  |  | 0% | 0% | 20% |  |  | 0 | 0 | 0.5 |  |  | None | Not Given | By User | By User | Laura Lowes | none | none | none |  |  | No | 2011-08-24 Changed DS2 beta from 0.3 to 0.4 to avoid negative probability beyond 1% story drift. | YES
B1041.051a | B1041.051a | ACI 318 OMF with weak beams and weak joints, beam flexural or shear response, Conc Col & Bm = 24" x 24", Beam one side | ACI318 OMF, beam flexure-shear or shear failure, beam flexural response. Meets the following requirements: (1) Beam Vn < Veq. Costing is on a per joint basis. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 132 | EA 1 | YES | NO | Beams exhibit residual crack widths > 0.06 in. No significant spalling. No fracture or buckling of reinforcing. | Beams exhibit residual crack widths > 0.06 in. Spalling of cover concrete exposes beam and joint transverse reinforcement but not longitudinal reinforcement. No fracture or buckling of reinforcing. | Beams exhibit residual crack widths > 0.06 in. Spalling of beam cover concrete exposes a significant length of beam longitudinal reinforcement. Crushing of beam core concrete may occur. Fracture or buckling of reinf. requiring replacement may occur. |  |  | 1 | 1 | 1 |  |  | 0.0175 | 0.02 | 0.03 |  |  | Not Specified | 0.27 | 0.32 |  |  | 0.4 | 0.15 | 0.15 |  |  | 0.4 | 0.4 | 0.4 |  |  | NO | YES | Average | Average | Superior | Superior | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 8 feet either side of damaged area. Clean area adjacent to the damaged concrete. Prepare spalled concrete and adjacent cracks, as necessary, to be patched and to receive the epoxy injection. Patch concrete with grout. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems as necessary. | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 15 feet either side of damaged area. Shore damaged member(s) a minimum of one level below (more levels may be required). Remove damaged concrete at least 1 inch beyond the exposed reinforcing steel. Place concrete forms. Place concrete. Remove forms. Remove shores after one week. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary). | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 15 feet either side of damaged component. Shore damaged member(s) a minimum of one level below (more levels may be required). Remove damaged component. Place and splice (as necessary) new reinforcing steel to existing, undamaged reinforcing. Place concrete forms. Place concrete. Remove forms. Remove shores after one week. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary). |  |  | NO | NO | NO |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | NO | YES |  |  | 0% | 0% | 20% |  |  | 0 | 0 | 0.5 |  |  | None | Not Given | By User | By User | Laura Lowes | B1041.051a-DS1-1.JPG | B1041.051a-DS2-1.JPG | B1041.051a-DS3-1.JPG |  |  | No | 2011-08-24 Changed DS2 beta from 0.3 to 0.4 to avoid negative probability beyond 1% story drift. | YES
B1041.051b | B1041.051b | ACI 318 OMF with weak beams and weak joints, beam flexural or shear response, Conc Col & Bm = 24" x 24", Beam both sides | ACI318 OMF, beam flexure-shear or shear failure, beam flexural response. Meets the following requirements: (1) Beam Vn < Veq. Costing is on a per joint basis. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 133 | EA 1 | YES | NO | Beams exhibit residual crack widths > 0.06 in. No significant spalling. No fracture or buckling of reinforcing. | Beams exhibit residual crack widths > 0.06 in. Spalling of cover concrete exposes beam and joint transverse reinforcement but not longitudinal reinforcement. No fracture or buckling of reinforcing. | Beams exhibit residual crack widths > 0.06 in. Spalling of beam cover concrete exposes a significant length of beam longitudinal reinforcement. Crushing of beam core concrete may occur. Fracture or buckling of reinf. requiring replacement may occur. |  |  | 1 | 1 | 1 |  |  | 0.0175 | 0.02 | 0.03 |  |  | Not Specified | 0.27 | 0.32 |  |  | 0.4 | 0.15 | 0.15 |  |  | 0.4 | 0.4 | 0.4 |  |  | NO | YES | Average | Average | Superior | Superior | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 8 feet either side of damaged area. Clean area adjacent to the damaged concrete. Prepare spalled concrete and adjacent cracks, as necessary, to be patched and to receive the epoxy injection. Patch concrete with grout. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems as necessary. | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 15 feet either side of damaged area. Shore damaged member(s) a minimum of one level below (more levels may be required). Remove damaged concrete at least 1 inch beyond the exposed reinforcing steel. Place concrete forms. Place concrete. Remove forms. Remove shores after one week. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary). | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 15 feet either side of damaged component. Shore damaged member(s) a minimum of one level below (more levels may be required). Remove damaged component. Place and splice (as necessary) new reinforcing steel to existing, undamaged reinforcing. Place concrete forms. Place concrete. Remove forms. Remove shores after one week. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary). |  |  | NO | NO | NO |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | NO | YES |  |  | 0% | 0% | 20% |  |  | 0 | 0 | 0.5 |  |  | None | Not Given | By User | By User | Laura Lowes | B1041.051a-DS1-1.JPG | B1041.051a-DS2-1.JPG | B1041.051a-DS3-1.JPG |  |  | No | 2011-08-24 Changed DS2 beta from 0.3 to 0.4 to avoid negative probability beyond 1% story drift. | YES
B1041.052a | B1041.052a | ACI 318 OMF with weak beams and weak joints, beam flexural or shear response, Conc Col & Bm = 24" x 36", Beam one side | ACI318 OMF, beam flexure-shear or shear failure, beam flexural response. Meets the following requirements: (1) Beam Vn < Veq. Costing is on a per joint basis. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 134 | EA 1 | YES | NO | Beams exhibit residual crack widths > 0.06 in. No significant spalling. No fracture or buckling of reinforcing. | Beams exhibit residual crack widths > 0.06 in. Spalling of cover concrete exposes beam and joint transverse reinforcement but not longitudinal reinforcement. No fracture or buckling of reinforcing. | Beams exhibit residual crack widths > 0.06 in. Spalling of beam cover concrete exposes a significant length of beam longitudinal reinforcement. Crushing of beam core concrete may occur. Fracture or buckling of reinf. requiring replacement may occur. |  |  | 1 | 1 | 1 |  |  | 0.0175 | 0.02 | 0.03 |  |  | Not Specified | 0.27 | 0.32 |  |  | 0.4 | 0.15 | 0.15 |  |  | 0.4 | 0.4 | 0.4 |  |  | NO | YES | Average | Average | Superior | Superior | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 8 feet either side of damaged area. Clean area adjacent to the damaged concrete. Prepare spalled concrete and adjacent cracks, as necessary, to be patched and to receive the epoxy injection. Patch concrete with grout. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems as necessary. | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 15 feet either side of damaged area. Shore damaged member(s) a minimum of one level below (more levels may be required). Remove damaged concrete at least 1 inch beyond the exposed reinforcing steel. Place concrete forms. Place concrete. Remove forms. Remove shores after one week. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary). | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 15 feet either side of damaged component. Shore damaged member(s) a minimum of one level below (more levels may be required). Remove damaged component. Place and splice (as necessary) new reinforcing steel to existing, undamaged reinforcing. Place concrete forms. Place concrete. Remove forms. Remove shores after one week. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary). |  |  | NO | NO | NO |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | NO | YES |  |  | 0% | 0% | 20% |  |  | 0 | 0 | 0.5 |  |  | None | Not Given | By User | By User | Laura Lowes | B1041.051a-DS1-1.JPG | B1041.051a-DS2-1.JPG | B1041.051a-DS3-1.JPG |  |  | No | 2011-08-24 Changed DS2 beta from 0.3 to 0.4 to avoid negative probability beyond 1% story drift. | YES
B1041.052b | B1041.052b | ACI 318 OMF with weak beams and weak joints, beam flexural or shear response, Conc Col & Bm = 24" x 36", Beam both sides | ACI318 OMF, beam flexure-shear or shear failure, beam flexural response. Meets the following requirements: (1) Beam Vn < Veq. Costing is on a per joint basis. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 135 | EA 1 | YES | NO | Beams exhibit residual crack widths > 0.06 in. No significant spalling. No fracture or buckling of reinforcing. | Beams exhibit residual crack widths > 0.06 in. Spalling of cover concrete exposes beam and joint transverse reinforcement but not longitudinal reinforcement. No fracture or buckling of reinforcing. | Beams exhibit residual crack widths > 0.06 in. Spalling of beam cover concrete exposes a significant length of beam longitudinal reinforcement. Crushing of beam core concrete may occur. Fracture or buckling of reinf. requiring replacement may occur. |  |  | 1 | 1 | 1 |  |  | 0.0175 | 0.02 | 0.03 |  |  | Not Specified | 0.27 | 0.32 |  |  | 0.4 | 0.15 | 0.15 |  |  | 0.4 | 0.4 | 0.4 |  |  | NO | YES | Average | Average | Superior | Superior | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 8 feet either side of damaged area. Clean area adjacent to the damaged concrete. Prepare spalled concrete and adjacent cracks, as necessary, to be patched and to receive the epoxy injection. Patch concrete with grout. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems as necessary. | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 15 feet either side of damaged area. Shore damaged member(s) a minimum of one level below (more levels may be required). Remove damaged concrete at least 1 inch beyond the exposed reinforcing steel. Place concrete forms. Place concrete. Remove forms. Remove shores after one week. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary). | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 15 feet either side of damaged component. Shore damaged member(s) a minimum of one level below (more levels may be required). Remove damaged component. Place and splice (as necessary) new reinforcing steel to existing, undamaged reinforcing. Place concrete forms. Place concrete. Remove forms. Remove shores after one week. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary). |  |  | NO | NO | NO |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | NO | YES |  |  | 0% | 0% | 20% |  |  | 0 | 0 | 0.5 |  |  | None | Not Given | By User | By User | Laura Lowes | B1041.051a-DS1-1.JPG | B1041.051a-DS2-1.JPG | B1041.051a-DS3-1.JPG |  |  | No | 2011-08-24 Changed DS2 beta from 0.3 to 0.4 to avoid negative probability beyond 1% story drift. | YES
B1041.053a | B1041.053a | ACI 318 OMF with weak beams and weak joints, beam flexural or shear response, Conc Col & Bm = 36" x 36", Beam one side | ACI318 OMF, beam flexure-shear or shear failure, beam flexural response. Meets the following requirements: (1) Beam Vn < Veq. Costing is on a per joint basis. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 136 | EA 1 | YES | NO | Beams exhibit residual crack widths > 0.06 in. No significant spalling. No fracture or buckling of reinforcing. | Beams exhibit residual crack widths > 0.06 in. Spalling of cover concrete exposes beam and joint transverse reinforcement but not longitudinal reinforcement. No fracture or buckling of reinforcing. | Beams exhibit residual crack widths > 0.06 in. Spalling of beam cover concrete exposes a significant length of beam longitudinal reinforcement. Crushing of beam core concrete may occur. Fracture or buckling of reinf. requiring replacement may occur. |  |  | 1 | 1 | 1 |  |  | 0.0175 | 0.02 | 0.03 |  |  | Not Specified | 0.27 | 0.32 |  |  | 0.4 | 0.15 | 0.15 |  |  | 0.4 | 0.4 | 0.4 |  |  | NO | YES | Average | Average | Superior | Superior | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 8 feet either side of damaged area. Clean area adjacent to the damaged concrete. Prepare spalled concrete and adjacent cracks, as necessary, to be patched and to receive the epoxy injection. Patch concrete with grout. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems as necessary. | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 15 feet either side of damaged area. Shore damaged member(s) a minimum of one level below (more levels may be required). Remove damaged concrete at least 1 inch beyond the exposed reinforcing steel. Place concrete forms. Place concrete. Remove forms. Remove shores after one week. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary). | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 15 feet either side of damaged component. Shore damaged member(s) a minimum of one level below (more levels may be required). Remove damaged component. Place and splice (as necessary) new reinforcing steel to existing, undamaged reinforcing. Place concrete forms. Place concrete. Remove forms. Remove shores after one week. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary). |  |  | NO | NO | NO |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | NO | YES |  |  | 0% | 0% | 20% |  |  | 0 | 0 | 0.5 |  |  | None | Not Given | By User | By User | Laura Lowes | B1041.051a-DS1-1.JPG | B1041.051a-DS2-1.JPG | B1041.051a-DS3-1.JPG |  |  | No | 2011-08-24 Changed DS2 beta from 0.3 to 0.4 to avoid negative probability beyond 1% story drift. | YES
B1041.053b | B1041.053b | ACI 318 OMF with weak beams and weak joints, beam flexural or shear response, Conc Col & Bm = 36" x 36", Beam both sides | ACI318 OMF, beam flexure-shear or shear failure, beam flexural response. Meets the following requirements: (1) Beam Vn < Veq. Costing is on a per joint basis. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 137 | EA 1 | YES | NO | Beams exhibit residual crack widths > 0.06 in. No significant spalling. No fracture or buckling of reinforcing. | Beams exhibit residual crack widths > 0.06 in. Spalling of cover concrete exposes beam and joint transverse reinforcement but not longitudinal reinforcement. No fracture or buckling of reinforcing. | Beams exhibit residual crack widths > 0.06 in. Spalling of beam cover concrete exposes a significant length of beam longitudinal reinforcement. Crushing of beam core concrete may occur. Fracture or buckling of reinf. requiring replacement may occur. |  |  | 1 | 1 | 1 |  |  | 0.0175 | 0.02 | 0.03 |  |  | Not Specified | 0.27 | 0.32 |  |  | 0.4 | 0.15 | 0.15 |  |  | 0.4 | 0.4 | 0.4 |  |  | NO | YES | Average | Average | Superior | Superior | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 8 feet either side of damaged area. Clean area adjacent to the damaged concrete. Prepare spalled concrete and adjacent cracks, as necessary, to be patched and to receive the epoxy injection. Patch concrete with grout. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems as necessary. | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 15 feet either side of damaged area. Shore damaged member(s) a minimum of one level below (more levels may be required). Remove damaged concrete at least 1 inch beyond the exposed reinforcing steel. Place concrete forms. Place concrete. Remove forms. Remove shores after one week. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary). | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 15 feet either side of damaged component. Shore damaged member(s) a minimum of one level below (more levels may be required). Remove damaged component. Place and splice (as necessary) new reinforcing steel to existing, undamaged reinforcing. Place concrete forms. Place concrete. Remove forms. Remove shores after one week. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary). |  |  | NO | NO | NO |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | NO | YES |  |  | 0% | 0% | 20% |  |  | 0 | 0 | 0.5 |  |  | None | Not Given | By User | By User | Laura Lowes | B1041.051a-DS1-1.JPG | B1041.051a-DS2-1.JPG | B1041.051a-DS3-1.JPG |  |  | No | 2011-08-24 Changed DS2 beta from 0.3 to 0.4 to avoid negative probability beyond 1% story drift. | YES
B1041.061a | B1041.061a | ACI 318 OMF with weak columns, Conc Col & Bm = 24" x 24", Beam one side | ACI318 OMF, column shear or flexural-shear failure, column flexural response. Meets the following requirements: (1) Column Pu < 0.6Agf'c, (2) Column Vn < Veq Costing is on a per joint basis. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 138 | EA 1 | YES | NO | Columns exhibit residual crack widths > 0.06 in. No significant spalling. No fracture or buckling of reinf. | Columns exhibit residual crack widths > 0.06 in. Spalling of cover concrete exposes column transverse reinforcement but not longitudinal reinforcement. No fracture or buckling of reinforcing. | Columns exhibit residual crack widths > 0.06 in. Spalling of column cover concrete exposes a significant length of column longitudinal reinforcement. Crushing of column core concrete may occur. Fracture or buckling of reinf. requiring replacement may occur. |  |  | 1 | 1 | 1 |  |  | 0.015 | 0.0175 | 0.02 |  |  | Not Specified | 0.27 | 0.18 |  |  | 0.4 | 0.15 | 0.35 |  |  | 0.4 | 0.4 | 0.4 |  |  | NO | YES | Average | Average | Superior | Superior | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 8 feet either side of damaged area. Clean area adjacent to the damaged concrete. Prepare spalled concrete and adjacent cracks, as necessary, to be patched and to receive the epoxy injection. Patch concrete with grout. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems as necessary. | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 15 feet either side of damaged area. Shore damaged member(s) a minimum of one level below (more levels may be required). Remove damaged concrete at least 1 inch beyond the exposed reinforcing steel. Place concrete forms. Place concrete. Remove forms. Remove shores after one week. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary). | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 15 feet either side of damaged component. Shore damaged member(s) a minimum of one level below (more levels may be required). Remove damaged component. Place and splice (as necessary) new reinforcing steel to existing, undamaged reinforcing. Place concrete forms. Place concrete. Remove forms. Remove shores after one week. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary). |  |  | NO | NO | NO |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | NO | YES |  |  | 0% | 0% | 10% |  |  | 0 | 0 | 0.5 |  |  | None | Not Given | By User | By User | Laura Lowes | B1041.051a-DS1-1.JPG | B1041.051a-DS2-1.JPG | B1041.051a-DS3-1.JPG |  |  | No | 2011-08-24 Changed DS2 beta from 0.3 to 0.4 to avoid negative probability beyond 1% story drift. | YES
B1041.061b | B1041.061b | ACI 318 OMF with weak columns, Conc Col & Bm = 24" x 24", Beam both sides | ACI318 OMF, column shear or flexural-shear failure, column flexural response. Meets the following requirements: (1) Column Pu < 0.6Agf'c, (2) Column Vn < Veq Costing is on a per joint basis. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 139 | EA 1 | YES | NO | Columns exhibit residual crack widths > 0.06 in. No significant spalling. No fracture or buckling of reinf. | Columns exhibit residual crack widths > 0.06 in. Spalling of cover concrete exposes column transverse reinforcement but not longitudinal reinforcement. No fracture or buckling of reinforcing. | Columns exhibit residual crack widths > 0.06 in. Spalling of column cover concrete exposes a significant length of column longitudinal reinforcement. Crushing of column core concrete may occur. Fracture or buckling of reinf. requiring replacement may occur. |  |  | 1 | 1 | 1 |  |  | 0.015 | 0.0175 | 0.02 |  |  | Not Specified | 0.27 | 0.18 |  |  | 0.4 | 0.15 | 0.35 |  |  | 0.4 | 0.4 | 0.4 |  |  | NO | YES | Average | Average | Superior | Superior | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 8 feet either side of damaged area. Clean area adjacent to the damaged concrete. Prepare spalled concrete and adjacent cracks, as necessary, to be patched and to receive the epoxy injection. Patch concrete with grout. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems as necessary. | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 15 feet either side of damaged area. Shore damaged member(s) a minimum of one level below (more levels may be required). Remove damaged concrete at least 1 inch beyond the exposed reinforcing steel. Place concrete forms. Place concrete. Remove forms. Remove shores after one week. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary). | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 15 feet either side of damaged component. Shore damaged member(s) a minimum of one level below (more levels may be required). Remove damaged component. Place and splice (as necessary) new reinforcing steel to existing, undamaged reinforcing. Place concrete forms. Place concrete. Remove forms. Remove shores after one week. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary). |  |  | NO | NO | NO |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | NO | YES |  |  | 0% | 0% | 10% |  |  | 0 | 0 | 0.5 |  |  | None | Not Given | By User | By User | Laura Lowes | B1041.051a-DS1-1.JPG | B1041.051a-DS2-1.JPG | B1041.051a-DS3-1.JPG |  |  | No | 2011-08-24 Changed DS2 beta from 0.3 to 0.4 to avoid negative probability beyond 1% story drift. | YES
B1041.062a | B1041.062a | ACI 318 OMF with weak columns, Conc Col & Bm = 24" x 36", Beam one side | ACI318 OMF, column shear or flexural-shear failure, column flexural response. Meets the following requirements: (1) Column Pu < 0.6Agf'c, (2) Column Vn < Veq Costing is on a per joint basis. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 140 | EA 1 | YES | NO | Columns exhibit residual crack widths > 0.06 in. No significant spalling. No fracture or buckling of reinf. | Columns exhibit residual crack widths > 0.06 in. Spalling of cover concrete exposes column transverse reinforcement but not longitudinal reinforcement. No fracture or buckling of reinforcing. | Columns exhibit residual crack widths > 0.06 in. Spalling of column cover concrete exposes a significant length of column longitudinal reinforcement. Crushing of column core concrete may occur. Fracture or buckling of reinf. requiring replacement may occur. |  |  | 1 | 1 | 1 |  |  | 0.015 | 0.0175 | 0.02 |  |  | Not Specified | 0.27 | 0.18 |  |  | 0.4 | 0.15 | 0.35 |  |  | 0.4 | 0.4 | 0.4 |  |  | NO | YES | Average | Average | Superior | Superior | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 8 feet either side of damaged area. Clean area adjacent to the damaged concrete. Prepare spalled concrete and adjacent cracks, as necessary, to be patched and to receive the epoxy injection. Patch concrete with grout. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems as necessary. | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 15 feet either side of damaged area. Shore damaged member(s) a minimum of one level below (more levels may be required). Remove damaged concrete at least 1 inch beyond the exposed reinforcing steel. Place concrete forms. Place concrete. Remove forms. Remove shores after one week. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary). | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 15 feet either side of damaged component. Shore damaged member(s) a minimum of one level below (more levels may be required). Remove damaged component. Place and splice (as necessary) new reinforcing steel to existing, undamaged reinforcing. Place concrete forms. Place concrete. Remove forms. Remove shores after one week. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary). |  |  | NO | NO | NO |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | NO | YES |  |  | 0% | 0% | 10% |  |  | 0 | 0 | 0.5 |  |  | None | Not Given | By User | By User | Laura Lowes | B1041.051a-DS1-1.JPG | B1041.051a-DS2-1.JPG | B1041.051a-DS3-1.JPG |  |  | No | 2011-08-24 Changed DS2 beta from 0.3 to 0.4 to avoid negative probability beyond 1% story drift. | YES
B1041.062b | B1041.062b | ACI 318 OMF with weak columns, Conc Col & Bm = 24" x 36", Beam both sides | ACI318 OMF, column shear or flexural-shear failure, column flexural response. Meets the following requirements: (1) Column Pu < 0.6Agf'c, (2) Column Vn < Veq Costing is on a per joint basis. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 141 | EA 1 | YES | NO | Columns exhibit residual crack widths > 0.06 in. No significant spalling. No fracture or buckling of reinf. | Columns exhibit residual crack widths > 0.06 in. Spalling of cover concrete exposes column transverse reinforcement but not longitudinal reinforcement. No fracture or buckling of reinforcing. | Columns exhibit residual crack widths > 0.06 in. Spalling of column cover concrete exposes a significant length of column longitudinal reinforcement. Crushing of column core concrete may occur. Fracture or buckling of reinf. requiring replacement may occur. |  |  | 1 | 1 | 1 |  |  | 0.015 | 0.0175 | 0.02 |  |  | Not Specified | 0.27 | 0.18 |  |  | 0.4 | 0.15 | 0.35 |  |  | 0.4 | 0.4 | 0.4 |  |  | NO | YES | Average | Average | Superior | Superior | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 8 feet either side of damaged area. Clean area adjacent to the damaged concrete. Prepare spalled concrete and adjacent cracks, as necessary, to be patched and to receive the epoxy injection. Patch concrete with grout. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems as necessary. | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 15 feet either side of damaged area. Shore damaged member(s) a minimum of one level below (more levels may be required). Remove damaged concrete at least 1 inch beyond the exposed reinforcing steel. Place concrete forms. Place concrete. Remove forms. Remove shores after one week. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary). | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 15 feet either side of damaged component. Shore damaged member(s) a minimum of one level below (more levels may be required). Remove damaged component. Place and splice (as necessary) new reinforcing steel to existing, undamaged reinforcing. Place concrete forms. Place concrete. Remove forms. Remove shores after one week. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary). |  |  | NO | NO | NO |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | NO | YES |  |  | 0% | 0% | 10% |  |  | 0 | 0 | 0.5 |  |  | None | Not Given | By User | By User | Laura Lowes | B1041.051a-DS1-1.JPG | B1041.051a-DS2-1.JPG | B1041.051a-DS3-1.JPG |  |  | No | 2011-08-24 Changed DS2 beta from 0.3 to 0.4 to avoid negative probability beyond 1% story drift. | YES
B1041.063a | B1041.063a | ACI 318 OMF with weak columns, Conc Col & Bm = 36" x 36", Beam one side | ACI318 OMF, column shear or flexural-shear failure, column flexural response. Meets the following requirements: (1) Column Pu < 0.6Agf'c, (2) Column Vn < Veq Costing is on a per joint basis. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 142 | EA 1 | YES | NO | Columns exhibit residual crack widths > 0.06 in. No significant spalling. No fracture or buckling of reinf. | Columns exhibit residual crack widths > 0.06 in. Spalling of cover concrete exposes column transverse reinforcement but not longitudinal reinforcement. No fracture or buckling of reinforcing. | Columns exhibit residual crack widths > 0.06 in. Spalling of column cover concrete exposes a significant length of column longitudinal reinforcement. Crushing of column core concrete may occur. Fracture or buckling of reinf. requiring replacement may occur. |  |  | 1 | 1 | 1 |  |  | 0.015 | 0.0175 | 0.02 |  |  | Not Specified | 0.27 | 0.18 |  |  | 0.4 | 0.15 | 0.35 |  |  | 0.4 | 0.4 | 0.4 |  |  | NO | YES | Average | Average | Superior | Superior | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 8 feet either side of damaged area. Clean area adjacent to the damaged concrete. Prepare spalled concrete and adjacent cracks, as necessary, to be patched and to receive the epoxy injection. Patch concrete with grout. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems as necessary. | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 15 feet either side of damaged area. Shore damaged member(s) a minimum of one level below (more levels may be required). Remove damaged concrete at least 1 inch beyond the exposed reinforcing steel. Place concrete forms. Place concrete. Remove forms. Remove shores after one week. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary). | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 15 feet either side of damaged component. Shore damaged member(s) a minimum of one level below (more levels may be required). Remove damaged component. Place and splice (as necessary) new reinforcing steel to existing, undamaged reinforcing. Place concrete forms. Place concrete. Remove forms. Remove shores after one week. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary). |  |  | NO | NO | NO |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | NO | YES |  |  | 0% | 0% | 10% |  |  | 0 | 0 | 0.5 |  |  | None | Not Given | By User | By User | Laura Lowes | B1041.051a-DS1-1.JPG | B1041.051a-DS2-1.JPG | B1041.051a-DS3-1.JPG |  |  | No | 2011-08-24 Changed DS2 beta from 0.3 to 0.4 to avoid negative probability beyond 1% story drift. | YES
B1041.063b | B1041.063b | ACI 318 OMF with weak columns, Conc Col & Bm = 36" x 36", Beam both sides | ACI318 OMF, column shear or flexural-shear failure, column flexural response. Meets the following requirements: (1) Column Pu < 0.6Agf'c, (2) Column Vn < Veq Costing is on a per joint basis. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 143 | EA 1 | YES | NO | Columns exhibit residual crack widths > 0.06 in. No significant spalling. No fracture or buckling of reinf. | Columns exhibit residual crack widths > 0.06 in. Spalling of cover concrete exposes column transverse reinforcement but not longitudinal reinforcement. No fracture or buckling of reinforcing. | Columns exhibit residual crack widths > 0.06 in. Spalling of column cover concrete exposes a significant length of column longitudinal reinforcement. Crushing of column core concrete may occur. Fracture or buckling of reinf. requiring replacement may occur. |  |  | 1 | 1 | 1 |  |  | 0.015 | 0.0175 | 0.02 |  |  | Not Specified | 0.27 | 0.18 |  |  | 0.4 | 0.15 | 0.35 |  |  | 0.4 | 0.4 | 0.4 |  |  | NO | YES | Average | Average | Superior | Superior | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 8 feet either side of damaged area. Clean area adjacent to the damaged concrete. Prepare spalled concrete and adjacent cracks, as necessary, to be patched and to receive the epoxy injection. Patch concrete with grout. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems as necessary. | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 15 feet either side of damaged area. Shore damaged member(s) a minimum of one level below (more levels may be required). Remove damaged concrete at least 1 inch beyond the exposed reinforcing steel. Place concrete forms. Place concrete. Remove forms. Remove shores after one week. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary). | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 15 feet either side of damaged component. Shore damaged member(s) a minimum of one level below (more levels may be required). Remove damaged component. Place and splice (as necessary) new reinforcing steel to existing, undamaged reinforcing. Place concrete forms. Place concrete. Remove forms. Remove shores after one week. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary). |  |  | NO | NO | NO |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | NO | YES |  |  | 0% | 0% | 10% |  |  | 0 | 0 | 0.5 |  |  | None | Not Given | By User | By User | Laura Lowes | B1041.051a-DS1-1.JPG | B1041.051a-DS2-1.JPG | B1041.051a-DS3-1.JPG |  |  | No | 2011-08-24 Changed DS2 beta from 0.3 to 0.4 to avoid negative probability beyond 1% story drift. | YES
B1041.071a | B1041.071a | ACI 318 OMF weak columns w/ high axial load, Conc Col & Bm = 24" x 24", Beam one side | ACI318 OMF, column flexure, flexural-shear, or shear failure at high axial load. Column flexural-shear response. Meets the following requirements: (1) Column Pu > 0.6Agf'c, (2) Column Vn < Veq Costing is on a per joint basis. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 144 | EA 1 | YES | NO | Concrete Cracking: beams, joints or possibly. Residual concrete crack widths exceed 0.06in. (1.5 mm). Column exhibits residual crack widths that require epoxy injection. | Concrete Crushing: slabs, beams or joints. Spalling of beam, column or joint cover concrete exposes longitudinal reinforcement or strength loss initiates in laboratory testing. Exhibits concrete spalling that exposes longitudinal steel or crushing of core concrete. |  |  |  | 1 | 1 |  |  |  | 0.0025 | 0.005 |  |  |  | Not Specified | Not Specified |  |  |  | 0.4 | 0.5 |  |  |  | 0.4 | 0.5 |  |  |  | NO | YES | Marginal | Average | Superior | Superior | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 8 feet either side of damaged area. Clean area adjacent to the damaged concrete. Prepare spalled concrete and adjacent cracks, as necessary, to be patched and to receive the epoxy injection. Patch concrete with grout. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems as necessary. | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 15 feet either side of damaged component. Shore damaged member(s) a minimum of one level below (more levels may be required). Remove damaged component. Place and splice (as necessary) new reinforcing steel to existing, undamaged reinforcing. Place concrete forms. Place concrete. Remove forms. Remove shores after one week. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary). |  |  |  | NO | NO |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | YES |  |  |  | 0% | 10% |  |  |  | 0 | 0.5 |  |  |  | This fragility has been changed to match B1041.121. ASCE6 is closest to column high axial OMF. | Not Given | By User | By User | Laura Lowes | B1041.071a-DS1-2.JPG | B1041.071a-DS2-1.JPG |  |  |  | No | 2011-08-24 Negative probability below 0.1% drift - overlap deemed acceptable. | YES
B1041.071b | B1041.071b | ACI 318 OMF weak columns w/ high axial load, Conc Col & Bm = 24" x 24", Beam both sides | ACI318 OMF, column flexure, flexural-shear, or shear failure at high axial load. Column flexural-shear response. Meets the following requirements: (1) Column Pu > 0.6Agf'c, (2) Column Vn < Veq Costing is on a per joint basis. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 145 | EA 1 | YES | NO | Concrete Cracking: beams, joints or possibly. Residual concrete crack widths exceed 0.06in. (1.5 mm). Column exhibits residual crack widths that require epoxy injection. | Concrete Crushing: slabs, beams or joints. Spalling of beam, column or joint cover concrete exposes longitudinal reinforcement or strength loss initiates in laboratory testing. Exhibits concrete spalling that exposes longitudinal steel or crushing of core concrete. |  |  |  | 1 | 1 |  |  |  | 0.0025 | 0.005 |  |  |  | Not Specified | Not Specified |  |  |  | 0.4 | 0.5 |  |  |  | 0.4 | 0.5 |  |  |  | NO | YES | Marginal | Average | Superior | Superior | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 8 feet either side of damaged area. Clean area adjacent to the damaged concrete. Prepare spalled concrete and adjacent cracks, as necessary, to be patched and to receive the epoxy injection. Patch concrete with grout. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems as necessary. | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 15 feet either side of damaged component. Shore damaged member(s) a minimum of one level below (more levels may be required). Remove damaged component. Place and splice (as necessary) new reinforcing steel to existing, undamaged reinforcing. Place concrete forms. Place concrete. Remove forms. Remove shores after one week. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary). |  |  |  | NO | NO |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | YES |  |  |  | 0% | 10% |  |  |  | 0 | 0.5 |  |  |  | This fragility has been changed to match B1041.121. ASCE6 is closest to column high axial OMF. | Not Given | By User | By User | Laura Lowes | B1041.071a-DS1-2.JPG | B1041.071a-DS2-1.JPG |  |  |  | No | 2011-08-24 Negative probability below 0.1% drift - overlap deemed acceptable. | YES
B1041.072a | B1041.072a | ACI 318 OMF weak columns w/ high axial load, Conc Col & Bm = 24" x 36", Beam one side | ACI318 OMF, column flexure, flexural-shear, or shear failure at high axial load. Column flexural-shear response. Meets the following requirements: (1) Column Pu > 0.6Agf'c, (2) Column Vn < Veq Costing is on a per joint basis. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 146 | EA 1 | YES | NO | Concrete Cracking: beams, joints or possibly. Residual concrete crack widths exceed 0.06in. (1.5 mm). Column exhibits residual crack widths that require epoxy injection. | Concrete Crushing: slabs, beams or joints. Spalling of beam, column or joint cover concrete exposes longitudinal reinforcement or strength loss initiates in laboratory testing. Exhibits concrete spalling that exposes longitudinal steel or crushing of core concrete. |  |  |  | 1 | 1 |  |  |  | 0.0025 | 0.005 |  |  |  | Not Specified | Not Specified |  |  |  | 0.4 | 0.5 |  |  |  | 0.4 | 0.5 |  |  |  | NO | YES | Marginal | Average | Superior | Superior | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 8 feet either side of damaged area. Clean area adjacent to the damaged concrete. Prepare spalled concrete and adjacent cracks, as necessary, to be patched and to receive the epoxy injection. Patch concrete with grout. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems as necessary. | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 15 feet either side of damaged component. Shore damaged member(s) a minimum of one level below (more levels may be required). Remove damaged component. Place and splice (as necessary) new reinforcing steel to existing, undamaged reinforcing. Place concrete forms. Place concrete. Remove forms. Remove shores after one week. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary). |  |  |  | NO | NO |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | YES |  |  |  | 0% | 10% |  |  |  | 0 | 0.5 |  |  |  | This fragility has been changed to match B1041.121. ASCE6 is closest to column high axial OMF. | Not Given | By User | By User | Laura Lowes | B1041.071a-DS1-2.JPG | B1041.071a-DS2-1.JPG |  |  |  | No | 2011-08-24 Negative probability below 0.1% drift - overlap deemed acceptable. | YES
B1041.072b | B1041.072b | ACI 318 OMF weak columns w/ high axial load, Conc Col & Bm = 24" x 36", Beam both sides | ACI318 OMF, column flexure, flexural-shear, or shear failure at high axial load. Column flexural-shear response. Meets the following requirements: (1) Column Pu > 0.6Agf'c, (2) Column Vn < Veq Costing is on a per joint basis. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 147 | EA 1 | YES | NO | Concrete Cracking: beams, joints or possibly. Residual concrete crack widths exceed 0.06in. (1.5 mm). Column exhibits residual crack widths that require epoxy injection. | Concrete Crushing: slabs, beams or joints. Spalling of beam, column or joint cover concrete exposes longitudinal reinforcement or strength loss initiates in laboratory testing. Exhibits concrete spalling that exposes longitudinal steel or crushing of core concrete. |  |  |  | 1 | 1 |  |  |  | 0.0025 | 0.005 |  |  |  | Not Specified | Not Specified |  |  |  | 0.4 | 0.5 |  |  |  | 0.4 | 0.5 |  |  |  | NO | YES | Marginal | Average | Superior | Superior | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 8 feet either side of damaged area. Clean area adjacent to the damaged concrete. Prepare spalled concrete and adjacent cracks, as necessary, to be patched and to receive the epoxy injection. Patch concrete with grout. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems as necessary. | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 15 feet either side of damaged component. Shore damaged member(s) a minimum of one level below (more levels may be required). Remove damaged component. Place and splice (as necessary) new reinforcing steel to existing, undamaged reinforcing. Place concrete forms. Place concrete. Remove forms. Remove shores after one week. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary). |  |  |  | NO | NO |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | YES |  |  |  | 0% | 10% |  |  |  | 0 | 0.5 |  |  |  | This fragility has been changed to match B1041.121. ASCE6 is closest to column high axial OMF. | Not Given | By User | By User | Laura Lowes | B1041.071a-DS1-2.JPG | B1041.071a-DS2-1.JPG |  |  |  | No | 2011-08-24 Negative probability below 0.1% drift - overlap deemed acceptable. | YES
B1041.073a | B1041.073a | ACI 318 OMF weak columns w/ high axial load, Conc Col & Bm = 36" x 36", Beam one side | ACI318 OMF, column flexure, flexural-shear, or shear failure at high axial load. Column flexural-shear response. Meets the following requirements: (1) Column Pu > 0.6Agf'c, (2) Column Vn < Veq Costing is on a per joint basis. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 148 | EA 1 | YES | NO | Concrete Cracking: beams, joints or possibly. Residual concrete crack widths exceed 0.06in. (1.5 mm). Column exhibits residual crack widths that require epoxy injection. | Concrete Crushing: slabs, beams or joints. Spalling of beam, column or joint cover concrete exposes longitudinal reinforcement or strength loss initiates in laboratory testing. Exhibits concrete spalling that exposes longitudinal steel or crushing of core concrete. |  |  |  | 1 | 1 |  |  |  | 0.0025 | 0.005 |  |  |  | Not Specified | Not Specified |  |  |  | 0.4 | 0.5 |  |  |  | 0.4 | 0.5 |  |  |  | NO | YES | Marginal | Average | Superior | Superior | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 8 feet either side of damaged area. Clean area adjacent to the damaged concrete. Prepare spalled concrete and adjacent cracks, as necessary, to be patched and to receive the epoxy injection. Patch concrete with grout. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems as necessary. | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 15 feet either side of damaged component. Shore damaged member(s) a minimum of one level below (more levels may be required). Remove damaged component. Place and splice (as necessary) new reinforcing steel to existing, undamaged reinforcing. Place concrete forms. Place concrete. Remove forms. Remove shores after one week. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary). |  |  |  | NO | NO |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | YES |  |  |  | 0% | 10% |  |  |  | 0 | 0.5 |  |  |  | This fragility has been changed to match B1041.121. ASCE6 is closest to column high axial OMF. | Not Given | By User | By User | Laura Lowes | B1041.071a-DS1-2.JPG | B1041.071a-DS2-1.JPG |  |  |  | No | 2011-08-24 Negative probability below 0.1% drift - overlap deemed acceptable. | YES
B1041.073b | B1041.073b | ACI 318 OMF weak columns w/ high axial load, Conc Col & Bm = 36" x 36", Beam both sides | ACI318 OMF, column flexure, flexural-shear, or shear failure at high axial load. Column flexural-shear response. Meets the following requirements: (1) Column Pu > 0.6Agf'c, (2) Column Vn < Veq Costing is on a per joint basis. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 149 | EA 1 | YES | NO | Concrete Cracking: beams, joints or possibly. Residual concrete crack widths exceed 0.06in. (1.5 mm). Column exhibits residual crack widths that require epoxy injection. | Concrete Crushing: slabs, beams or joints. Spalling of beam, column or joint cover concrete exposes longitudinal reinforcement or strength loss initiates in laboratory testing. Exhibits concrete spalling that exposes longitudinal steel or crushing of core concrete. |  |  |  | 1 | 1 |  |  |  | 0.0025 | 0.005 |  |  |  | Not Specified | Not Specified |  |  |  | 0.4 | 0.5 |  |  |  | 0.4 | 0.5 |  |  |  | NO | YES | Marginal | Average | Superior | Superior | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 8 feet either side of damaged area. Clean area adjacent to the damaged concrete. Prepare spalled concrete and adjacent cracks, as necessary, to be patched and to receive the epoxy injection. Patch concrete with grout. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems as necessary. | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 15 feet either side of damaged component. Shore damaged member(s) a minimum of one level below (more levels may be required). Remove damaged component. Place and splice (as necessary) new reinforcing steel to existing, undamaged reinforcing. Place concrete forms. Place concrete. Remove forms. Remove shores after one week. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary). |  |  |  | NO | NO |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | YES |  |  |  | 0% | 10% |  |  |  | 0 | 0.5 |  |  |  | This fragility has been changed to match B1041.121. ASCE6 is closest to column high axial OMF. | Not Given | By User | By User | Laura Lowes | B1041.071a-DS1-2.JPG | B1041.071a-DS2-1.JPG |  |  |  | No | 2011-08-24 Negative probability below 0.1% drift - overlap deemed acceptable. | YES
B1041.081a | B1041.081a | Non-conforming MF with weak joints and beam flexural response, Conc Col & Bm = 24" x 24", Beam one side | Non-Conforming MF, joint shear failure, beam flexural response. Meets the following requirements: (1) Sum Mcol / Sum Mbeam > 1.2, (2) ASCE41 non-compliant joint transverse reinforcing and or joint V/Vn > 1.2, (3) IGH beam ductility per ASCE41-06 Table 6-7i, (4) Compliant beam transverse reinforcing with LOW beam V / bwd(f'c)^0.5. Costing is on a per joint basis. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 150 | EA 1 | YES | NO | Beams or joints exhibit residual crack widths > 0.06 in. No significant spalling. No fracture or buckling of reinforcing. | Beams or joints exhibit residual crack widths > 0.06 in. Spalling of cover concrete exposes beam and joint transverse reinforcement but not longitudinal reinforcement. No fracture or buckling of reinforcing. | Beams or joints exhibit residual crack widths > 0.06 in. Spalling of cover concrete exposes a significant length of beam longitudinal reinforcement or column longitudinal reinforcement in the joint. Crushing of beam or joint core concrete may occur. Fracture or buckling of reinforcing requiring replacement may occur. |  |  | 1 | 1 | 1 |  |  | 0.0175 | 0.0225 | 0.0322 |  |  | 0.17 | 0.27 | 0.32 |  |  | 0.3 | 0.13 | 0.15 |  |  | 0.4 | 0.4 | 0.4 |  |  | NO | YES | Marginal | Average | Superior | Superior | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 8 feet either side of damaged area. Clean area adjacent to the damaged concrete. Prepare spalled concrete and adjacent cracks, as necessary, to be patched and to receive the epoxy injection. Patch concrete with grout. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems as necessary. | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 15 feet either side of damaged component. Shore damaged member(s) a minimum of one level below (more levels may be required). Remove damaged component. Place and splice (as necessary) new reinforcing steel to existing, undamaged reinforcing. Place concrete forms. Place concrete. Remove forms. Remove shores after one week. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary). | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 15 feet either side of damaged component. Shore damaged member(s) a minimum of one level below (more levels may be required). Remove damaged component. Place and splice (as necessary) new reinforcing steel to existing, undamaged reinforcing. Place concrete forms. Place concrete. Remove forms. Remove shores after one week. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary). |  |  | NO | NO | NO |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | NO | YES |  |  | 0% | 0% | 20% |  |  | 0 | 0 | 0.5 |  |  | None | Not Given | By User | By User | Laura Lowes | B1041.001a-DS1-1.JPG | B1041.031a-DS2-1.JPG | B1041.031a-DS3-1.JPG |  |  | No | 2011-08-24 DS3 beta changed from 0.3 to 0.4 in order to avoid negative probability. | YES
B1041.081b | B1041.081b | Non-conforming MF with weak joints and beam flexural response, Conc Col & Bm = 24" x 24", Beam both sides | Non-Conforming MF, joint shear failure, beam flexural response. Meets the following requirements: (1) Sum Mcol / Sum Mbeam > 1.2, (2) ASCE41 non-compliant joint transverse reinforcing and or joint V/Vn > 1.2, (3) IGH beam ductility per ASCE41-06 Table 6-7i, (4) Compliant beam transverse reinforcing with LOW beam V / bwd(f'c)^0.5. Costing is on a per joint basis. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 151 | EA 1 | YES | NO | Beams or joints exhibit residual crack widths > 0.06 in. No significant spalling. No fracture or buckling of reinforcing. | Beams or joints exhibit residual crack widths > 0.06 in. Spalling of cover concrete exposes beam and joint transverse reinforcement but not longitudinal reinforcement. No fracture or buckling of reinforcing. | Beams or joints exhibit residual crack widths > 0.06 in. Spalling of cover concrete exposes a significant length of beam longitudinal reinforcement or column longitudinal reinforcement in the joint. Crushing of beam or joint core concrete may occur. Fracture or buckling of reinforcing requiring replacement may occur. |  |  | 1 | 1 | 1 |  |  | 0.0175 | 0.0225 | 0.0322 |  |  | 0.17 | 0.27 | 0.32 |  |  | 0.3 | 0.13 | 0.15 |  |  | 0.4 | 0.4 | 0.4 |  |  | NO | YES | Marginal | Average | Superior | Superior | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 8 feet either side of damaged area. Clean area adjacent to the damaged concrete. Prepare spalled concrete and adjacent cracks, as necessary, to be patched and to receive the epoxy injection. Patch concrete with grout. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems as necessary. | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 15 feet either side of damaged component. Shore damaged member(s) a minimum of one level below (more levels may be required). Remove damaged component. Place and splice (as necessary) new reinforcing steel to existing, undamaged reinforcing. Place concrete forms. Place concrete. Remove forms. Remove shores after one week. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary). | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 15 feet either side of damaged component. Shore damaged member(s) a minimum of one level below (more levels may be required). Remove damaged component. Place and splice (as necessary) new reinforcing steel to existing, undamaged reinforcing. Place concrete forms. Place concrete. Remove forms. Remove shores after one week. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary). |  |  | NO | NO | NO |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | NO | YES |  |  | 0% | 0% | 20% |  |  | 0 | 0 | 0.5 |  |  | None | Not Given | By User | By User | Laura Lowes | B1041.001a-DS1-1.JPG | B1041.031a-DS2-1.JPG | B1041.031a-DS3-1.JPG |  |  | No | 2011-08-24 DS3 beta changed from 0.3 to 0.4 in order to avoid negative probability. | YES
B1041.082a | B1041.082a | Non-conforming MF with weak joints and beam flexural response, Conc Col & Bm = 24" x 36", Beam one side | Non-Conforming MF, joint shear failure, beam flexural response. Meets the following requirements: (1) Sum Mcol / Sum Mbeam > 1.2, (2) ASCE41 non-compliant joint transverse reinforcing and or joint V/Vn > 1.2, (3) IGH beam ductility per ASCE41-06 Table 6-7i, (4) Compliant beam transverse reinforcing with LOW beam V / bwd(f'c)^0.5. Costing is on a per joint basis. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 152 | EA 1 | YES | NO | Beams or joints exhibit residual crack widths > 0.06 in. No significant spalling. No fracture or buckling of reinforcing. | Beams or joints exhibit residual crack widths > 0.06 in. Spalling of cover concrete exposes beam and joint transverse reinforcement but not longitudinal reinforcement. No fracture or buckling of reinforcing. | Beams or joints exhibit residual crack widths > 0.06 in. Spalling of cover concrete exposes a significant length of beam longitudinal reinforcement or column longitudinal reinforcement in the joint. Crushing of beam or joint core concrete may occur. Fracture or buckling of reinforcing requiring replacement may occur. |  |  | 1 | 1 | 1 |  |  | 0.0175 | 0.0225 | 0.0322 |  |  | 0.17 | 0.27 | 0.32 |  |  | 0.3 | 0.13 | 0.15 |  |  | 0.4 | 0.4 | 0.4 |  |  | NO | YES | Marginal | Average | Superior | Superior | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 8 feet either side of damaged area. Clean area adjacent to the damaged concrete. Prepare spalled concrete and adjacent cracks, as necessary, to be patched and to receive the epoxy injection. Patch concrete with grout. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems as necessary. | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 15 feet either side of damaged area. Shore damaged member(s) a minimum of one level below (more levels may be required). Remove damaged concrete at least 1 inch beyond the exposed reinforcing steel. Place concrete forms. Place concrete. Remove forms. Remove shores after one week. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary). | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 15 feet either side of damaged component. Shore damaged member(s) a minimum of one level below (more levels may be required). Remove damaged component. Place and splice (as necessary) new reinforcing steel to existing, undamaged reinforcing. Place concrete forms. Place concrete. Remove forms. Remove shores after one week. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary). |  |  | NO | NO | NO |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | NO | YES |  |  | 0% | 0% | 20% |  |  | 0 | 0 | 0.5 |  |  | None | Not Given | By User | By User | Laura Lowes | B1041.001a-DS1-1.JPG | B1041.031a-DS2-1.JPG | B1041.031a-DS3-1.JPG |  |  | No | 2011-08-24 DS3 beta changed from 0.3 to 0.4 in order to avoid negative probability. | YES
B1041.082b | B1041.082b | Non-conforming MF with weak joints and beam flexural response, Conc Col & Bm = 24" x 36", Beam both sides | Non-Conforming MF, joint shear failure, beam flexural response. Meets the following requirements: (1) Sum Mcol / Sum Mbeam > 1.2, (2) ASCE41 non-compliant joint transverse reinforcing and or joint V/Vn > 1.2, (3) IGH beam ductility per ASCE41-06 Table 6-7i, (4) Compliant beam transverse reinforcing with LOW beam V / bwd(f'c)^0.5. Costing is on a per joint basis. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 153 | EA 1 | YES | NO | Beams or joints exhibit residual crack widths > 0.06 in. No significant spalling. No fracture or buckling of reinforcing. | Beams or joints exhibit residual crack widths > 0.06 in. Spalling of cover concrete exposes beam and joint transverse reinforcement but not longitudinal reinforcement. No fracture or buckling of reinforcing. | Beams or joints exhibit residual crack widths > 0.06 in. Spalling of cover concrete exposes a significant length of beam longitudinal reinforcement or column longitudinal reinforcement in the joint. Crushing of beam or joint core concrete may occur. Fracture or buckling of reinforcing requiring replacement may occur. |  |  | 1 | 1 | 1 |  |  | 0.0175 | 0.0225 | 0.0322 |  |  | 0.17 | 0.27 | 0.32 |  |  | 0.3 | 0.13 | 0.15 |  |  | 0.4 | 0.4 | 0.4 |  |  | NO | YES | Marginal | Average | Superior | Superior | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 8 feet either side of damaged area. Clean area adjacent to the damaged concrete. Prepare spalled concrete and adjacent cracks, as necessary, to be patched and to receive the epoxy injection. Patch concrete with grout. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems as necessary. | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 15 feet either side of damaged area. Shore damaged member(s) a minimum of one level below (more levels may be required). Remove damaged concrete at least 1 inch beyond the exposed reinforcing steel. Place concrete forms. Place concrete. Remove forms. Remove shores after one week. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary). | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 15 feet either side of damaged component. Shore damaged member(s) a minimum of one level below (more levels may be required). Remove damaged component. Place and splice (as necessary) new reinforcing steel to existing, undamaged reinforcing. Place concrete forms. Place concrete. Remove forms. Remove shores after one week. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary). |  |  | NO | NO | NO |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | NO | YES |  |  | 0% | 0% | 20% |  |  | 0 | 0 | 0.5 |  |  | None | Not Given | By User | By User | Laura Lowes | B1041.001a-DS1-1.JPG | B1041.031a-DS2-1.JPG | B1041.031a-DS3-1.JPG |  |  | No | 2011-08-24 DS3 beta changed from 0.3 to 0.4 in order to avoid negative probability. | YES
B1041.083a | B1041.083a | Non-conforming MF with weak joints and beam flexural response, Conc Col & Bm = 36" x 36", Beam one side | Non-Conforming MF, joint shear failure, beam flexural response. Meets the following requirements: (1) Sum Mcol / Sum Mbeam > 1.2, (2) ASCE41 non-compliant joint transverse reinforcing and or joint V/Vn > 1.2, (3) IGH beam ductility per ASCE41-06 Table 6-7i, (4) Compliant beam transverse reinforcing with LOW beam V / bwd(f'c)^0.5. Costing is on a per joint basis. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 154 | EA 1 | YES | NO | Beams or joints exhibit residual crack widths > 0.06 in. No significant spalling. No fracture or buckling of reinforcing. | Beams or joints exhibit residual crack widths > 0.06 in. Spalling of cover concrete exposes beam and joint transverse reinforcement but not longitudinal reinforcement. No fracture or buckling of reinforcing. | Beams or joints exhibit residual crack widths > 0.06 in. Spalling of cover concrete exposes a significant length of beam longitudinal reinforcement or column longitudinal reinforcement in the joint. Crushing of beam or joint core concrete may occur. Fracture or buckling of reinforcing requiring replacement may occur. |  |  | 1 | 1 | 1 |  |  | 0.0175 | 0.0225 | 0.0322 |  |  | 0.17 | 0.27 | 0.32 |  |  | 0.3 | 0.13 | 0.15 |  |  | 0.4 | 0.4 | 0.4 |  |  | NO | YES | Marginal | Average | Superior | Superior | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 8 feet either side of damaged area. Clean area adjacent to the damaged concrete. Prepare spalled concrete and adjacent cracks, as necessary, to be patched and to receive the epoxy injection. Patch concrete with grout. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems as necessary. | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 15 feet either side of damaged area. Shore damaged member(s) a minimum of one level below (more levels may be required). Remove damaged concrete at least 1 inch beyond the exposed reinforcing steel. Place concrete forms. Place concrete. Remove forms. Remove shores after one week. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary). | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 15 feet either side of damaged component. Shore damaged member(s) a minimum of one level below (more levels may be required). Remove damaged component. Place and splice (as necessary) new reinforcing steel to existing, undamaged reinforcing. Place concrete forms. Place concrete. Remove forms. Remove shores after one week. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary). |  |  | NO | NO | NO |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | NO | YES |  |  | 0% | 0% | 20% |  |  | 0 | 0 | 0.5 |  |  | None | Not Given | By User | By User | Laura Lowes | B1041.001a-DS1-1.JPG | B1041.031a-DS2-1.JPG | B1041.031a-DS3-1.JPG |  |  | No | 2011-08-24 DS3 beta changed from 0.3 to 0.4 in order to avoid negative probability. | YES
B1041.083b | B1041.083b | Non-conforming MF with weak joints and beam flexural response, Conc Col & Bm = 36" x 36", Beam both sides | Non-Conforming MF, joint shear failure, beam flexural response. Meets the following requirements: (1) Sum Mcol / Sum Mbeam > 1.2, (2) ASCE41 non-compliant joint transverse reinforcing and or joint V/Vn > 1.2, (3) IGH beam ductility per ASCE41-06 Table 6-7i, (4) Compliant beam transverse reinforcing with LOW beam V / bwd(f'c)^0.5. Costing is on a per joint basis. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 155 | EA 1 | YES | NO | Beams or joints exhibit residual crack widths > 0.06 in. No significant spalling. No fracture or buckling of reinforcing. | Beams or joints exhibit residual crack widths > 0.06 in. Spalling of cover concrete exposes beam and joint transverse reinforcement but not longitudinal reinforcement. No fracture or buckling of reinforcing. | Beams or joints exhibit residual crack widths > 0.06 in. Spalling of cover concrete exposes a significant length of beam longitudinal reinforcement or column longitudinal reinforcement in the joint. Crushing of beam or joint core concrete may occur. Fracture or buckling of reinforcing requiring replacement may occur. |  |  | 1 | 1 | 1 |  |  | 0.0175 | 0.0225 | 0.0322 |  |  | 0.17 | 0.27 | 0.32 |  |  | 0.3 | 0.13 | 0.15 |  |  | 0.4 | 0.4 | 0.4 |  |  | NO | YES | Marginal | Average | Superior | Superior | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 8 feet either side of damaged area. Clean area adjacent to the damaged concrete. Prepare spalled concrete and adjacent cracks, as necessary, to be patched and to receive the epoxy injection. Patch concrete with grout. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems as necessary. | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 15 feet either side of damaged area. Shore damaged member(s) a minimum of one level below (more levels may be required). Remove damaged concrete at least 1 inch beyond the exposed reinforcing steel. Place concrete forms. Place concrete. Remove forms. Remove shores after one week. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary). | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 15 feet either side of damaged component. Shore damaged member(s) a minimum of one level below (more levels may be required). Remove damaged component. Place and splice (as necessary) new reinforcing steel to existing, undamaged reinforcing. Place concrete forms. Place concrete. Remove forms. Remove shores after one week. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary). |  |  | NO | NO | NO |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | NO | YES |  |  | 0% | 0% | 20% |  |  | 0 | 0 | 0.5 |  |  | None | Not Given | By User | By User | Laura Lowes | B1041.001a-DS1-1.JPG | B1041.031a-DS2-1.JPG | B1041.031a-DS3-1.JPG |  |  | No | 2011-08-24 DS3 beta changed from 0.3 to 0.4 in order to avoid negative probability. | YES
B1041.091a | B1041.091a | Non-conforming MF with weak joints and column flexural response, Conc Col & Bm = 24" x 24", Beam one side | Non-Conforming MF, joint shear failure, column flexural response. Meets the following requirements: (1) Sum Mcol / Sum Mbeam < 0.8, (2) [...TBD…], (3) Non-compliant column transverse reinforcement and or joint V/Vn > 1.2 Costing is on a per joint basis. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 156 | EA 1 | YES | NO | Columns exhibit residual crack widths > 0.06 in. No significant spalling. No fracture or buckling of reinf. | Columns exhibit residual crack widths > 0.06 in. Spalling of cover concrete exposes column transverse reinforcement but not longitudinal reinforcement. No fracture or buckling of reinforcing. | Columns exhibit residual crack widths > 0.06 in. Spalling of column cover concrete exposes a significant length of column longitudinal reinforcement. Crushing of column core concrete may occur. Fracture or buckling of reinforcing requiring replacement may occur. |  |  | 1 | 1 | 1 |  |  | 0.015 | 0.0175 | 0.02 |  |  | Not Specified | 0.27 | 0.18 |  |  | 0.4 | 0.15 | 0.35 |  |  | 0.4 | 0.4 | 0.4 |  |  | NO | YES | Marginal | Average | Superior | Superior | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 8 feet either side of damaged area. Clean area adjacent to the damaged concrete. Prepare spalled concrete and adjacent cracks, as necessary, to be patched and to receive the epoxy injection. Patch concrete with grout. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems as necessary. | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 15 feet either side of damaged area. Shore damaged member(s) a minimum of one level below (more levels may be required). Remove damaged concrete at least 1 inch beyond the exposed reinforcing steel. Place concrete forms. Place concrete. Remove forms. Remove shores after one week. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary). | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 15 feet either side of damaged component. Shore damaged member(s) a minimum of one level below (more levels may be required). Remove damaged component. Place and splice (as necessary) new reinforcing steel to existing, undamaged reinforcing. Place concrete forms. Place concrete. Remove forms. Remove shores after one week. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary). |  |  | NO | NO | NO |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | NO | YES |  |  | 0% | 0% | 15% |  |  | 0 | 0 | 0.5 |  |  | This fragility is same as B1041.061. Closest match available. | Not Given | By User | By User | Laura Lowes | none | none | none |  |  | No | 2011-08-24 DS3 beta changed from 0.3 to 0.4 in order to avoid negative probability. | YES
B1041.091b | B1041.091b | Non-conforming MF with weak joints and column flexural response, Conc Col & Bm = 24" x 24", Beam both sides | Non-Conforming MF, joint shear failure, column flexural response. Meets the following requirements: (1) Sum Mcol / Sum Mbeam < 0.8, (2) [...TBD…], (3) Non-compliant column transverse reinforcement and or joint V/Vn > 1.2 Costing is on a per joint basis. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 157 | EA 1 | YES | NO | Columns exhibit residual crack widths > 0.06 in. No significant spalling. No fracture or buckling of reinf. | Columns exhibit residual crack widths > 0.06 in. Spalling of cover concrete exposes column transverse reinforcement but not longitudinal reinforcement. No fracture or buckling of reinforcing. | Columns exhibit residual crack widths > 0.06 in. Spalling of column cover concrete exposes a significant length of column longitudinal reinforcement. Crushing of column core concrete may occur. Fracture or buckling of reinforcing requiring replacement may occur. |  |  | 1 | 1 | 1 |  |  | 0.015 | 0.0175 | 0.02 |  |  | Not Specified | 0.27 | 0.18 |  |  | 0.4 | 0.15 | 0.35 |  |  | 0.4 | 0.4 | 0.4 |  |  | NO | YES | Marginal | Average | Superior | Superior | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 8 feet either side of damaged area. Clean area adjacent to the damaged concrete. Prepare spalled concrete and adjacent cracks, as necessary, to be patched and to receive the epoxy injection. Patch concrete with grout. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems as necessary. | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 15 feet either side of damaged area. Shore damaged member(s) a minimum of one level below (more levels may be required). Remove damaged concrete at least 1 inch beyond the exposed reinforcing steel. Place concrete forms. Place concrete. Remove forms. Remove shores after one week. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary). | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 15 feet either side of damaged component. Shore damaged member(s) a minimum of one level below (more levels may be required). Remove damaged component. Place and splice (as necessary) new reinforcing steel to existing, undamaged reinforcing. Place concrete forms. Place concrete. Remove forms. Remove shores after one week. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary). |  |  | NO | NO | NO |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | NO | YES |  |  | 0% | 0% | 15% |  |  | 0 | 0 | 0.5 |  |  | This fragility is same as B1041.061. Closest match available. | Not Given | By User | By User | Laura Lowes | none | none | none |  |  | No | 2011-08-24 DS3 beta changed from 0.3 to 0.4 in order to avoid negative probability. | YES
B1041.092a | B1041.092a | Non-conforming MF with weak joints and column flexural response, Conc Col & Bm = 24" x 36", Beam one side | Non-Conforming MF, joint shear failure, column flexural response. Meets the following requirements: (1) Sum Mcol / Sum Mbeam < 0.8, (2) [...TBD…], (3) Non-compliant column transverse reinforcement and or joint V/Vn > 1.2 Costing is on a per joint basis. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 158 | EA 1 | YES | NO | Columns exhibit residual crack widths > 0.06 in. No significant spalling. No fracture or buckling of reinf. | Columns exhibit residual crack widths > 0.06 in. Spalling of cover concrete exposes column transverse reinforcement but not longitudinal reinforcement. No fracture or buckling of reinforcing. | Columns exhibit residual crack widths > 0.06 in. Spalling of column cover concrete exposes a significant length of column longitudinal reinforcement. Crushing of column core concrete may occur. Fracture or buckling of reinforcing requiring replacement may occur. |  |  | 1 | 1 | 1 |  |  | 0.015 | 0.0175 | 0.02 |  |  | Not Specified | 0.27 | 0.18 |  |  | 0.4 | 0.15 | 0.35 |  |  | 0.4 | 0.4 | 0.4 |  |  | NO | YES | Marginal | Average | Superior | Superior | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 8 feet either side of damaged area. Clean area adjacent to the damaged concrete. Prepare spalled concrete and adjacent cracks, as necessary, to be patched and to receive the epoxy injection. Patch concrete with grout. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems as necessary. | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 15 feet either side of damaged area. Shore damaged member(s) a minimum of one level below (more levels may be required). Remove damaged concrete at least 1 inch beyond the exposed reinforcing steel. Place concrete forms. Place concrete. Remove forms. Remove shores after one week. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary). | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 15 feet either side of damaged component. Shore damaged member(s) a minimum of one level below (more levels may be required). Remove damaged component. Place and splice (as necessary) new reinforcing steel to existing, undamaged reinforcing. Place concrete forms. Place concrete. Remove forms. Remove shores after one week. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary). |  |  | NO | NO | NO |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | NO | YES |  |  | 0% | 0% | 15% |  |  | 0 | 0 | 0.5 |  |  | This fragility is same as B1041.061. Closest match available. | Not Given | By User | By User | Laura Lowes | none | none | none |  |  | No | 2011-08-24 DS3 beta changed from 0.3 to 0.4 in order to avoid negative probability. | YES
B1041.092b | B1041.092b | Non-conforming MF with weak joints and column flexural response, Conc Col & Bm = 24" x 36", Beam both sides | Non-Conforming MF, joint shear failure, column flexural response. Meets the following requirements: (1) Sum Mcol / Sum Mbeam < 0.8, (2) [...TBD…], (3) Non-compliant column transverse reinforcement and or joint V/Vn > 1.2 Costing is on a per joint basis. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 159 | EA 1 | YES | NO | Columns exhibit residual crack widths > 0.06 in. No significant spalling. No fracture or buckling of reinf. | Columns exhibit residual crack widths > 0.06 in. Spalling of cover concrete exposes column transverse reinforcement but not longitudinal reinforcement. No fracture or buckling of reinforcing. | Columns exhibit residual crack widths > 0.06 in. Spalling of column cover concrete exposes a significant length of column longitudinal reinforcement. Crushing of column core concrete may occur. Fracture or buckling of reinforcing requiring replacement may occur. |  |  | 1 | 1 | 1 |  |  | 0.015 | 0.0175 | 0.02 |  |  | Not Specified | 0.27 | 0.18 |  |  | 0.4 | 0.15 | 0.35 |  |  | 0.4 | 0.4 | 0.4 |  |  | NO | YES | Marginal | Average | Superior | Superior | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 8 feet either side of damaged area. Clean area adjacent to the damaged concrete. Prepare spalled concrete and adjacent cracks, as necessary, to be patched and to receive the epoxy injection. Patch concrete with grout. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems as necessary. | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 15 feet either side of damaged area. Shore damaged member(s) a minimum of one level below (more levels may be required). Remove damaged concrete at least 1 inch beyond the exposed reinforcing steel. Place concrete forms. Place concrete. Remove forms. Remove shores after one week. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary). | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 15 feet either side of damaged component. Shore damaged member(s) a minimum of one level below (more levels may be required). Remove damaged component. Place and splice (as necessary) new reinforcing steel to existing, undamaged reinforcing. Place concrete forms. Place concrete. Remove forms. Remove shores after one week. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary). |  |  | NO | NO | NO |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | NO | YES |  |  | 0% | 0% | 15% |  |  | 0 | 0 | 0.5 |  |  | This fragility is same as B1041.061. Closest match available. | Not Given | By User | By User | Laura Lowes | none | none | none |  |  | No | 2011-08-24 DS3 beta changed from 0.3 to 0.4 in order to avoid negative probability. | YES
B1041.093a | B1041.093a | Non-conforming MF with weak joints and column flexural response, Conc Col & Bm = 36" x 36", Beam one side | Non-Conforming MF, joint shear failure, column flexural response. Meets the following requirements: (1) Sum Mcol / Sum Mbeam < 0.8, (2) [...TBD…], (3) Non-compliant column transverse reinforcement and or joint V/Vn > 1.2 Costing is on a per joint basis. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 160 | EA 1 | YES | NO | Columns exhibit residual crack widths > 0.06 in. No significant spalling. No fracture or buckling of reinf. | Columns exhibit residual crack widths > 0.06 in. Spalling of cover concrete exposes column transverse reinforcement but not longitudinal reinforcement. No fracture or buckling of reinforcing. | Columns exhibit residual crack widths > 0.06 in. Spalling of column cover concrete exposes a significant length of column longitudinal reinforcement. Crushing of column core concrete may occur. Fracture or buckling of reinforcing requiring replacement may occur. |  |  | 1 | 1 | 1 |  |  | 0.015 | 0.0175 | 0.02 |  |  | Not Specified | 0.27 | 0.18 |  |  | 0.4 | 0.15 | 0.35 |  |  | 0.4 | 0.4 | 0.4 |  |  | NO | YES | Marginal | Average | Superior | Superior | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 8 feet either side of damaged area. Clean area adjacent to the damaged concrete. Prepare spalled concrete and adjacent cracks, as necessary, to be patched and to receive the epoxy injection. Patch concrete with grout. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems as necessary. | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 15 feet either side of damaged area. Shore damaged member(s) a minimum of one level below (more levels may be required). Remove damaged concrete at least 1 inch beyond the exposed reinforcing steel. Place concrete forms. Place concrete. Remove forms. Remove shores after one week. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary). | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 15 feet either side of damaged component. Shore damaged member(s) a minimum of one level below (more levels may be required). Remove damaged component. Place and splice (as necessary) new reinforcing steel to existing, undamaged reinforcing. Place concrete forms. Place concrete. Remove forms. Remove shores after one week. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary). |  |  | NO | NO | NO |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | NO | YES |  |  | 0% | 0% | 15% |  |  | 0 | 0 | 0.5 |  |  | This fragility is same as B1041.061. Closest match available. | Not Given | By User | By User | Laura Lowes | none | none | none |  |  | No | 2011-08-24 DS3 beta changed from 0.3 to 0.4 in order to avoid negative probability. | YES
B1041.093b | B1041.093b | Non-conforming MF with weak joints and column flexural response, Conc Col & Bm = 36" x 36", Beam both sides | Non-Conforming MF, joint shear failure, column flexural response. Meets the following requirements: (1) Sum Mcol / Sum Mbeam < 0.8, (2) [...TBD…], (3) Non-compliant column transverse reinforcement and or joint V/Vn > 1.2 Costing is on a per joint basis. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 161 | EA 1 | YES | NO | Columns exhibit residual crack widths > 0.06 in. No significant spalling. No fracture or buckling of reinf. | Columns exhibit residual crack widths > 0.06 in. Spalling of cover concrete exposes column transverse reinforcement but not longitudinal reinforcement. No fracture or buckling of reinforcing. | Columns exhibit residual crack widths > 0.06 in. Spalling of column cover concrete exposes a significant length of column longitudinal reinforcement. Crushing of column core concrete may occur. Fracture or buckling of reinforcing requiring replacement may occur. |  |  | 1 | 1 | 1 |  |  | 0.015 | 0.0175 | 0.02 |  |  | Not Specified | 0.27 | 0.18 |  |  | 0.4 | 0.15 | 0.35 |  |  | 0.4 | 0.4 | 0.4 |  |  | NO | YES | Marginal | Average | Superior | Superior | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 8 feet either side of damaged area. Clean area adjacent to the damaged concrete. Prepare spalled concrete and adjacent cracks, as necessary, to be patched and to receive the epoxy injection. Patch concrete with grout. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems as necessary. | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 15 feet either side of damaged area. Shore damaged member(s) a minimum of one level below (more levels may be required). Remove damaged concrete at least 1 inch beyond the exposed reinforcing steel. Place concrete forms. Place concrete. Remove forms. Remove shores after one week. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary). | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 15 feet either side of damaged component. Shore damaged member(s) a minimum of one level below (more levels may be required). Remove damaged component. Place and splice (as necessary) new reinforcing steel to existing, undamaged reinforcing. Place concrete forms. Place concrete. Remove forms. Remove shores after one week. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary). |  |  | NO | NO | NO |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | NO | YES |  |  | 0% | 0% | 15% |  |  | 0 | 0 | 0.5 |  |  | This fragility is same as B1041.061. Closest match available. | Not Given | By User | By User | Laura Lowes | none | none | none |  |  | No | 2011-08-24 DS3 beta changed from 0.3 to 0.4 in order to avoid negative probability. | YES
B1041.101a | B1041.101a | Non-conforming MF, weak beams and strong joints, Conc Col & Bm = 24" x 24", Beam one side | Non-Conforming MF, beam shear failure, beam flexural response. Meets the following requirements: (1) Beam with HIGH V/bwd(f'c)^0.5 or non-compliant transverse beam reinforcing. Costing is on a per joint basis. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 162 | EA 1 | YES | NO | Beams exhibit residual crack widths > 0.06 in. No significant spalling. No fracture or buckling of reinforcing. | Beams exhibit residual crack widths > 0.06 in. Spalling of cover concrete exposes beam and joint transverse reinforcement but not longitudinal reinforcement. No fracture or buckling of reinforcing. | Beams exhibit residual crack widths > 0.06 in. Spalling of beam cover concrete exposes a significant length of beam longitudinal reinforcement. Crushing of beam core concrete may occur. Fracture or buckling of reinforcing requiring replacement may occur. |  |  | 1 | 1 | 1 |  |  | 0.015 | 0.02 | 0.025 |  |  | Not Specified | 0.27 | 0.15 |  |  | 0.4 | 0.15 | 0.35 |  |  | 0.4 | 0.4 | 0.4 |  |  | NO | YES | Marginal | Average | Superior | Superior | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 8 feet either side of damaged area. Clean area adjacent to the damaged concrete. Prepare spalled concrete and adjacent cracks, as necessary, to be patched and to receive the epoxy injection. Patch concrete with grout. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems as necessary. | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 15 feet either side of damaged area. Shore damaged member(s) a minimum of one level below (more levels may be required). Remove damaged concrete at least 1 inch beyond the exposed reinforcing steel. Place concrete forms. Place concrete. Remove forms. Remove shores after one week. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary). | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 15 feet either side of damaged component. Shore damaged member(s) a minimum of one level below (more levels may be required). Remove damaged component. Place and splice (as necessary) new reinforcing steel to existing, undamaged reinforcing. Place concrete forms. Place concrete. Remove forms. Remove shores after one week. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary). |  |  | NO | NO | NO |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | NO | YES |  |  | 0% | 0% | 25% |  |  | 0 | 0 | 0.5 |  |  | None | Not Given | By User | By User | Laura Lowes | B1041.051a-DS1-1.JPG | B1041.051a-DS2-1.JPG | B1041.051a-DS3-1.JPG |  |  | No | 2011-08-24 DS3 beta changed from 0.3 to 0.4 in order to avoid negative probability. | YES
B1041.101b | B1041.101b | Non-conforming MF, weak beams and strong joints, Conc Col & Bm = 24" x 24", Beam both sides | Non-Conforming MF, beam shear failure, beam flexural response. Meets the following requirements: (1) Beam with HIGH V/bwd(f'c)^0.5 or non-compliant transverse beam reinforcing. Costing is on a per joint basis. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 163 | EA 1 | YES | NO | Beams exhibit residual crack widths > 0.06 in. No significant spalling. No fracture or buckling of reinforcing. | Beams exhibit residual crack widths > 0.06 in. Spalling of cover concrete exposes beam and joint transverse reinforcement but not longitudinal reinforcement. No fracture or buckling of reinforcing. | Beams exhibit residual crack widths > 0.06 in. Spalling of beam cover concrete exposes a significant length of beam longitudinal reinforcement. Crushing of beam core concrete may occur. Fracture or buckling of reinforcing requiring replacement may occur. |  |  | 1 | 1 | 1 |  |  | 0.015 | 0.02 | 0.025 |  |  | Not Specified | 0.27 | 0.15 |  |  | 0.4 | 0.15 | 0.35 |  |  | 0.4 | 0.4 | 0.4 |  |  | NO | YES | Marginal | Average | Superior | Superior | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 8 feet either side of damaged area. Clean area adjacent to the damaged concrete. Prepare spalled concrete and adjacent cracks, as necessary, to be patched and to receive the epoxy injection. Patch concrete with grout. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems as necessary. | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 15 feet either side of damaged area. Shore damaged member(s) a minimum of one level below (more levels may be required). Remove damaged concrete at least 1 inch beyond the exposed reinforcing steel. Place concrete forms. Place concrete. Remove forms. Remove shores after one week. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary). | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 15 feet either side of damaged component. Shore damaged member(s) a minimum of one level below (more levels may be required). Remove damaged component. Place and splice (as necessary) new reinforcing steel to existing, undamaged reinforcing. Place concrete forms. Place concrete. Remove forms. Remove shores after one week. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary). |  |  | NO | NO | NO |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | NO | YES |  |  | 0% | 0% | 25% |  |  | 0 | 0 | 0.5 |  |  | None | Not Given | By User | By User | Laura Lowes | B1041.051a-DS1-1.JPG | B1041.051a-DS2-1.JPG | B1041.051a-DS3-1.JPG |  |  | No | 2011-08-24 DS3 beta changed from 0.3 to 0.4 in order to avoid negative probability. | YES
B1041.102a | B1041.102a | Non-conforming MF, weak beams and strong joints, Conc Col & Bm = 24" x 36", Beam one side | Non-Conforming MF, beam shear failure, beam flexural response. Meets the following requirements: (1) Beam with HIGH V/bwd(f'c)^0.5 or non-compliant transverse beam reinforcing. Costing is on a per joint basis. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 164 | EA 1 | YES | NO | Beams exhibit residual crack widths > 0.06 in. No significant spalling. No fracture or buckling of reinforcing. | Beams exhibit residual crack widths > 0.06 in. Spalling of cover concrete exposes beam and joint transverse reinforcement but not longitudinal reinforcement. No fracture or buckling of reinforcing. | Beams exhibit residual crack widths > 0.06 in. Spalling of beam cover concrete exposes a significant length of beam longitudinal reinforcement. Crushing of beam core concrete may occur. Fracture or buckling of reinforcing requiring replacement may occur. |  |  | 1 | 1 | 1 |  |  | 0.015 | 0.02 | 0.025 |  |  | Not Specified | 0.27 | 0.15 |  |  | 0.4 | 0.15 | 0.35 |  |  | 0.4 | 0.4 | 0.4 |  |  | NO | YES | Marginal | Average | Superior | Superior | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 8 feet either side of damaged area. Clean area adjacent to the damaged concrete. Prepare spalled concrete and adjacent cracks, as necessary, to be patched and to receive the epoxy injection. Patch concrete with grout. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems as necessary. | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 15 feet either side of damaged area. Shore damaged member(s) a minimum of one level below (more levels may be required). Remove damaged concrete at least 1 inch beyond the exposed reinforcing steel. Place concrete forms. Place concrete. Remove forms. Remove shores after one week. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary). | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 15 feet either side of damaged component. Shore damaged member(s) a minimum of one level below (more levels may be required). Remove damaged component. Place and splice (as necessary) new reinforcing steel to existing, undamaged reinforcing. Place concrete forms. Place concrete. Remove forms. Remove shores after one week. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary). |  |  | NO | NO | NO |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | NO | YES |  |  | 0% | 0% | 25% |  |  | 0 | 0 | 0.5 |  |  | None | Not Given | By User | By User | Laura Lowes | B1041.051a-DS1-1.JPG | B1041.051a-DS2-1.JPG | B1041.051a-DS3-1.JPG |  |  | No | 2011-08-24 DS3 beta changed from 0.3 to 0.4 in order to avoid negative probability. | YES
B1041.102b | B1041.102b | Non-conforming MF, weak beams and strong joints, Conc Col & Bm = 24" x 36", Beam both sides | Non-Conforming MF, beam shear failure, beam flexural response. Meets the following requirements: (1) Beam with HIGH V/bwd(f'c)^0.5 or non-compliant transverse beam reinforcing. Costing is on a per joint basis. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 165 | EA 1 | YES | NO | Beams exhibit residual crack widths > 0.06 in. No significant spalling. No fracture or buckling of reinforcing. | Beams exhibit residual crack widths > 0.06 in. Spalling of cover concrete exposes beam and joint transverse reinforcement but not longitudinal reinforcement. No fracture or buckling of reinforcing. | Beams exhibit residual crack widths > 0.06 in. Spalling of beam cover concrete exposes a significant length of beam longitudinal reinforcement. Crushing of beam core concrete may occur. Fracture or buckling of reinforcing requiring replacement may occur. |  |  | 1 | 1 | 1 |  |  | 0.015 | 0.02 | 0.025 |  |  | Not Specified | 0.27 | 0.15 |  |  | 0.4 | 0.15 | 0.35 |  |  | 0.4 | 0.4 | 0.4 |  |  | NO | YES | Marginal | Average | Superior | Superior | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 8 feet either side of damaged area. Clean area adjacent to the damaged concrete. Prepare spalled concrete and adjacent cracks, as necessary, to be patched and to receive the epoxy injection. Patch concrete with grout. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems as necessary. | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 15 feet either side of damaged area. Shore damaged member(s) a minimum of one level below (more levels may be required). Remove damaged concrete at least 1 inch beyond the exposed reinforcing steel. Place concrete forms. Place concrete. Remove forms. Remove shores after one week. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary). | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 15 feet either side of damaged component. Shore damaged member(s) a minimum of one level below (more levels may be required). Remove damaged component. Place and splice (as necessary) new reinforcing steel to existing, undamaged reinforcing. Place concrete forms. Place concrete. Remove forms. Remove shores after one week. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary). |  |  | NO | NO | NO |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | NO | YES |  |  | 0% | 0% | 25% |  |  | 0 | 0 | 0.5 |  |  | None | Not Given | By User | By User | Laura Lowes | B1041.051a-DS1-1.JPG | B1041.051a-DS2-1.JPG | B1041.051a-DS3-1.JPG |  |  | No | 2011-08-24 DS3 beta changed from 0.3 to 0.4 in order to avoid negative probability. | YES
B1041.103a | B1041.103a | Non-conforming MF, weak beams and strong joints, Conc Col & Bm = 36" x 36", Beam one side | Non-Conforming MF, beam shear failure, beam flexural response. Meets the following requirements: (1) Beam with HIGH V/bwd(f'c)^0.5 or non-compliant transverse beam reinforcing. Costing is on a per joint basis. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 166 | EA 1 | YES | NO | Beams exhibit residual crack widths > 0.06 in. No significant spalling. No fracture or buckling of reinforcing. | Beams exhibit residual crack widths > 0.06 in. Spalling of cover concrete exposes beam and joint transverse reinforcement but not longitudinal reinforcement. No fracture or buckling of reinforcing. | Beams exhibit residual crack widths > 0.06 in. Spalling of beam cover concrete exposes a significant length of beam longitudinal reinforcement. Crushing of beam core concrete may occur. Fracture or buckling of reinforcing requiring replacement may occur. |  |  | 1 | 1 | 1 |  |  | 0.015 | 0.02 | 0.025 |  |  | Not Specified | 0.27 | 0.15 |  |  | 0.4 | 0.15 | 0.35 |  |  | 0.4 | 0.4 | 0.4 |  |  | NO | YES | Marginal | Average | Superior | Superior | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 8 feet either side of damaged area. Clean area adjacent to the damaged concrete. Prepare spalled concrete and adjacent cracks, as necessary, to be patched and to receive the epoxy injection. Patch concrete with grout. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems as necessary. | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 15 feet either side of damaged area. Shore damaged member(s) a minimum of one level below (more levels may be required). Remove damaged concrete at least 1 inch beyond the exposed reinforcing steel. Place concrete forms. Place concrete. Remove forms. Remove shores after one week. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary). | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 15 feet either side of damaged component. Shore damaged member(s) a minimum of one level below (more levels may be required). Remove damaged component. Place and splice (as necessary) new reinforcing steel to existing, undamaged reinforcing. Place concrete forms. Place concrete. Remove forms. Remove shores after one week. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary). |  |  | NO | NO | NO |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | NO | YES |  |  | 0% | 0% | 25% |  |  | 0 | 0 | 0.5 |  |  | None | Not Given | By User | By User | Laura Lowes | B1041.051a-DS1-1.JPG | B1041.051a-DS2-1.JPG | B1041.051a-DS3-1.JPG |  |  | No | 2011-08-24 DS3 beta changed from 0.3 to 0.4 in order to avoid negative probability. | YES
B1041.103b | B1041.103b | Non-conforming MF, weak beams and strong joints, Conc Col & Bm = 36" x 36", Beam both sides | Non-Conforming MF, beam shear failure, beam flexural response. Meets the following requirements: (1) Beam with HIGH V/bwd(f'c)^0.5 or non-compliant transverse beam reinforcing. Costing is on a per joint basis. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 167 | EA 1 | YES | NO | Beams exhibit residual crack widths > 0.06 in. No significant spalling. No fracture or buckling of reinforcing. | Beams exhibit residual crack widths > 0.06 in. Spalling of cover concrete exposes beam and joint transverse reinforcement but not longitudinal reinforcement. No fracture or buckling of reinforcing. | Beams exhibit residual crack widths > 0.06 in. Spalling of beam cover concrete exposes a significant length of beam longitudinal reinforcement. Crushing of beam core concrete may occur. Fracture or buckling of reinforcing requiring replacement may occur. |  |  | 1 | 1 | 1 |  |  | 0.015 | 0.02 | 0.025 |  |  | Not Specified | 0.27 | 0.15 |  |  | 0.4 | 0.15 | 0.35 |  |  | 0.4 | 0.4 | 0.4 |  |  | NO | YES | Marginal | Average | Superior | Superior | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 8 feet either side of damaged area. Clean area adjacent to the damaged concrete. Prepare spalled concrete and adjacent cracks, as necessary, to be patched and to receive the epoxy injection. Patch concrete with grout. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems as necessary. | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 15 feet either side of damaged area. Shore damaged member(s) a minimum of one level below (more levels may be required). Remove damaged concrete at least 1 inch beyond the exposed reinforcing steel. Place concrete forms. Place concrete. Remove forms. Remove shores after one week. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary). | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 15 feet either side of damaged component. Shore damaged member(s) a minimum of one level below (more levels may be required). Remove damaged component. Place and splice (as necessary) new reinforcing steel to existing, undamaged reinforcing. Place concrete forms. Place concrete. Remove forms. Remove shores after one week. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary). |  |  | NO | NO | NO |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | NO | YES |  |  | 0% | 0% | 25% |  |  | 0 | 0 | 0.5 |  |  | None | Not Given | By User | By User | Laura Lowes | B1041.051a-DS1-1.JPG | B1041.051a-DS2-1.JPG | B1041.051a-DS3-1.JPG |  |  | No | 2011-08-24 DS3 beta changed from 0.3 to 0.4 in order to avoid negative probability. | YES
B1041.111a | B1041.111a | Non-conforming MF, weak columns, Conc Col & Bm = 24" x 24", Beam one side | Non-Conforming MF, column flexure-shear or shear failure, column flexural response. Meets the following requirements: (1) […TBD…] Costing is on a per joint basis. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 168 | EA 1 | YES | NO | Columns exhibit residual crack widths > 0.06 in. No significant spalling. No fracture or buckling of reinforcing. | Columns exhibit residual crack widths > 0.06 in. Spalling of cover concrete exposes column transverse reinforcement but not longitudinal reinforcement. No fracture or buckling of reinforcing. | Columns exhibit residual crack widths > 0.06 in. Spalling of column cover concrete exposes a significant length of column longitudinal reinforcement. Crushing of column core concrete may occur. Fracture or buckling of reinforcing requiring replacement may occur. |  |  | 1 | 1 | 1 |  |  | 0.015 | 0.02 | 0.025 |  |  | Not Specified | 0.27 | 0.15 |  |  | 0.4 | 0.15 | 0.35 |  |  | 0.4 | 0.4 | 0.4 |  |  | NO | YES | Marginal | Average | Superior | Superior | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 8 feet either side of damaged area. Clean area adjacent to the damaged concrete. Prepare spalled concrete and adjacent cracks, as necessary, to be patched and to receive the epoxy injection. Patch concrete with grout. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems as necessary. | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 15 feet either side of damaged area. Shore damaged member(s) a minimum of one level below (more levels may be required). Remove damaged concrete at least 1 inch beyond the exposed reinforcing steel. Place concrete forms. Place concrete. Remove forms. Remove shores after one week. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary). | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 15 feet either side of damaged component. Shore damaged member(s) a minimum of one level below (more levels may be required). Remove damaged component. Place and splice (as necessary) new reinforcing steel to existing, undamaged reinforcing. Place concrete forms. Place concrete. Remove forms. Remove shores after one week. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary). |  |  | NO | NO | NO |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | NO | YES |  |  | 0% | 0% | 10% |  |  | 0 | 0 | 0.5 |  |  | None | Not Given | By User | By User | Laura Lowes | B1041.051a-DS1-1.JPG | B1041.051a-DS2-1.JPG | B1041.051a-DS3-1.JPG |  |  | No | 2011-08-24 DS3 beta changed from 0.3 to 0.4 in order to avoid negative probability. | YES
B1041.111b | B1041.111b | Non-conforming MF, weak columns, Conc Col & Bm = 24" x 24", Beam both sides | Non-Conforming MF, column flexure-shear or shear failure, column flexural response. Meets the following requirements: (1) […TBD…] Costing is on a per joint basis. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 169 | EA 1 | YES | NO | Columns exhibit residual crack widths > 0.06 in. No significant spalling. No fracture or buckling of reinforcing. | Columns exhibit residual crack widths > 0.06 in. Spalling of cover concrete exposes column transverse reinforcement but not longitudinal reinforcement. No fracture or buckling of reinforcing. | Columns exhibit residual crack widths > 0.06 in. Spalling of column cover concrete exposes a significant length of column longitudinal reinforcement. Crushing of column core concrete may occur. Fracture or buckling of reinforcing requiring replacement may occur. |  |  | 1 | 1 | 1 |  |  | 0.015 | 0.02 | 0.025 |  |  | Not Specified | 0.27 | 0.15 |  |  | 0.4 | 0.15 | 0.35 |  |  | 0.4 | 0.4 | 0.4 |  |  | NO | YES | Marginal | Average | Superior | Superior | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 8 feet either side of damaged area. Clean area adjacent to the damaged concrete. Prepare spalled concrete and adjacent cracks, as necessary, to be patched and to receive the epoxy injection. Patch concrete with grout. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems as necessary. | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 15 feet either side of damaged area. Shore damaged member(s) a minimum of one level below (more levels may be required). Remove damaged concrete at least 1 inch beyond the exposed reinforcing steel. Place concrete forms. Place concrete. Remove forms. Remove shores after one week. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary). | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 15 feet either side of damaged component. Shore damaged member(s) a minimum of one level below (more levels may be required). Remove damaged component. Place and splice (as necessary) new reinforcing steel to existing, undamaged reinforcing. Place concrete forms. Place concrete. Remove forms. Remove shores after one week. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary). |  |  | NO | NO | NO |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | NO | YES |  |  | 0% | 0% | 10% |  |  | 0 | 0 | 0.5 |  |  | None | Not Given | By User | By User | Laura Lowes | B1041.051a-DS1-1.JPG | B1041.051a-DS2-1.JPG | B1041.051a-DS3-1.JPG |  |  | No | 2011-08-24 DS3 beta changed from 0.3 to 0.4 in order to avoid negative probability. | YES
B1041.112a | B1041.112a | Non-conforming MF, weak columns, Conc Col & Bm = 24" x 36", Beam one side | Non-Conforming MF, column flexure-shear or shear failure, column flexural response. Meets the following requirements: (1) […TBD…] Costing is on a per joint basis. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 170 | EA 1 | YES | NO | Columns exhibit residual crack widths > 0.06 in. No significant spalling. No fracture or buckling of reinforcing. | Columns exhibit residual crack widths > 0.06 in. Spalling of cover concrete exposes column transverse reinforcement but not longitudinal reinforcement. No fracture or buckling of reinforcing. | Columns exhibit residual crack widths > 0.06 in. Spalling of column cover concrete exposes a significant length of column longitudinal reinforcement. Crushing of column core concrete may occur. Fracture or buckling of reinforcing requiring replacement may occur. |  |  | 1 | 1 | 1 |  |  | 0.015 | 0.02 | 0.025 |  |  | Not Specified | 0.27 | 0.15 |  |  | 0.4 | 0.15 | 0.35 |  |  | 0.4 | 0.4 | 0.4 |  |  | NO | YES | Marginal | Average | Superior | Superior | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 8 feet either side of damaged area. Clean area adjacent to the damaged concrete. Prepare spalled concrete and adjacent cracks, as necessary, to be patched and to receive the epoxy injection. Patch concrete with grout. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems as necessary. | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 15 feet either side of damaged area. Shore damaged member(s) a minimum of one level below (more levels may be required). Remove damaged concrete at least 1 inch beyond the exposed reinforcing steel. Place concrete forms. Place concrete. Remove forms. Remove shores after one week. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary). | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 15 feet either side of damaged component. Shore damaged member(s) a minimum of one level below (more levels may be required). Remove damaged component. Place and splice (as necessary) new reinforcing steel to existing, undamaged reinforcing. Place concrete forms. Place concrete. Remove forms. Remove shores after one week. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary). |  |  | NO | NO | NO |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | NO | YES |  |  | 0% | 0% | 10% |  |  | 0 | 0 | 0.5 |  |  | None | Not Given | By User | By User | Laura Lowes | B1041.051a-DS1-1.JPG | B1041.051a-DS2-1.JPG | B1041.051a-DS3-1.JPG |  |  | No | 2011-08-24 DS3 beta changed from 0.3 to 0.4 in order to avoid negative probability. | YES
B1041.112b | B1041.112b | Non-conforming MF, weak columns, Conc Col & Bm = 24" x 36", Beam both sides | Non-Conforming MF, column flexure-shear or shear failure, column flexural response. Meets the following requirements: (1) […TBD…] Costing is on a per joint basis. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 171 | EA 1 | YES | NO | Columns exhibit residual crack widths > 0.06 in. No significant spalling. No fracture or buckling of reinforcing. | Columns exhibit residual crack widths > 0.06 in. Spalling of cover concrete exposes column transverse reinforcement but not longitudinal reinforcement. No fracture or buckling of reinforcing. | Columns exhibit residual crack widths > 0.06 in. Spalling of column cover concrete exposes a significant length of column longitudinal reinforcement. Crushing of column core concrete may occur. Fracture or buckling of reinforcing requiring replacement may occur. |  |  | 1 | 1 | 1 |  |  | 0.015 | 0.02 | 0.025 |  |  | Not Specified | 0.27 | 0.15 |  |  | 0.4 | 0.15 | 0.35 |  |  | 0.4 | 0.4 | 0.4 |  |  | NO | YES | Marginal | Average | Superior | Superior | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 8 feet either side of damaged area. Clean area adjacent to the damaged concrete. Prepare spalled concrete and adjacent cracks, as necessary, to be patched and to receive the epoxy injection. Patch concrete with grout. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems as necessary. | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 15 feet either side of damaged area. Shore damaged member(s) a minimum of one level below (more levels may be required). Remove damaged concrete at least 1 inch beyond the exposed reinforcing steel. Place concrete forms. Place concrete. Remove forms. Remove shores after one week. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary). | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 15 feet either side of damaged component. Shore damaged member(s) a minimum of one level below (more levels may be required). Remove damaged component. Place and splice (as necessary) new reinforcing steel to existing, undamaged reinforcing. Place concrete forms. Place concrete. Remove forms. Remove shores after one week. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary). |  |  | NO | NO | NO |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | NO | YES |  |  | 0% | 0% | 10% |  |  | 0 | 0 | 0.5 |  |  | None | Not Given | By User | By User | Laura Lowes | B1041.051a-DS1-1.JPG | B1041.051a-DS2-1.JPG | B1041.051a-DS3-1.JPG |  |  | No | 2011-08-24 DS3 beta changed from 0.3 to 0.4 in order to avoid negative probability. | YES
B1041.113a | B1041.113a | Non-conforming MF, weak columns, Conc Col & Bm = 36" x 36", Beam one side | Non-Conforming MF, column flexure-shear or shear failure, column flexural response. Meets the following requirements: (1) […TBD…] Costing is on a per joint basis. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 172 | EA 1 | YES | NO | Columns exhibit residual crack widths > 0.06 in. No significant spalling. No fracture or buckling of reinforcing. | Columns exhibit residual crack widths > 0.06 in. Spalling of cover concrete exposes column transverse reinforcement but not longitudinal reinforcement. No fracture or buckling of reinforcing. | Columns exhibit residual crack widths > 0.06 in. Spalling of column cover concrete exposes a significant length of column longitudinal reinforcement. Crushing of column core concrete may occur. Fracture or buckling of reinforcing requiring replacement may occur. |  |  | 1 | 1 | 1 |  |  | 0.015 | 0.02 | 0.025 |  |  | Not Specified | 0.27 | 0.15 |  |  | 0.4 | 0.15 | 0.35 |  |  | 0.4 | 0.4 | 0.4 |  |  | NO | YES | Marginal | Average | Superior | Superior | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 8 feet either side of damaged area. Clean area adjacent to the damaged concrete. Prepare spalled concrete and adjacent cracks, as necessary, to be patched and to receive the epoxy injection. Patch concrete with grout. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems as necessary. | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 15 feet either side of damaged area. Shore damaged member(s) a minimum of one level below (more levels may be required). Remove damaged concrete at least 1 inch beyond the exposed reinforcing steel. Place concrete forms. Place concrete. Remove forms. Remove shores after one week. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary). | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 15 feet either side of damaged component. Shore damaged member(s) a minimum of one level below (more levels may be required). Remove damaged component. Place and splice (as necessary) new reinforcing steel to existing, undamaged reinforcing. Place concrete forms. Place concrete. Remove forms. Remove shores after one week. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary). |  |  | NO | NO | NO |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | NO | YES |  |  | 0% | 0% | 10% |  |  | 0 | 0 | 0.5 |  |  | None | Not Given | By User | By User | Laura Lowes | B1041.051a-DS1-1.JPG | B1041.051a-DS2-1.JPG | B1041.051a-DS3-1.JPG |  |  | No | 2011-08-24 DS3 beta changed from 0.3 to 0.4 in order to avoid negative probability. | YES
B1041.113b | B1041.113b | Non-conforming MF, weak columns, Conc Col & Bm = 36" x 36", Beam both sides | Non-Conforming MF, column flexure-shear or shear failure, column flexural response. Meets the following requirements: (1) […TBD…] Costing is on a per joint basis. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 173 | EA 1 | YES | NO | Columns exhibit residual crack widths > 0.06 in. No significant spalling. No fracture or buckling of reinforcing. | Columns exhibit residual crack widths > 0.06 in. Spalling of cover concrete exposes column transverse reinforcement but not longitudinal reinforcement. No fracture or buckling of reinforcing. | Columns exhibit residual crack widths > 0.06 in. Spalling of column cover concrete exposes a significant length of column longitudinal reinforcement. Crushing of column core concrete may occur. Fracture or buckling of reinforcing requiring replacement may occur. |  |  | 1 | 1 | 1 |  |  | 0.015 | 0.02 | 0.025 |  |  | Not Specified | 0.27 | 0.15 |  |  | 0.4 | 0.15 | 0.35 |  |  | 0.4 | 0.4 | 0.4 |  |  | NO | YES | Marginal | Average | Superior | Superior | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 8 feet either side of damaged area. Clean area adjacent to the damaged concrete. Prepare spalled concrete and adjacent cracks, as necessary, to be patched and to receive the epoxy injection. Patch concrete with grout. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems as necessary. | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 15 feet either side of damaged area. Shore damaged member(s) a minimum of one level below (more levels may be required). Remove damaged concrete at least 1 inch beyond the exposed reinforcing steel. Place concrete forms. Place concrete. Remove forms. Remove shores after one week. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary). | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 15 feet either side of damaged component. Shore damaged member(s) a minimum of one level below (more levels may be required). Remove damaged component. Place and splice (as necessary) new reinforcing steel to existing, undamaged reinforcing. Place concrete forms. Place concrete. Remove forms. Remove shores after one week. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary). |  |  | NO | NO | NO |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | NO | YES |  |  | 0% | 0% | 10% |  |  | 0 | 0 | 0.5 |  |  | None | Not Given | By User | By User | Laura Lowes | B1041.051a-DS1-1.JPG | B1041.051a-DS2-1.JPG | B1041.051a-DS3-1.JPG |  |  | No | 2011-08-24 DS3 beta changed from 0.3 to 0.4 in order to avoid negative probability. | YES
B1041.121a | B1041.121a | Non-conforming MF, weak columns and strong joints, Conc Col & Bm = 24" x 24", Beam both sides | Non-Conforming MF, column flexure, flexure-shear, or shear failure, column flexural response. Meets the following requirements: (1) Column Pu > 0.6f'cAg, (2) Column Vn < Veq Costing is on a per joint basis. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 174 | EA 1 | YES | NO | Concrete Cracking: beams, joints or possibly. Residual concrete crack widths exceed 0.06in. (1.5 mm). Column exhibits residual crack widths that require epoxy injection. | Concrete Crushing: slabs, beams or joints. Spalling of beam, column or joint cover concrete exposes longitudinal reinforcement or strength loss initiates in laboratory testing. Exhibits concrete spalling that exposes longitudinal steel or crushing of core concrete. |  |  |  | 1 | 1 |  |  |  | 0.0025 | 0.005 |  |  |  | Not Specified | Not Specified |  |  |  | 0.4 | 0.5 |  |  |  | 0.4 | 0.5 |  |  |  | NO | YES | Marginal | Average | Superior | Superior | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 8 feet either side of damaged area. Clean area adjacent to the damaged concrete. Prepare spalled concrete and adjacent cracks, as necessary, to be patched and to receive the epoxy injection. Patch concrete with grout. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems as necessary. | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 15 feet either side of damaged component. Shore damaged member(s) a minimum of one level below (more levels may be required). Remove damaged component. Place and splice (as necessary) new reinforcing steel to existing, undamaged reinforcing. Place concrete forms. Place concrete. Remove forms. Remove shores after one week. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary). |  |  |  | NO | NO |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | YES |  |  |  | 0% | 10% |  |  |  | 0 | 0.5 |  |  |  | None | Not Given | By User | By User | Laura Lowes | B1041.071a-DS1-2.JPG | B1041.071a-DS2-1.JPG |  |  |  | No | 2011-08-24 Negative probability below 0.1% drift - overlap deemed acceptable. | YES
B1041.121b | B1041.121b | Non-conforming MF, weak columns and strong joints, Conc Col & Bm = 24" x 24", Beam one side | Non-Conforming MF, column flexure, flexure-shear, or shear failure, column flexural response. Meets the following requirements: (1) Column Pu > 0.6f'cAg, (2) Column Vn < Veq Costing is on a per joint basis. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 175 | EA 1 | YES | NO | Concrete Cracking: beams, joints or possibly. Residual concrete crack widths exceed 0.06in. (1.5 mm). Column exhibits residual crack widths that require epoxy injection. | Concrete Crushing: slabs, beams or joints. Spalling of beam, column or joint cover concrete exposes longitudinal reinforcement or strength loss initiates in laboratory testing. Exhibits concrete spalling that exposes longitudinal steel or crushing of core concrete. |  |  |  | 1 | 1 |  |  |  | 0.0025 | 0.005 |  |  |  | Not Specified | Not Specified |  |  |  | 0.4 | 0.5 |  |  |  | 0.4 | 0.5 |  |  |  | NO | YES | Marginal | Average | Superior | Superior | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 8 feet either side of damaged area. Clean area adjacent to the damaged concrete. Prepare spalled concrete and adjacent cracks, as necessary, to be patched and to receive the epoxy injection. Patch concrete with grout. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems as necessary. | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 15 feet either side of damaged component. Shore damaged member(s) a minimum of one level below (more levels may be required). Remove damaged component. Place and splice (as necessary) new reinforcing steel to existing, undamaged reinforcing. Place concrete forms. Place concrete. Remove forms. Remove shores after one week. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary). |  |  |  | NO | NO |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | YES |  |  |  | 0% | 10% |  |  |  | 0 | 0.5 |  |  |  | None | Not Given | By User | By User | Laura Lowes | B1041.071a-DS1-2.JPG | B1041.071a-DS2-1.JPG |  |  |  | No | 2011-08-24 Negative probability below 0.1% drift - overlap deemed acceptable. | YES
B1041.122a | B1041.122a | Non-conforming MF, weak columns and strong joints, Conc Col & Bm = 24" x 36", Beam one side | Non-Conforming MF, column flexure, flexure-shear, or shear failure, column flexural response. Meets the following requirements: (1) Column Pu > 0.6f'cAg, (2) Column Vn < Veq Costing is on a per joint basis. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 176 | EA 1 | YES | NO | Concrete Cracking: beams, joints or possibly. Residual concrete crack widths exceed 0.06in. (1.5 mm). Column exhibits residual crack widths that require epoxy injection. | Concrete Crushing: slabs, beams or joints. Spalling of beam, column or joint cover concrete exposes longitudinal reinforcement or strength loss initiates in laboratory testing. Exhibits concrete spalling that exposes longitudinal steel or crushing of core concrete. |  |  |  | 1 | 1 |  |  |  | 0.0025 | 0.005 |  |  |  | Not Specified | Not Specified |  |  |  | 0.4 | 0.5 |  |  |  | 0.4 | 0.5 |  |  |  | NO | YES | Marginal | Average | Superior | Superior | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 8 feet either side of damaged area. Clean area adjacent to the damaged concrete. Prepare spalled concrete and adjacent cracks, as necessary, to be patched and to receive the epoxy injection. Patch concrete with grout. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems as necessary. | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 15 feet either side of damaged component. Shore damaged member(s) a minimum of one level below (more levels may be required). Remove damaged component. Place and splice (as necessary) new reinforcing steel to existing, undamaged reinforcing. Place concrete forms. Place concrete. Remove forms. Remove shores after one week. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary). |  |  |  | NO | NO |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | YES |  |  |  | 0% | 10% |  |  |  | 0 | 0.5 |  |  |  | None | Not Given | By User | By User | Laura Lowes | B1041.071a-DS1-2.JPG | B1041.071a-DS2-1.JPG |  |  |  | No | 2011-08-24 Negative probability below 0.1% drift - overlap deemed acceptable. | YES
B1041.122b | B1041.122b | Non-conforming MF, weak columns and strong joints, Conc Col & Bm = 24" x 36", Beam both sides | Non-Conforming MF, column flexure, flexure-shear, or shear failure, column flexural response. Meets the following requirements: (1) Column Pu > 0.6f'cAg, (2) Column Vn < Veq Costing is on a per joint basis. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 177 | EA 1 | YES | NO | Concrete Cracking: beams, joints or possibly. Residual concrete crack widths exceed 0.06in. (1.5 mm). Column exhibits residual crack widths that require epoxy injection. | Concrete Crushing: slabs, beams or joints. Spalling of beam, column or joint cover concrete exposes longitudinal reinforcement or strength loss initiates in laboratory testing. Exhibits concrete spalling that exposes longitudinal steel or crushing of core concrete. |  |  |  | 1 | 1 |  |  |  | 0.0025 | 0.005 |  |  |  | Not Specified | Not Specified |  |  |  | 0.4 | 0.5 |  |  |  | 0.4 | 0.5 |  |  |  | NO | YES | Marginal | Average | Superior | Superior | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 8 feet either side of damaged area. Clean area adjacent to the damaged concrete. Prepare spalled concrete and adjacent cracks, as necessary, to be patched and to receive the epoxy injection. Patch concrete with grout. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems as necessary. | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 15 feet either side of damaged component. Shore damaged member(s) a minimum of one level below (more levels may be required). Remove damaged component. Place and splice (as necessary) new reinforcing steel to existing, undamaged reinforcing. Place concrete forms. Place concrete. Remove forms. Remove shores after one week. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary). |  |  |  | NO | NO |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | YES |  |  |  | 0% | 10% |  |  |  | 0 | 0.5 |  |  |  | None | Not Given | By User | By User | Laura Lowes | B1041.071a-DS1-2.JPG | B1041.071a-DS2-1.JPG |  |  |  | No | 2011-08-24 Negative probability below 0.1% drift - overlap deemed acceptable. | YES
B1041.123a | B1041.123a | Non-conforming MF, weak columns and strong joints, Conc Col & Bm = 36" x 36", Beam one side | Non-Conforming MF, column flexure, flexure-shear, or shear failure, column flexural response. Meets the following requirements: (1) Column Pu > 0.6f'cAg, (2) Column Vn < Veq Costing is on a per joint basis. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 178 | EA 1 | YES | NO | Concrete Cracking: beams, joints or possibly. Residual concrete crack widths exceed 0.06in. (1.5 mm). Column exhibits residual crack widths that require epoxy injection. | Concrete Crushing: slabs, beams or joints. Spalling of beam, column or joint cover concrete exposes longitudinal reinforcement or strength loss initiates in laboratory testing. Exhibits concrete spalling that exposes longitudinal steel or crushing of core concrete. |  |  |  | 1 | 1 |  |  |  | 0.0025 | 0.005 |  |  |  | Not Specified | Not Specified |  |  |  | 0.4 | 0.5 |  |  |  | 0.4 | 0.5 |  |  |  | NO | YES | Marginal | Average | Superior | Superior | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 8 feet either side of damaged area. Clean area adjacent to the damaged concrete. Prepare spalled concrete and adjacent cracks, as necessary, to be patched and to receive the epoxy injection. Patch concrete with grout. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems as necessary. | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 15 feet either side of damaged component. Shore damaged member(s) a minimum of one level below (more levels may be required). Remove damaged component. Place and splice (as necessary) new reinforcing steel to existing, undamaged reinforcing. Place concrete forms. Place concrete. Remove forms. Remove shores after one week. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary). |  |  |  | NO | NO |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | YES |  |  |  | 0% | 10% |  |  |  | 0 | 0.5 |  |  |  | None | Not Given | By User | By User | Laura Lowes | B1041.071a-DS1-2.JPG | B1041.071a-DS2-1.JPG |  |  |  | No | 2011-08-24 Negative probability below 0.1% drift - overlap deemed acceptable. | YES
B1041.123b | B1041.123b | Non-conforming MF, weak columns and strong joints, Conc Col & Bm = 36" x 36", Beam both sides | Non-Conforming MF, column flexure, flexure-shear, or shear failure, column flexural response. Meets the following requirements: (1) Column Pu > 0.6f'cAg, (2) Column Vn < Veq Costing is on a per joint basis. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 179 | EA 1 | YES | NO | Concrete Cracking: beams, joints or possibly. Residual concrete crack widths exceed 0.06in. (1.5 mm). Column exhibits residual crack widths that require epoxy injection. | Concrete Crushing: slabs, beams or joints. Spalling of beam, column or joint cover concrete exposes longitudinal reinforcement or strength loss initiates in laboratory testing. Exhibits concrete spalling that exposes longitudinal steel or crushing of core concrete. |  |  |  | 1 | 1 |  |  |  | 0.0025 | 0.005 |  |  |  | Not Specified | Not Specified |  |  |  | 0.4 | 0.5 |  |  |  | 0.4 | 0.5 |  |  |  | NO | YES | Marginal | Average | Superior | Superior | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 8 feet either side of damaged area. Clean area adjacent to the damaged concrete. Prepare spalled concrete and adjacent cracks, as necessary, to be patched and to receive the epoxy injection. Patch concrete with grout. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems as necessary. | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 15 feet either side of damaged component. Shore damaged member(s) a minimum of one level below (more levels may be required). Remove damaged component. Place and splice (as necessary) new reinforcing steel to existing, undamaged reinforcing. Place concrete forms. Place concrete. Remove forms. Remove shores after one week. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary). |  |  |  | NO | NO |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | YES |  |  |  | 0% | 10% |  |  |  | 0 | 0.5 |  |  |  | None | Not Given | By User | By User | Laura Lowes | B1041.071a-DS1-2.JPG | B1041.071a-DS2-1.JPG |  |  |  | No | 2011-08-24 Negative probability below 0.1% drift - overlap deemed acceptable. | YES
B1041.131a | B1041.131a | Non-conforming MF with inadequate development of reinforcing, Conc Col & Bm = 24" x 24", Beam one side | Non-Conforming MF, non-ductile failure, non-ductile response. May exhibit the following: (1) Splice detailing or length inadequate per ASCE 41-06 Table 6-7iii, (2) Beam or column reinforcing spliced at the face of joint, (3) Beam longitudinal steel discontinuous through joint per ASCE41-06 Table 6-7iii. Costing is on a per joint basis. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 180 | EA 1 | YES | NO | Damage is concentrated in beams, columns or joints depending on location of non-compliant detail. Beams, columns or joints exhibit residual crack widths > 0.06 in. No significant spalling. No fracture or buckling of reinforcing. | Damage is concentrated in beams, columns or joints depending on location of non-compliant detail. Beams, columns or joints exhibit residual crack widths > 0.06 in. Spalling of column cover concrete exposes a significant length of column longitudinal reinforcement. Crushing of column core concrete may occur. Fracture or buckling of reinf. requiring replacement may occur. |  |  |  | 1 | 1 |  |  |  | 0.015 | 0.02 |  |  |  | Not Specified | Not Specified |  |  |  | 0.4 | 0.4 |  |  |  | 0.4 | 0.4 |  |  |  | NO | YES | Marginal | Average | Superior | Superior | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 8 feet either side of damaged area. Clean area adjacent to the damaged concrete. Prepare spalled concrete and adjacent cracks, as necessary, to be patched and to receive the epoxy injection. Patch concrete with grout. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems as necessary. | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 15 feet either side of damaged component. Shore damaged member(s) a minimum of one level below (more levels may be required). Remove damaged component. Place and splice (as necessary) new reinforcing steel to existing, undamaged reinforcing. Place concrete forms. Place concrete. Remove forms. Remove shores after one week. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary). |  |  |  | NO | NO |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | YES |  |  |  | 0% | 10% |  |  |  | 0 | 0.5 |  |  |  | None | Not Given | By User | By User | Laura Lowes | none | none |  |  |  | No | None | YES
B1041.131b | B1041.131b | Non-conforming MF with inadequate development of reinforcing, Conc Col & Bm = 24" x 24", Beam both sides | Non-Conforming MF, non-ductile failure, non-ductile response. May exhibit the following: (1) Splice detailing or length inadequate per ASCE 41-06 Table 6-7iii, (2) Beam or column reinforcing spliced at the face of joint, (3) Beam longitudinal steel discontinuous through joint per ASCE41-06 Table 6-7iii. Costing is on a per joint basis. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 181 | EA 1 | YES | NO | Damage is concentrated in beams, columns or joints depending on location of non-compliant detail. Beams, columns or joints exhibit residual crack widths > 0.06 in. No significant spalling. No fracture or buckling of reinforcing. | Damage is concentrated in beams, columns or joints depending on location of non-compliant detail. Beams, columns or joints exhibit residual crack widths > 0.06 in. Spalling of column cover concrete exposes a significant length of column longitudinal reinforcement. Crushing of column core concrete may occur. Fracture or buckling of reinf. requiring replacement may occur. |  |  |  | 1 | 1 |  |  |  | 0.015 | 0.02 |  |  |  | Not Specified | Not Specified |  |  |  | 0.4 | 0.4 |  |  |  | 0.4 | 0.4 |  |  |  | NO | YES | Marginal | Average | Superior | Superior | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 8 feet either side of damaged area. Clean area adjacent to the damaged concrete. Prepare spalled concrete and adjacent cracks, as necessary, to be patched and to receive the epoxy injection. Patch concrete with grout. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems as necessary. | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 15 feet either side of damaged component. Shore damaged member(s) a minimum of one level below (more levels may be required). Remove damaged component. Place and splice (as necessary) new reinforcing steel to existing, undamaged reinforcing. Place concrete forms. Place concrete. Remove forms. Remove shores after one week. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary). |  |  |  | NO | NO |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | YES |  |  |  | 0% | 10% |  |  |  | 0 | 0.5 |  |  |  | None | Not Given | By User | By User | Laura Lowes | none | none |  |  |  | No | None | YES
B1041.132a | B1041.132a | Non-conforming MF with inadequate development of reinforcing, Conc Col & Bm = 24" x 36", Beam one side | Non-Conforming MF, non-ductile failure, non-ductile response. May exhibit the following: (1) Splice detailing or length inadequate per ASCE 41-06 Table 6-7iii, (2) Beam or column reinforcing spliced at the face of joint, (3) Beam longitudinal steel discontinuous through joint per ASCE41-06 Table 6-7iii. Costing is on a per joint basis. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 182 | EA 1 | YES | NO | Damage is concentrated in beams, columns or joints depending on location of non-compliant detail. Beams, columns or joints exhibit residual crack widths > 0.06 in. No significant spalling. No fracture or buckling of reinforcing. | Damage is concentrated in beams, columns or joints depending on location of non-compliant detail. Beams, columns or joints exhibit residual crack widths > 0.06 in. Spalling of column cover concrete exposes a significant length of column longitudinal reinforcement. Crushing of column core concrete may occur. Fracture or buckling of reinf. requiring replacement may occur. |  |  |  | 1 | 1 |  |  |  | 0.015 | 0.02 |  |  |  | Not Specified | Not Specified |  |  |  | 0.4 | 0.4 |  |  |  | 0.4 | 0.4 |  |  |  | NO | YES | Marginal | Average | Superior | Superior | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 8 feet either side of damaged area. Clean area adjacent to the damaged concrete. Prepare spalled concrete and adjacent cracks, as necessary, to be patched and to receive the epoxy injection. Patch concrete with grout. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems as necessary. | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 15 feet either side of damaged component. Shore damaged member(s) a minimum of one level below (more levels may be required). Remove damaged component. Place and splice (as necessary) new reinforcing steel to existing, undamaged reinforcing. Place concrete forms. Place concrete. Remove forms. Remove shores after one week. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary). |  |  |  | NO | NO |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | YES |  |  |  | 0% | 10% |  |  |  | 0 | 0.5 |  |  |  | None | Not Given | By User | By User | Laura Lowes | none | none |  |  |  | No | None | YES
B1041.132b | B1041.132b | Non-conforming MF with inadequate development of reinforcing, Conc Col & Bm = 24" x 36", Beam both sides | Non-Conforming MF, non-ductile failure, non-ductile response. May exhibit the following: (1) Splice detailing or length inadequate per ASCE 41-06 Table 6-7iii, (2) Beam or column reinforcing spliced at the face of joint, (3) Beam longitudinal steel discontinuous through joint per ASCE41-06 Table 6-7iii. Costing is on a per joint basis. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 183 | EA 1 | YES | NO | Damage is concentrated in beams, columns or joints depending on location of non-compliant detail. Beams, columns or joints exhibit residual crack widths > 0.06 in. No significant spalling. No fracture or buckling of reinforcing. | Damage is concentrated in beams, columns or joints depending on location of non-compliant detail. Beams, columns or joints exhibit residual crack widths > 0.06 in. Spalling of column cover concrete exposes a significant length of column longitudinal reinforcement. Crushing of column core concrete may occur. Fracture or buckling of reinf. requiring replacement may occur. |  |  |  | 1 | 1 |  |  |  | 0.015 | 0.02 |  |  |  | Not Specified | Not Specified |  |  |  | 0.4 | 0.4 |  |  |  | 0.4 | 0.4 |  |  |  | NO | YES | Marginal | Average | Superior | Superior | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 8 feet either side of damaged area. Clean area adjacent to the damaged concrete. Prepare spalled concrete and adjacent cracks, as necessary, to be patched and to receive the epoxy injection. Patch concrete with grout. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems as necessary. | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 15 feet either side of damaged component. Shore damaged member(s) a minimum of one level below (more levels may be required). Remove damaged component. Place and splice (as necessary) new reinforcing steel to existing, undamaged reinforcing. Place concrete forms. Place concrete. Remove forms. Remove shores after one week. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary). |  |  |  | NO | NO |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | YES |  |  |  | 0% | 10% |  |  |  | 0 | 0.5 |  |  |  | None | Not Given | By User | By User | Laura Lowes | none | none |  |  |  | No | None | YES
B1041.133a | B1041.133a | Non-conforming MF with inadequate development of reinforcing, Conc Col & Bm = 36" x 36", Beam one side | Non-Conforming MF, non-ductile failure, non-ductile response. May exhibit the following: (1) Splice detailing or length inadequate per ASCE 41-06 Table 6-7iii, (2) Beam or column reinforcing spliced at the face of joint, (3) Beam longitudinal steel discontinuous through joint per ASCE41-06 Table 6-7iii. Costing is on a per joint basis. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 184 | EA 1 | YES | NO | Damage is concentrated in beams, columns or joints depending on location of non-compliant detail. Beams, columns or joints exhibit residual crack widths > 0.06 in. No significant spalling. No fracture or buckling of reinforcing. | Damage is concentrated in beams, columns or joints depending on location of non-compliant detail. Beams, columns or joints exhibit residual crack widths > 0.06 in. Spalling of column cover concrete exposes a significant length of column longitudinal reinforcement. Crushing of column core concrete may occur. Fracture or buckling of reinf. requiring replacement may occur. |  |  |  | 1 | 1 |  |  |  | 0.015 | 0.02 |  |  |  | Not Specified | Not Specified |  |  |  | 0.4 | 0.4 |  |  |  | 0.4 | 0.4 |  |  |  | NO | YES | Marginal | Average | Superior | Superior | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 8 feet either side of damaged area. Clean area adjacent to the damaged concrete. Prepare spalled concrete and adjacent cracks, as necessary, to be patched and to receive the epoxy injection. Patch concrete with grout. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems as necessary. | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 15 feet either side of damaged component. Shore damaged member(s) a minimum of one level below (more levels may be required). Remove damaged component. Place and splice (as necessary) new reinforcing steel to existing, undamaged reinforcing. Place concrete forms. Place concrete. Remove forms. Remove shores after one week. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary). |  |  |  | NO | NO |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | YES |  |  |  | 0% | 10% |  |  |  | 0 | 0.5 |  |  |  | None | Not Given | By User | By User | Laura Lowes | none | none |  |  |  | No | None | YES
B1041.133b | B1041.133b | Non-conforming MF with inadequate development of reinforcing, Conc Col & Bm = 36" x 36", Beam both sides | Non-Conforming MF, non-ductile failure, non-ductile response. May exhibit the following: (1) Splice detailing or length inadequate per ASCE 41-06 Table 6-7iii, (2) Beam or column reinforcing spliced at the face of joint, (3) Beam longitudinal steel discontinuous through joint per ASCE41-06 Table 6-7iii. Costing is on a per joint basis. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 185 | EA 1 | YES | NO | Damage is concentrated in beams, columns or joints depending on location of non-compliant detail. Beams, columns or joints exhibit residual crack widths > 0.06 in. No significant spalling. No fracture or buckling of reinforcing. | Damage is concentrated in beams, columns or joints depending on location of non-compliant detail. Beams, columns or joints exhibit residual crack widths > 0.06 in. Spalling of column cover concrete exposes a significant length of column longitudinal reinforcement. Crushing of column core concrete may occur. Fracture or buckling of reinf. requiring replacement may occur. |  |  |  | 1 | 1 |  |  |  | 0.015 | 0.02 |  |  |  | Not Specified | Not Specified |  |  |  | 0.4 | 0.4 |  |  |  | 0.4 | 0.4 |  |  |  | NO | YES | Marginal | Average | Superior | Superior | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 8 feet either side of damaged area. Clean area adjacent to the damaged concrete. Prepare spalled concrete and adjacent cracks, as necessary, to be patched and to receive the epoxy injection. Patch concrete with grout. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems as necessary. | Remove furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary) 15 feet either side of damaged component. Shore damaged member(s) a minimum of one level below (more levels may be required). Remove damaged component. Place and splice (as necessary) new reinforcing steel to existing, undamaged reinforcing. Place concrete forms. Place concrete. Remove forms. Remove shores after one week. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumbing systems (as necessary). |  |  |  | NO | NO |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | YES |  |  |  | 0% | 10% |  |  |  | 0 | 0.5 |  |  |  | None | Not Given | By User | By User | Laura Lowes | none | none |  |  |  | No | None | YES
B1044.001 | B1044.001 | Rectangular low aspect ratio concrete walls 8" or less thick single curtain up to 15' high | Costing for each 144 ft^2 Wall Panel, Orthogonal web reinforcement, f'c > 2500 psi, P/(A*f'c) <= 0.2 | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 186 | SF 144 | NO | NO | Cracks with maximum widths greater than 0.04 in but less than 0.12 in. | Crushed core concrete; localized concrete cracking with widths greater than 0.12 in; buckling of vertical rebar. | Sliding of the wall resulting in large residual displacement; distributed concrete cracking with widths greater than 0.12 in; fracture of rebar. |  |  | 1 | 1 | 1 |  |  | 0.0055 | 0.0109 | 0.013 |  |  | 0.35 | 0.27 | 0.35 |  |  | 0.1 | 0.1 | 0.1 |  |  | 0.36 | 0.3 | 0.36 |  |  | NO | YES | Average | Average | Superior | Superior | Remove furnishings, ceilings and mechanical, electrical and plumping systems (as necessary) 5 feet either side of damaged area. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumping systems (as necessary). | (1) Relocate office eqpt & furniture within 6 ft. of wall, both sides. Install protective covers on floor finishes & adjacent curtain wall system. (2) Remove arch. finishes on wall, both sides. (3) Relocate MEP systems within 6 ft. of wall. (4) Prepare & inject grout 330 ft. of crack per 100 ft2 of wall. (5) Remove 15 ft2 per 100 ft2 of wall & 10 1-ft. long sections of #8 buckled vert. rebar. (6) Replace buckled rebar with new rebar, attach to exposed ends of (E) rebar with mech splices; provide 8 #4 seismic ties at 4 in. oc, ea end of wall; re-bend 16 horiz. rebar in wall around new rebar. (7) Install formwork & cast 5ksi concrete into pockets cut in step 5. (8) Strip forms, clean-up, reinstall/return office eqpt., finishes, furniture & MEP. | (1) Relocate eqpt.& furniture within 10 ft. of wall, both sides. Install protection on floor & adjacent walls. (2) Remove wall finishes, both sides. (3) Relocate MEP within 10 ft. of wall. (4) Remove damaged wall in 5-ft.lengths. (5) Install bars: a. 12#9 A706 bars in bz ea. end; mech splices to (E) ; b. #4 A706 dbl sets of seismic ties at 4 in. oc ea bz; c. #4 A706 bar at 6 in. oc, ewef; lap new vert. bars to (E) at top of wall; drill & epoxy bars into wall/fdn at 6 in. oc to match new rebar above. Anchor horiz. Bars in bz with seismic hks or lap 24 in. with (E) horiz. bars. (6) Form wall. Cast 5ksi concrete in 3-ft. lifts; with 1-in. top gap for grout day after casting. (7) Remove forms, clean-up & reinstall/return eqpt, finishes, furniture & MEP. |  |  | NO | NO | NO |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | YES | YES |  |  | 0% | 50% | 25% |  |  | 0 | 0.5 | 0.5 |  |  | Full repair description does not fully fit on sheet - consider shortening. Description will fit in PACT. | Not Given | By User | By User | Andrew Whittaker | B1044.001-DS1-1.JPG | B1044.001-DS2-1.JPG | B1044.001-DS3-1.JPG |  |  | No | 2011-08-24 Negative probability below 0.5% drift - overlap deemed acceptable. | YES
B1044.002 | B1044.002 | Rectangular low aspect ratio concrete walls 8" or less thick single curtain 16' high to 24' high | Costing for each 400 ft^2 Wall Panel, Orthogonal web reinforcement, f'c > 2500 psi, P/(A*f'c) <= 0.2 | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 187 | SF 400 | NO | NO | Cracks with maximum widths greater than 0.04 in but less than 0.12 in. | Crushed core concrete; localized concrete cracking with widths greater than 0.12 in; buckling of vertical rebar. | Sliding of the wall resulting in large residual displacement; distributed concrete cracking with widths greater than 0.12 in; fracture of rebar. |  |  | 1 | 1 | 1 |  |  | 0.0055 | 0.0109 | 0.013 |  |  | 0.35 | 0.27 | 0.35 |  |  | 0.1 | 0.1 | 0.1 |  |  | 0.36 | 0.3 | 0.36 |  |  | NO | YES | Average | Average | Superior | Superior | Remove furnishings, ceilings and mechanical, electrical and plumping systems (as necessary) 5 feet either side of damaged area. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumping systems (as necessary). | (1) Relocate office eqpt & furniture within 6 ft. of wall, both sides. Install protective covers on floor finishes & adjacent curtain wall system. (2) Remove arch. finishes on wall, both sides. (3) Relocate MEP systems within 6 ft. of wall. (4) Prepare & inject grout 330 ft. of crack per 100 ft2 of wall. (5) Remove 15 ft2 per 100 ft2 of wall & 10 1-ft. long sections of #8 buckled vert. rebar. (6) Replace buckled rebar with new rebar, attach to exposed ends of (E) rebar with mech splices; provide 8 #4 seismic ties at 4 in. oc, ea end of wall; re-bend 16 horiz. rebar in wall around new rebar. (7) Install formwork & cast 5ksi concrete into pockets cut in step 5. (8) Strip forms, clean-up, reinstall/return office eqpt., finishes, furniture & MEP. | (1) Relocate eqpt.& furniture within 10 ft. of wall, both sides. Install protection on floor & adjacent walls. (2) Remove wall finishes, both sides. (3) Relocate MEP within 10 ft. of wall. (4) Remove damaged wall in 5-ft.lengths. (5) Install bars: a. 12#9 A706 bars in bz ea. end; mech splices to (E) ; b. #4 A706 dbl sets of seismic ties at 4 in. oc ea bz; c. #4 A706 bar at 6 in. oc, ewef; lap new vert. bars to (E) at top of wall; drill & epoxy bars into wall/fdn at 6 in. oc to match new rebar above. Anchor horiz. Bars in bz with seismic hks or lap 24 in. with (E) horiz. bars. (6) Form wall. Cast 5ksi concrete in 3-ft. lifts; with 1-in. top gap for grout day after casting. (7) Remove forms, clean-up & reinstall/return eqpt, finishes, furniture & MEP. |  |  | NO | NO | NO |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | YES | YES |  |  | 0% | 50% | 25% |  |  | 0 | 0.5 | 0.5 |  |  | Full repair description does not fully fit on sheet - consider shortening. Description will fit in PACT. | Not Given | By User | By User | Andrew Whittaker | B1044.001-DS1-1.JPG | B1044.001-DS2-1.JPG | B1044.001-DS3-1.JPG |  |  | No | 2011-08-24 Negative probability below 0.5% drift - overlap deemed acceptable. | YES
B1044.003 | B1044.003 | Rectangular low aspect ratio concrete walls 8" or less thick single curtain 25' high to 40' high | Costing for each 900 ft^2 Wall Panel, Orthogonal web reinforcement, f'c > 2500 psi, P/(A*f'c) <= 0.2 | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 188 | SF 900 | NO | NO | Cracks with maximum widths greater than 0.04 in but less than 0.12 in. | Crushed core concrete; localized concrete cracking with widths greater than 0.12 in; buckling of vertical rebar. | Sliding of the wall resulting in large residual displacement; distributed concrete cracking with widths greater than 0.12 in; fracture of rebar. |  |  | 1 | 1 | 1 |  |  | 0.0055 | 0.0109 | 0.013 |  |  | 0.35 | 0.27 | 0.35 |  |  | 0.1 | 0.1 | 0.1 |  |  | 0.36 | 0.3 | 0.36 |  |  | NO | YES | Average | Average | Superior | Superior | Remove furnishings, ceilings and mechanical, electrical and plumping systems (as necessary) 5 feet either side of damaged area. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumping systems (as necessary). | (1) Relocate office eqpt & furniture within 6 ft. of wall, both sides. Install protective covers on floor finishes & adjacent curtain wall system. (2) Remove arch. finishes on wall, both sides. (3) Relocate MEP systems within 6 ft. of wall. (4) Prepare & inject grout 330 ft. of crack per 100 ft2 of wall. (5) Remove 15 ft2 per 100 ft2 of wall & 10 1-ft. long sections of #8 buckled vert. rebar. (6) Replace buckled rebar with new rebar, attach to exposed ends of (E) rebar with mech splices; provide 8 #4 seismic ties at 4 in. oc, ea end of wall; re-bend 16 horiz. rebar in wall around new rebar. (7) Install formwork & cast 5ksi concrete into pockets cut in step 5. (8) Strip forms, clean-up, reinstall/return office eqpt., finishes, furniture & MEP. | (1) Relocate eqpt.& furniture within 10 ft. of wall, both sides. Install protection on floor & adjacent walls. (2) Remove wall finishes, both sides. (3) Relocate MEP within 10 ft. of wall. (4) Remove damaged wall in 5-ft.lengths. (5) Install bars: a. 12#9 A706 bars in bz ea. end; mech splices to (E) ; b. #4 A706 dbl sets of seismic ties at 4 in. oc ea bz; c. #4 A706 bar at 6 in. oc, ewef; lap new vert. bars to (E) at top of wall; drill & epoxy bars into wall/fdn at 6 in. oc to match new rebar above. Anchor horiz. Bars in bz with seismic hks or lap 24 in. with (E) horiz. bars. (6) Form wall. Cast 5ksi concrete in 3-ft. lifts; with 1-in. top gap for grout day after casting. (7) Remove forms, clean-up & reinstall/return eqpt, finishes, furniture & MEP. |  |  | NO | NO | NO |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | YES | YES |  |  | 0% | 50% | 25% |  |  | 0 | 0.5 | 0.5 |  |  | Full repair description does not fully fit on sheet - consider shortening. Description will fit in PACT. | Not Given | By User | By User | Andrew Whittaker | B1044.001-DS1-1.JPG | B1044.001-DS2-1.JPG | B1044.001-DS3-1.JPG |  |  | No | 2011-08-24 Negative probability below 0.5% drift - overlap deemed acceptable. | YES
B1044.011 | B1044.011 | Rectangular low aspect ratio concrete walls 8"-16" double curtain; with heights of up to 15' | Costing for each 144 ft^2 Wall Panel, Orthogonal web reinforcement, f'c > 2500 psi, P/(A*f'c) <= 0.2 | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 189 | SF 144 | NO | NO | Cracks with maximum widths greater than 0.04 in but less than 0.12 in. | Crushed core concrete; localized concrete cracking with widths greater than 0.12 in; buckling of vertical rebar. | Sliding of the wall resulting in large residual displacement; distributed concrete cracking with widths greater than 0.12 in; fracture of rebar. |  |  | 1 | 1 | 1 |  |  | 0.0055 | 0.0109 | 0.013 |  |  | 0.35 | 0.27 | 0.35 |  |  | 0.1 | 0.1 | 0.1 |  |  | 0.36 | 0.3 | 0.36 |  |  | NO | YES | Average | Average | Superior | Superior | Remove furnishings, ceilings and mechanical, electrical and plumping systems (as necessary) 5 feet either side of damaged area. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumping systems (as necessary). | (1) Relocate office eqpt & furniture within 6 ft. of wall, both sides. Install protective covers on floor finishes & adjacent curtain wall system. (2) Remove arch. finishes on wall, both sides. (3) Relocate MEP systems within 6 ft. of wall. (4) Prepare & inject grout 330 ft. of crack per 100 ft2 of wall. (5) Remove 15 ft2 per 100 ft2 of wall & 10 1-ft. long sections of #8 buckled vert. rebar. (6) Replace buckled rebar with new rebar, attach to exposed ends of (E) rebar with mech splices; provide 8 #4 seismic ties at 4 in. oc, ea end of wall; re-bend 16 horiz. rebar in wall around new rebar. (7) Install formwork & cast 5ksi concrete into pockets cut in step 5. (8) Strip forms, clean-up, reinstall/return office eqpt., finishes, furniture & MEP. | (1) Relocate eqpt.& furniture within 10 ft. of wall, both sides. Install protection on floor & adjacent walls. (2) Remove wall finishes, both sides. (3) Relocate MEP within 10 ft. of wall. (4) Remove damaged wall in 5-ft.lengths. (5) Install bars: a. 12#9 A706 bars in bz ea. end; mech splices to (E) ; b. #4 A706 dbl sets of seismic ties at 4 in. oc ea bz; c. #4 A706 bar at 6 in. oc, ewef; lap new vert. bars to (E) at top of wall; drill & epoxy bars into wall/fdn at 6 in. oc to match new rebar above. Anchor horiz. Bars in bz with seismic hks or lap 24 in. with (E) horiz. bars. (6) Form wall. Cast 5ksi concrete in 3-ft. lifts; with 1-in. top gap for grout day after casting. (7) Remove forms, clean-up & reinstall/return eqpt, finishes, furniture & MEP. |  |  | NO | NO | NO |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | YES | YES |  |  | 0% | 50% | 25% |  |  | 0 | 0.5 | 0.5 |  |  | Full repair description does not fully fit on sheet - consider shortening. Description will fit in PACT. | Not Given | By User | By User | Andrew Whittaker | B1044.001-DS1-1.JPG | B1044.001-DS2-1.JPG | B1044.001-DS3-1.JPG |  |  | No | 2011-08-24 Negative probability below 0.5% drift - overlap deemed acceptable. | YES
B1044.012 | B1044.012 | Rectangular low aspect ratio concrete walls 8"-16" double curtain; with heights of 16' to 24' | Costing for each 400 ft^2 Wall Panel, Orthogonal web reinforcement, f'c > 2500 psi, P/(A*f'c) <= 0.2 | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 190 | SF 400 | NO | NO | Cracks with maximum widths greater than 0.04 in but less than 0.12 in. | Crushed core concrete; localized concrete cracking with widths greater than 0.12 in; buckling of vertical rebar. | Sliding of the wall resulting in large residual displacement; distributed concrete cracking with widths greater than 0.12 in; fracture of rebar. |  |  | 1 | 1 | 1 |  |  | 0.0055 | 0.0109 | 0.013 |  |  | 0.35 | 0.27 | 0.35 |  |  | 0.1 | 0.1 | 0.1 |  |  | 0.36 | 0.3 | 0.36 |  |  | NO | YES | Average | Average | Superior | Superior | Remove furnishings, ceilings and mechanical, electrical and plumping systems (as necessary) 5 feet either side of damaged area. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumping systems (as necessary). | (1) Relocate office eqpt & furniture within 6 ft. of wall, both sides. Install protective covers on floor finishes & adjacent curtain wall system. (2) Remove arch. finishes on wall, both sides. (3) Relocate MEP systems within 6 ft. of wall. (4) Prepare & inject grout 330 ft. of crack per 100 ft2 of wall. (5) Remove 15 ft2 per 100 ft2 of wall & 10 1-ft. long sections of #8 buckled vert. rebar. (6) Replace buckled rebar with new rebar, attach to exposed ends of (E) rebar with mech splices; provide 8 #4 seismic ties at 4 in. oc, ea end of wall; re-bend 16 horiz. rebar in wall around new rebar. (7) Install formwork & cast 5ksi concrete into pockets cut in step 5. (8) Strip forms, clean-up, reinstall/return office eqpt., finishes, furniture & MEP. | (1) Relocate eqpt.& furniture within 10 ft. of wall, both sides. Install protection on floor & adjacent walls. (2) Remove wall finishes, both sides. (3) Relocate MEP within 10 ft. of wall. (4) Remove damaged wall in 5-ft.lengths. (5) Install bars: a. 12#9 A706 bars in bz ea. end; mech splices to (E) ; b. #4 A706 dbl sets of seismic ties at 4 in. oc ea bz; c. #4 A706 bar at 6 in. oc, ewef; lap new vert. bars to (E) at top of wall; drill & epoxy bars into wall/fdn at 6 in. oc to match new rebar above. Anchor horiz. Bars in bz with seismic hks or lap 24 in. with (E) horiz. bars. (6) Form wall. Cast 5ksi concrete in 3-ft. lifts; with 1-in. top gap for grout day after casting. (7) Remove forms, clean-up & reinstall/return eqpt, finishes, furniture & MEP. |  |  | NO | NO | NO |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | YES | YES |  |  | 0% | 50% | 25% |  |  | 0 | 0.5 | 0.5 |  |  | Full repair description does not fully fit on sheet - consider shortening. Description will fit in PACT. | Not Given | By User | By User | Andrew Whittaker | B1044.001-DS1-1.JPG | B1044.001-DS2-1.JPG | B1044.001-DS3-1.JPG |  |  | No | 2011-08-24 Negative probability below 0.5% drift - overlap deemed acceptable. | YES
B1044.013 | B1044.013 | Rectangular low aspect ratio concrete walls 8"-16" double curtain; with heights of 24' to 40' | Costing for each 900 ft^2 Wall Panel, Orthogonal web reinforcement, f'c > 2500 psi, P/(A*f'c) <= 0.2 | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 191 | SF 900 | NO | NO | Cracks with maximum widths greater than 0.04 in but less than 0.12 in. | Crushed core concrete; localized concrete cracking with widths greater than 0.12 in; buckling of vertical rebar. | Sliding of the wall resulting in large residual displacement; distributed concrete cracking with widths greater than 0.12 in; fracture of rebar. |  |  | 1 | 1 | 1 |  |  | 0.0055 | 0.0109 | 0.013 |  |  | 0.35 | 0.27 | 0.35 |  |  | 0.1 | 0.1 | 0.1 |  |  | 0.36 | 0.3 | 0.36 |  |  | NO | YES | Average | Average | Superior | Superior | Remove furnishings, ceilings and mechanical, electrical and plumping systems (as necessary) 5 feet either side of damaged area. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumping systems (as necessary). | (1) Relocate office eqpt & furniture within 6 ft. of wall, both sides. Install protective covers on floor finishes & adjacent curtain wall system. (2) Remove arch. finishes on wall, both sides. (3) Relocate MEP systems within 6 ft. of wall. (4) Prepare & inject grout 330 ft. of crack per 100 ft2 of wall. (5) Remove 15 ft2 per 100 ft2 of wall & 10 1-ft. long sections of #8 buckled vert. rebar. (6) Replace buckled rebar with new rebar, attach to exposed ends of (E) rebar with mech splices; provide 8 #4 seismic ties at 4 in. oc, ea end of wall; re-bend 16 horiz. rebar in wall around new rebar. (7) Install formwork & cast 5ksi concrete into pockets cut in step 5. (8) Strip forms, clean-up, reinstall/return office eqpt., finishes, furniture & MEP. | (1) Relocate eqpt.& furniture within 10 ft. of wall, both sides. Install protection on floor & adjacent walls. (2) Remove wall finishes, both sides. (3) Relocate MEP within 10 ft. of wall. (4) Remove damaged wall in 5-ft.lengths. (5) Install bars: a. 12#9 A706 bars in bz ea. end; mech splices to (E) ; b. #4 A706 dbl sets of seismic ties at 4 in. oc ea bz; c. #4 A706 bar at 6 in. oc, ewef; lap new vert. bars to (E) at top of wall; drill & epoxy bars into wall/fdn at 6 in. oc to match new rebar above. Anchor horiz. Bars in bz with seismic hks or lap 24 in. with (E) horiz. bars. (6) Form wall. Cast 5ksi concrete in 3-ft. lifts; with 1-in. top gap for grout day after casting. (7) Remove forms, clean-up & reinstall/return eqpt, finishes, furniture & MEP. |  |  | NO | NO | NO |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | YES | YES |  |  | 0% | 50% | 25% |  |  | 0 | 0.5 | 0.5 |  |  | Full repair description does not fully fit on sheet - consider shortening. Description will fit in PACT. | Not Given | By User | By User | Andrew Whittaker | B1044.001-DS1-1.JPG | B1044.001-DS2-1.JPG | B1044.001-DS3-1.JPG |  |  | No | 2011-08-24 Negative probability below 0.5% drift - overlap deemed acceptable. | YES
B1044.021 | B1044.021 | Rectangular low aspect ratio concrete walls 18"-24" thick with double curtain and heights up to 15' | Costing for each 144 ft^2 Wall Panel, Orthogonal web reinforcement, f'c > 2500 psi, P/(A*f'c) <= 0.2 | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 192 | SF 144 | NO | NO | Cracks with maximum widths greater than 0.04 in but less than 0.12 in. | Crushed core concrete; localized concrete cracking with widths greater than 0.12 in; buckling of vertical rebar. | Sliding of the wall resulting in large residual displacement; distributed concrete cracking with widths greater than 0.12 in; fracture of rebar. |  |  | 1 | 1 | 1 |  |  | 0.0055 | 0.0109 | 0.013 |  |  | 0.35 | 0.27 | 0.35 |  |  | 0.1 | 0.1 | 0.1 |  |  | 0.36 | 0.3 | 0.36 |  |  | NO | YES | Average | Average | Superior | Superior | Remove furnishings, ceilings and mechanical, electrical and plumping systems (as necessary) 5 feet either side of damaged area. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumping systems (as necessary). | (1) Relocate office eqpt & furniture within 6 ft. of wall, both sides. Install protective covers on floor finishes & adjacent curtain wall system. (2) Remove arch. finishes on wall, both sides. (3) Relocate MEP systems within 6 ft. of wall. (4) Prepare & inject grout 330 ft. of crack per 100 ft2 of wall. (5) Remove 15 ft2 per 100 ft2 of wall & 10 1-ft. long sections of #8 buckled vert. rebar. (6) Replace buckled rebar with new rebar, attach to exposed ends of (E) rebar with mech splices; provide 8 #4 seismic ties at 4 in. oc, ea end of wall; re-bend 16 horiz. rebar in wall around new rebar. (7) Install formwork & cast 5ksi concrete into pockets cut in step 5. (8) Strip forms, clean-up, reinstall/return office eqpt., finishes, furniture & MEP. | (1) Relocate eqpt.& furniture within 10 ft. of wall, both sides. Install protection on floor & adjacent walls. (2) Remove wall finishes, both sides. (3) Relocate MEP within 10 ft. of wall. (4) Remove damaged wall in 5-ft.lengths. (5) Install bars: a. 12#9 A706 bars in bz ea. end; mech splices to (E) ; b. #4 A706 dbl sets of seismic ties at 4 in. oc ea bz; c. #4 A706 bar at 6 in. oc, ewef; lap new vert. bars to (E) at top of wall; drill & epoxy bars into wall/fdn at 6 in. oc to match new rebar above. Anchor horiz. Bars in bz with seismic hks or lap 24 in. with (E) horiz. bars. (6) Form wall. Cast 5ksi concrete in 3-ft. lifts; with 1-in. top gap for grout day after casting. (7) Remove forms, clean-up & reinstall/return eqpt, finishes, furniture & MEP. |  |  | NO | NO | NO |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | YES | YES |  |  | 0% | 50% | 25% |  |  | 0 | 0.5 | 0.5 |  |  | Full repair description does not fully fit on sheet - consider shortening. Description will fit in PACT. | Not Given | By User | By User | Andrew Whittaker | B1044.001-DS1-1.JPG | B1044.001-DS2-1.JPG | B1044.001-DS3-1.JPG |  |  | No | 2011-08-24 Negative probability below 0.5% drift - overlap deemed acceptable. | YES
B1044.022 | B1044.022 | Rectangular low aspect ratio concrete walls 18"-24" thick with double curtain and heights 16' - 24' | Costing for each 400 ft^2 Wall Panel, Orthogonal web reinforcement, f'c > 2500 psi, P/(A*f'c) <= 0.2 | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 193 | SF 400 | NO | NO | Cracks with maximum widths greater than 0.04 in but less than 0.12 in. | Crushed core concrete; localized concrete cracking with widths greater than 0.12 in; buckling of vertical rebar. | Sliding of the wall resulting in large residual displacement; distributed concrete cracking with widths greater than 0.12 in; fracture of rebar. |  |  | 1 | 1 | 1 |  |  | 0.0055 | 0.0109 | 0.013 |  |  | 0.35 | 0.27 | 0.35 |  |  | 0.1 | 0.1 | 0.1 |  |  | 0.36 | 0.3 | 0.36 |  |  | NO | YES | Average | Average | Superior | Superior | Remove furnishings, ceilings and mechanical, electrical and plumping systems (as necessary) 5 feet either side of damaged area. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumping systems (as necessary). | (1) Relocate office eqpt & furniture within 6 ft. of wall, both sides. Install protective covers on floor finishes & adjacent curtain wall system. (2) Remove arch. finishes on wall, both sides. (3) Relocate MEP systems within 6 ft. of wall. (4) Prepare & inject grout 330 ft. of crack per 100 ft2 of wall. (5) Remove 15 ft2 per 100 ft2 of wall & 10 1-ft. long sections of #8 buckled vert. rebar. (6) Replace buckled rebar with new rebar, attach to exposed ends of (E) rebar with mech splices; provide 8 #4 seismic ties at 4 in. oc, ea end of wall; re-bend 16 horiz. rebar in wall around new rebar. (7) Install formwork & cast 5ksi concrete into pockets cut in step 5. (8) Strip forms, clean-up, reinstall/return office eqpt., finishes, furniture & MEP. | (1) Relocate eqpt.& furniture within 10 ft. of wall, both sides. Install protection on floor & adjacent walls. (2) Remove wall finishes, both sides. (3) Relocate MEP within 10 ft. of wall. (4) Remove damaged wall in 5-ft.lengths. (5) Install bars: a. 12#9 A706 bars in bz ea. end; mech splices to (E) ; b. #4 A706 dbl sets of seismic ties at 4 in. oc ea bz; c. #4 A706 bar at 6 in. oc, ewef; lap new vert. bars to (E) at top of wall; drill & epoxy bars into wall/fdn at 6 in. oc to match new rebar above. Anchor horiz. Bars in bz with seismic hks or lap 24 in. with (E) horiz. bars. (6) Form wall. Cast 5ksi concrete in 3-ft. lifts; with 1-in. top gap for grout day after casting. (7) Remove forms, clean-up & reinstall/return eqpt, finishes, furniture & MEP. |  |  | NO | NO | NO |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | YES | YES |  |  | 0% | 50% | 25% |  |  | 0 | 0.5 | 0.5 |  |  | Full repair description does not fully fit on sheet - consider shortening. Description will fit in PACT. | Not Given | By User | By User | Andrew Whittaker | B1044.001-DS1-1.JPG | B1044.001-DS2-1.JPG | B1044.001-DS3-1.JPG |  |  | No | 2011-08-24 Negative probability below 0.5% drift - overlap deemed acceptable. | YES
B1044.023 | B1044.023 | Rectangular low aspect ratio concrete walls 18"-24" thick with double curtain and heights 25' - 40' | Costing for each 900 ft^2 Wall Panel, Orthogonal web reinforcement, f'c > 2500 psi, P/(A*f'c) <= 0.2 | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 194 | SF 900 | NO | NO | Cracks with maximum widths greater than 0.04 in but less than 0.12 in. | Crushed core concrete; localized concrete cracking with widths greater than 0.12 in; buckling of vertical rebar. | Sliding of the wall resulting in large residual displacement; distributed concrete cracking with widths greater than 0.12 in; fracture of rebar. |  |  | 1 | 1 | 1 |  |  | 0.0055 | 0.0109 | 0.013 |  |  | 0.35 | 0.27 | 0.35 |  |  | 0.1 | 0.1 | 0.1 |  |  | 0.36 | 0.3 | 0.36 |  |  | NO | YES | Average | Average | Superior | Superior | Remove furnishings, ceilings and mechanical, electrical and plumping systems (as necessary) 5 feet either side of damaged area. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumping systems (as necessary). | (1) Relocate office eqpt & furniture within 6 ft. of wall, both sides. Install protective covers on floor finishes & adjacent curtain wall system. (2) Remove arch. finishes on wall, both sides. (3) Relocate MEP systems within 6 ft. of wall. (4) Prepare & inject grout 330 ft. of crack per 100 ft2 of wall. (5) Remove 15 ft2 per 100 ft2 of wall & 10 1-ft. long sections of #8 buckled vert. rebar. (6) Replace buckled rebar with new rebar, attach to exposed ends of (E) rebar with mech splices; provide 8 #4 seismic ties at 4 in. oc, ea end of wall; re-bend 16 horiz. rebar in wall around new rebar. (7) Install formwork & cast 5ksi concrete into pockets cut in step 5. (8) Strip forms, clean-up, reinstall/return office eqpt., finishes, furniture & MEP. | (1) Relocate eqpt.& furniture within 10 ft. of wall, both sides. Install protection on floor & adjacent walls. (2) Remove wall finishes, both sides. (3) Relocate MEP within 10 ft. of wall. (4) Remove damaged wall in 5-ft.lengths. (5) Install bars: a. 12#9 A706 bars in bz ea. end; mech splices to (E) ; b. #4 A706 dbl sets of seismic ties at 4 in. oc ea bz; c. #4 A706 bar at 6 in. oc, ewef; lap new vert. bars to (E) at top of wall; drill & epoxy bars into wall/fdn at 6 in. oc to match new rebar above. Anchor horiz. Bars in bz with seismic hks or lap 24 in. with (E) horiz. bars. (6) Form wall. Cast 5ksi concrete in 3-ft. lifts; with 1-in. top gap for grout day after casting. (7) Remove forms, clean-up & reinstall/return eqpt, finishes, furniture & MEP. |  |  | NO | NO | NO |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | YES | YES |  |  | 0% | 50% | 25% |  |  | 0 | 0.5 | 0.5 |  |  | Full repair description does not fully fit on sheet - consider shortening. Description will fit in PACT. | Not Given | By User | By User | Andrew Whittaker | B1044.001-DS1-1.JPG | B1044.001-DS2-1.JPG | B1044.001-DS3-1.JPG |  |  | No | 2011-08-24 Negative probability below 0.5% drift - overlap deemed acceptable. | YES
B1044.031 | B1044.031 | Low-rise reinforced concrete walls with return flanges, less than 8" thick up to 15' high | Costing for each 144 ft^2 Wall Panel, Orthogonal web reinforcement, f'c > 2500 psi, P/(A*f'c) <= 0.2 | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 195 | SF 144 | NO | NO | Crushed core concrete; localized concrete cracking with widths greater than 0.12 in; buckling of vertical rebar. | Sliding of the wall resulting in large residual displacement; distributed concrete cracking with widths greater than 0.12 in; fracture of rebar. |  |  |  | 1 | 1 |  |  |  | 0.0076 | 0.0134 |  |  |  | 0.33 | 0.45 |  |  |  | 0.1 | 0.1 |  |  |  | 0.35 | 0.45 |  |  |  | NO | YES | Average | Average | Superior | Superior | Remove furnishings, ceilings and mechanical, electrical and plumping systems (as necessary) 5 feet either side of damaged area. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumping systems (as necessary). | (1) Relocate eqpt.& furniture within 10 ft. of wall, both sides. Install protection on floor & adjacent walls. (2) Remove wall finishes, both sides. (3) Relocate MEP within 10 ft. of wall. (4) Remove damaged wall in 5-ft.lengths. (5) Install bars: a. 12#9 A706 bars in bz ea. end; mech splices to (E) ; b. #4 A706 dbl sets of seismic ties at 4 in. oc ea bz; c. #4 A706 bar at 6 in. oc, ewef; lap new vert. bars to (E) at top of wall; drill & epoxy bars into wall/fdn at 6 in. oc to match new rebar above. Anchor horiz. Bars in bz with seismic hks or lap 24 in. with (E) horiz. bars. (6) Form wall. Cast 5ksi concrete in 3-ft. lifts; with 1-in. top gap for grout day after casting. (7) Remove forms, clean-up & reinstall/return eqpt, finishes, furniture & MEP. |  |  |  | NO | NO |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | YES | YES |  |  |  | 50% | 25% |  |  |  | 0.5 | 0.5 |  |  |  | Full repair description does not fully fit on sheet - consider shortening. Description will fit in PACT. | Not Given | By User | By User | Andrew Whittaker | B1044.031-DS1-1.JPG | B1044.031-DS2-1.JPG |  |  |  | No | 2011-08-24 Negative probability below 0.5% drift - overlap deemed acceptable. | YES
B1044.032 | B1044.032 | Low-rise reinforced concrete walls with return flanges, less than 8" thick, 16' to 24' high | Costing for each 400 ft^2 Wall Panel, Orthogonal web reinforcement, f'c > 2500 psi, P/(A*f'c) <= 0.2 | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 196 | SF 400 | NO | NO | Crushed core concrete; localized concrete cracking with widths greater than 0.12 in; buckling of vertical rebar. | Sliding of the wall resulting in large residual displacement; distributed concrete cracking with widths greater than 0.12 in; fracture of rebar. |  |  |  | 1 | 1 |  |  |  | 0.0076 | 0.0134 |  |  |  | 0.33 | 0.45 |  |  |  | 0.1 | 0.1 |  |  |  | 0.35 | 0.45 |  |  |  | NO | YES | Average | Average | Superior | Superior | Remove furnishings, ceilings and mechanical, electrical and plumping systems (as necessary) 5 feet either side of damaged area. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumping systems (as necessary). | (1) Relocate eqpt.& furniture within 10 ft. of wall, both sides. Install protection on floor & adjacent walls. (2) Remove wall finishes, both sides. (3) Relocate MEP within 10 ft. of wall. (4) Remove damaged wall in 5-ft.lengths. (5) Install bars: a. 12#9 A706 bars in bz ea. end; mech splices to (E) ; b. #4 A706 dbl sets of seismic ties at 4 in. oc ea bz; c. #4 A706 bar at 6 in. oc, ewef; lap new vert. bars to (E) at top of wall; drill & epoxy bars into wall/fdn at 6 in. oc to match new rebar above. Anchor horiz. Bars in bz with seismic hks or lap 24 in. with (E) horiz. bars. (6) Form wall. Cast 5ksi concrete in 3-ft. lifts; with 1-in. top gap for grout day after casting. (7) Remove forms, clean-up & reinstall/return eqpt, finishes, furniture & MEP. |  |  |  | NO | NO |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | YES | YES |  |  |  | 50% | 25% |  |  |  | 0.5 | 0.5 |  |  |  | Full repair description does not fully fit on sheet - consider shortening. Description will fit in PACT. | Not Given | By User | By User | Andrew Whittaker | B1044.031-DS1-1.JPG | B1044.031-DS2-1.JPG |  |  |  | No | 2011-08-24 Negative probability below 0.5% drift - overlap deemed acceptable. | YES
B1044.033 | B1044.033 | Low-rise reinforced concrete walls with return flanges, less than 8" thick, 25' to 40' high | Costing for each 900 ft^2 Wall Panel, Orthogonal web reinforcement, f'c > 2500 psi, P/(A*f'c) <= 0.2 | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 197 | SF 900 | NO | NO | Crushed core concrete; localized concrete cracking with widths greater than 0.12 in; buckling of vertical rebar. | Sliding of the wall resulting in large residual displacement; distributed concrete cracking with widths greater than 0.12 in; fracture of rebar. |  |  |  | 1 | 1 |  |  |  | 0.0076 | 0.0134 |  |  |  | 0.33 | 0.45 |  |  |  | 0.1 | 0.1 |  |  |  | 0.35 | 0.45 |  |  |  | NO | YES | Average | Average | Superior | Superior | Remove furnishings, ceilings and mechanical, electrical and plumping systems (as necessary) 5 feet either side of damaged area. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumping systems (as necessary). | (1) Relocate eqpt.& furniture within 10 ft. of wall, both sides. Install protection on floor & adjacent walls. (2) Remove wall finishes, both sides. (3) Relocate MEP within 10 ft. of wall. (4) Remove damaged wall in 5-ft.lengths. (5) Install bars: a. 12#9 A706 bars in bz ea. end; mech splices to (E) ; b. #4 A706 dbl sets of seismic ties at 4 in. oc ea bz; c. #4 A706 bar at 6 in. oc, ewef; lap new vert. bars to (E) at top of wall; drill & epoxy bars into wall/fdn at 6 in. oc to match new rebar above. Anchor horiz. Bars in bz with seismic hks or lap 24 in. with (E) horiz. bars. (6) Form wall. Cast 5ksi concrete in 3-ft. lifts; with 1-in. top gap for grout day after casting. (7) Remove forms, clean-up & reinstall/return eqpt, finishes, furniture & MEP. |  |  |  | NO | NO |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | YES | YES |  |  |  | 50% | 25% |  |  |  | 0.5 | 0.5 |  |  |  | Full repair description does not fully fit on sheet - consider shortening. Description will fit in PACT. | Not Given | By User | By User | Andrew Whittaker | B1044.031-DS1-1.JPG | B1044.031-DS2-1.JPG |  |  |  | No | 2011-08-24 Negative probability below 0.5% drift - overlap deemed acceptable. | YES
B1044.041 | B1044.041 | Low-rise reinforced concrete walls with return flanges, 8" to 16" thick up to 15' high | Costing for each 144 ft^2 Wall Panel, Orthogonal web reinforcement, f'c > 2500 psi, P/(A*f'c) <= 0.2 | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 198 | SF 144 | NO | NO | Crushed core concrete; localized concrete cracking with widths greater than 0.12 in; buckling of vertical rebar. | Sliding of the wall resulting in large residual displacement; distributed concrete cracking with widths greater than 0.12 in; fracture of rebar. |  |  |  | 1 | 1 |  |  |  | 0.0076 | 0.0134 |  |  |  | 0.33 | 0.45 |  |  |  | 0.1 | 0.1 |  |  |  | 0.35 | 0.45 |  |  |  | NO | YES | Average | Average | Superior | Superior | Remove furnishings, ceilings and mechanical, electrical and plumping systems (as necessary) 5 feet either side of damaged area. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumping systems (as necessary). | (1) Relocate eqpt.& furniture within 10 ft. of wall, both sides. Install protection on floor & adjacent walls. (2) Remove wall finishes, both sides. (3) Relocate MEP within 10 ft. of wall. (4) Remove damaged wall in 5-ft.lengths. (5) Install bars: a. 12#9 A706 bars in bz ea. end; mech splices to (E) ; b. #4 A706 dbl sets of seismic ties at 4 in. oc ea bz; c. #4 A706 bar at 6 in. oc, ewef; lap new vert. bars to (E) at top of wall; drill & epoxy bars into wall/fdn at 6 in. oc to match new rebar above. Anchor horiz. Bars in bz with seismic hks or lap 24 in. with (E) horiz. bars. (6) Form wall. Cast 5ksi concrete in 3-ft. lifts; with 1-in. top gap for grout day after casting. (7) Remove forms, clean-up & reinstall/return eqpt, finishes, furniture & MEP. |  |  |  | NO | NO |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | YES | YES |  |  |  | 50% | 25% |  |  |  | 0.5 | 0.5 |  |  |  | Full repair description does not fully fit on sheet - consider shortening. Description will fit in PACT. | Not Given | By User | By User | Andrew Whittaker | B1044.031-DS1-1.JPG | B1044.031-DS2-1.JPG |  |  |  | No | 2011-08-24 Negative probability below 0.5% drift - overlap deemed acceptable. | YES
B1044.042 | B1044.042 | Low-rise reinforced concrete walls with return flanges, 8" to 16" thick, 16' to 24' high | Costing for each 400 ft^2 Wall Panel, Orthogonal web reinforcement, f'c > 2500 psi, P/(A*f'c) <= 0.2 | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 199 | SF 400 | NO | NO | Crushed core concrete; localized concrete cracking with widths greater than 0.12 in; buckling of vertical rebar. | Sliding of the wall resulting in large residual displacement; distributed concrete cracking with widths greater than 0.12 in; fracture of rebar. |  |  |  | 1 | 1 |  |  |  | 0.0076 | 0.0134 |  |  |  | 0.33 | 0.45 |  |  |  | 0.1 | 0.1 |  |  |  | 0.35 | 0.45 |  |  |  | NO | YES | Average | Average | Superior | Superior | Remove furnishings, ceilings and mechanical, electrical and plumping systems (as necessary) 5 feet either side of damaged area. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumping systems (as necessary). | (1) Relocate eqpt.& furniture within 10 ft. of wall, both sides. Install protection on floor & adjacent walls. (2) Remove wall finishes, both sides. (3) Relocate MEP within 10 ft. of wall. (4) Remove damaged wall in 5-ft.lengths. (5) Install bars: a. 12#9 A706 bars in bz ea. end; mech splices to (E) ; b. #4 A706 dbl sets of seismic ties at 4 in. oc ea bz; c. #4 A706 bar at 6 in. oc, ewef; lap new vert. bars to (E) at top of wall; drill & epoxy bars into wall/fdn at 6 in. oc to match new rebar above. Anchor horiz. Bars in bz with seismic hks or lap 24 in. with (E) horiz. bars. (6) Form wall. Cast 5ksi concrete in 3-ft. lifts; with 1-in. top gap for grout day after casting. (7) Remove forms, clean-up & reinstall/return eqpt, finishes, furniture & MEP. |  |  |  | NO | NO |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | YES | YES |  |  |  | 50% | 25% |  |  |  | 0.5 | 0.5 |  |  |  | Full repair description does not fully fit on sheet - consider shortening. Description will fit in PACT. | Not Given | By User | By User | Andrew Whittaker | B1044.031-DS1-1.JPG | B1044.031-DS2-1.JPG |  |  |  | No | 2011-08-24 Negative probability below 0.5% drift - overlap deemed acceptable. | YES
B1044.043 | B1044.043 | Low-rise reinforced concrete walls with return flanges, 8" to 16" thick, 25' to 40' high | Costing for each 900 ft^2 Wall Panel, Orthogonal web reinforcement, f'c > 2500 psi, P/(A*f'c) <= 0.2 | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 200 | SF 900 | NO | NO | Crushed core concrete; localized concrete cracking with widths greater than 0.12 in; buckling of vertical rebar. | Sliding of the wall resulting in large residual displacement; distributed concrete cracking with widths greater than 0.12 in; fracture of rebar. |  |  |  | 1 | 1 |  |  |  | 0.0076 | 0.0134 |  |  |  | 0.33 | 0.45 |  |  |  | 0.1 | 0.1 |  |  |  | 0.35 | 0.45 |  |  |  | NO | YES | Average | Average | Superior | Superior | Remove furnishings, ceilings and mechanical, electrical and plumping systems (as necessary) 5 feet either side of damaged area. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumping systems (as necessary). | (1) Relocate eqpt.& furniture within 10 ft. of wall, both sides. Install protection on floor & adjacent walls. (2) Remove wall finishes, both sides. (3) Relocate MEP within 10 ft. of wall. (4) Remove damaged wall in 5-ft.lengths. (5) Install bars: a. 12#9 A706 bars in bz ea. end; mech splices to (E) ; b. #4 A706 dbl sets of seismic ties at 4 in. oc ea bz; c. #4 A706 bar at 6 in. oc, ewef; lap new vert. bars to (E) at top of wall; drill & epoxy bars into wall/fdn at 6 in. oc to match new rebar above. Anchor horiz. Bars in bz with seismic hks or lap 24 in. with (E) horiz. bars. (6) Form wall. Cast 5ksi concrete in 3-ft. lifts; with 1-in. top gap for grout day after casting. (7) Remove forms, clean-up & reinstall/return eqpt, finishes, furniture & MEP. |  |  |  | NO | NO |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | YES | YES |  |  |  | 50% | 25% |  |  |  | 0.5 | 0.5 |  |  |  | Full repair description does not fully fit on sheet - consider shortening. Description will fit in PACT. | Not Given | By User | By User | Andrew Whittaker | B1044.031-DS1-1.JPG | B1044.031-DS2-1.JPG |  |  |  | No | 2011-08-24 Negative probability below 0.5% drift - overlap deemed acceptable. | YES
B1044.051 | B1044.051 | Low-rise reinforced concrete walls with return flanges, 17" to 24" thick" up to 15' high | Costing for each 144 ft^2 Wall Panel, Orthogonal web reinforcement, f'c > 2500 psi, P/(A*f'c) <= 0.2 | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 201 | SF 144 | NO | NO | Crushed core concrete; localized concrete cracking with widths greater than 0.12 in; buckling of vertical rebar. | Sliding of the wall resulting in large residual displacement; distributed concrete cracking with widths greater than 0.12 in; fracture of rebar. |  |  |  | 1 | 1 |  |  |  | 0.0076 | 0.0134 |  |  |  | 0.33 | 0.45 |  |  |  | 0.1 | 0.1 |  |  |  | 0.35 | 0.45 |  |  |  | NO | YES | Average | Average | Superior | Superior | Remove furnishings, ceilings and mechanical, electrical and plumping systems (as necessary) 5 feet either side of damaged area. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumping systems (as necessary). | (1) Relocate eqpt.& furniture within 10 ft. of wall, both sides. Install protection on floor & adjacent walls. (2) Remove wall finishes, both sides. (3) Relocate MEP within 10 ft. of wall. (4) Remove damaged wall in 5-ft.lengths. (5) Install bars: a. 12#9 A706 bars in bz ea. end; mech splices to (E) ; b. #4 A706 dbl sets of seismic ties at 4 in. oc ea bz; c. #4 A706 bar at 6 in. oc, ewef; lap new vert. bars to (E) at top of wall; drill & epoxy bars into wall/fdn at 6 in. oc to match new rebar above. Anchor horiz. Bars in bz with seismic hks or lap 24 in. with (E) horiz. bars. (6) Form wall. Cast 5ksi concrete in 3-ft. lifts; with 1-in. top gap for grout day after casting. (7) Remove forms, clean-up & reinstall/return eqpt, finishes, furniture & MEP. |  |  |  | NO | NO |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | YES | YES |  |  |  | 50% | 25% |  |  |  | 0.5 | 0.5 |  |  |  | Full repair description does not fully fit on sheet - consider shortening. Description will fit in PACT. | Not Given | By User | By User | Andrew Whittaker | B1044.031-DS1-1.JPG | B1044.031-DS2-1.JPG |  |  |  | No | 2011-08-24 Negative probability below 0.5% drift - overlap deemed acceptable. | YES
B1044.052 | B1044.052 | Low-rise reinforced concrete walls with return flanges, 17" to 24" thick, 16' to 24' high | Costing for each 400 ft^2 Wall Panel, Orthogonal web reinforcement, f'c > 2500 psi, P/(A*f'c) <= 0.2 | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 202 | SF 400 | NO | NO | Crushed core concrete; localized concrete cracking with widths greater than 0.12 in; buckling of vertical rebar. | Sliding of the wall resulting in large residual displacement; distributed concrete cracking with widths greater than 0.12 in; fracture of rebar. |  |  |  | 1 | 1 |  |  |  | 0.0076 | 0.0134 |  |  |  | 0.33 | 0.45 |  |  |  | 0.1 | 0.1 |  |  |  | 0.35 | 0.45 |  |  |  | NO | YES | Average | Average | Superior | Superior | Remove furnishings, ceilings and mechanical, electrical and plumping systems (as necessary) 5 feet either side of damaged area. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumping systems (as necessary). | (1) Relocate eqpt.& furniture within 10 ft. of wall, both sides. Install protection on floor & adjacent walls. (2) Remove wall finishes, both sides. (3) Relocate MEP within 10 ft. of wall. (4) Remove damaged wall in 5-ft.lengths. (5) Install bars: a. 12#9 A706 bars in bz ea. end; mech splices to (E) ; b. #4 A706 dbl sets of seismic ties at 4 in. oc ea bz; c. #4 A706 bar at 6 in. oc, ewef; lap new vert. bars to (E) at top of wall; drill & epoxy bars into wall/fdn at 6 in. oc to match new rebar above. Anchor horiz. Bars in bz with seismic hks or lap 24 in. with (E) horiz. bars. (6) Form wall. Cast 5ksi concrete in 3-ft. lifts; with 1-in. top gap for grout day after casting. (7) Remove forms, clean-up & reinstall/return eqpt, finishes, furniture & MEP. |  |  |  | NO | NO |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | YES | YES |  |  |  | 50% | 25% |  |  |  | 0.5 | 0.5 |  |  |  | Full repair description does not fully fit on sheet - consider shortening. Description will fit in PACT. | Not Given | By User | By User | Andrew Whittaker | B1044.031-DS1-1.JPG | B1044.031-DS2-1.JPG |  |  |  | No | 2011-08-24 Negative probability below 0.5% drift - overlap deemed acceptable. | YES
B1044.053 | B1044.053 | Low-rise reinforced concrete walls with return flanges, 17" to 24" thick, 25' to 40' high | Costing for each 900 ft^2 Wall Panel, Orthogonal web reinforcement, f'c > 2500 psi, P/(A*f'c) <= 0.2 | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 203 | SF 900 | NO | NO | Crushed core concrete; localized concrete cracking with widths greater than 0.12 in; buckling of vertical rebar. | Sliding of the wall resulting in large residual displacement; distributed concrete cracking with widths greater than 0.12 in; fracture of rebar. |  |  |  | 1 | 1 |  |  |  | 0.0076 | 0.0134 |  |  |  | 0.33 | 0.45 |  |  |  | 0.1 | 0.1 |  |  |  | 0.35 | 0.45 |  |  |  | NO | YES | Average | Average | Superior | Superior | Remove furnishings, ceilings and mechanical, electrical and plumping systems (as necessary) 5 feet either side of damaged area. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumping systems (as necessary). | (1) Relocate eqpt.& furniture within 10 ft. of wall, both sides. Install protection on floor & adjacent walls. (2) Remove wall finishes, both sides. (3) Relocate MEP within 10 ft. of wall. (4) Remove damaged wall in 5-ft.lengths. (5) Install bars: a. 12#9 A706 bars in bz ea. end; mech splices to (E) ; b. #4 A706 dbl sets of seismic ties at 4 in. oc ea bz; c. #4 A706 bar at 6 in. oc, ewef; lap new vert. bars to (E) at top of wall; drill & epoxy bars into wall/fdn at 6 in. oc to match new rebar above. Anchor horiz. Bars in bz with seismic hks or lap 24 in. with (E) horiz. bars. (6) Form wall. Cast 5ksi concrete in 3-ft. lifts; with 1-in. top gap for grout day after casting. (7) Remove forms, clean-up & reinstall/return eqpt, finishes, furniture & MEP. |  |  |  | NO | NO |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | YES | YES |  |  |  | 50% | 25% |  |  |  | 0.5 | 0.5 |  |  |  | Full repair description does not fully fit on sheet - consider shortening. Description will fit in PACT. | Not Given | By User | By User | Andrew Whittaker | B1044.031-DS1-1.JPG | B1044.031-DS2-1.JPG |  |  |  | No | 2011-08-24 Negative probability below 0.5% drift - overlap deemed acceptable. | YES
B1044.061 | B1044.061 | Low rise reinforced concrete walls with boundary columns, less than 8" thick, height <15' | Costing for each 144 ft^2 Wall Panel, Orthogonal web reinforcement, f'c > 2500 psi, P/(A*f'c) <= 0.2 | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 204 | SF 144 | NO | NO | Crushed core concrete; localized concrete cracking with widths greater than 0.12 in; buckling of vertical rebar. | Sliding of the wall resulting in large residual displacement; distributed concrete cracking with widths greater than 0.12 in; fracture of rebar. |  |  |  | 1 | 1 |  |  |  | 0.0033 | 0.0087 |  |  |  | 0.33 | 0.18 |  |  |  | 0.1 | 0.1 |  |  |  | 0.35 | 0.2 |  |  |  | NO | YES | Average | Average | Superior | Superior | Remove furnishings, ceilings and mechanical, electrical and plumping systems (as necessary) 5 feet either side of damaged area. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumping systems (as necessary). | (1) Relocate eqpt.& furniture within 10 ft. of wall, both sides. Install protection on floor & adjacent walls. (2) Remove wall finishes, both sides. (3) Relocate MEP within 10 ft. of wall. (4) Remove damaged wall in 5-ft.lengths. (5) Install bars: a. 12#9 A706 bars in bz ea. end; mech splices to (E) ; b. #4 A706 dbl sets of seismic ties at 4 in. oc ea bz; c. #4 A706 bar at 6 in. oc, ewef; lap new vert. bars to (E) at top of wall; drill & epoxy bars into wall/fdn at 6 in. oc to match new rebar above. Anchor horiz. Bars in bz with seismic hks or lap 24 in. with (E) horiz. bars. (6) Form wall. Cast 5ksi concrete in 3-ft. lifts; with 1-in. top gap for grout day after casting. (7) Remove forms, clean-up & reinstall/return eqpt, finishes, furniture & MEP. |  |  |  | NO | NO |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | YES | YES |  |  |  | 50% | 25% |  |  |  | 0.5 | 0.5 |  |  |  | Full repair description does not fully fit on sheet - consider shortening. Description will fit in PACT. | Not Given | By User | By User | Andrew Whittaker | B1044.061-DS1-1.JPG | B1044.061-DS2-1.JPG |  |  |  | No | None | YES
B1044.062 | B1044.062 | Low rise reinforced concrete walls with boundary columns, less than 8" thick, height between 16'-24' | Costing for each 400 ft^2 Wall Panel, Orthogonal web reinforcement, f'c > 2500 psi, P/(A*f'c) <= 0.2 | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 205 | SF 400 | NO | NO | Crushed core concrete; localized concrete cracking with widths greater than 0.12 in; buckling of vertical rebar. | Sliding of the wall resulting in large residual displacement; distributed concrete cracking with widths greater than 0.12 in; fracture of rebar. |  |  |  | 1 | 1 |  |  |  | 0.0033 | 0.0087 |  |  |  | 0.33 | 0.18 |  |  |  | 0.1 | 0.1 |  |  |  | 0.35 | 0.2 |  |  |  | NO | YES | Average | Average | Superior | Superior | Remove furnishings, ceilings and mechanical, electrical and plumping systems (as necessary) 5 feet either side of damaged area. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumping systems (as necessary). | (1) Relocate eqpt.& furniture within 10 ft. of wall, both sides. Install protection on floor & adjacent walls. (2) Remove wall finishes, both sides. (3) Relocate MEP within 10 ft. of wall. (4) Remove damaged wall in 5-ft.lengths. (5) Install bars: a. 12#9 A706 bars in bz ea. end; mech splices to (E) ; b. #4 A706 dbl sets of seismic ties at 4 in. oc ea bz; c. #4 A706 bar at 6 in. oc, ewef; lap new vert. bars to (E) at top of wall; drill & epoxy bars into wall/fdn at 6 in. oc to match new rebar above. Anchor horiz. Bars in bz with seismic hks or lap 24 in. with (E) horiz. bars. (6) Form wall. Cast 5ksi concrete in 3-ft. lifts; with 1-in. top gap for grout day after casting. (7) Remove forms, clean-up & reinstall/return eqpt, finishes, furniture & MEP. |  |  |  | NO | NO |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | YES | YES |  |  |  | 50% | 25% |  |  |  | 0.5 | 0.5 |  |  |  | Full repair description does not fully fit on sheet - consider shortening. Description will fit in PACT. | Not Given | By User | By User | Andrew Whittaker | B1044.061-DS1-1.JPG | B1044.061-DS2-1.JPG |  |  |  | No | None | YES
B1044.063 | B1044.063 | Low rise reinforced concrete walls with boundary columns, less than 8" thick, height between 24'-40' | Costing for each 900 ft^2 Wall Panel, Orthogonal web reinforcement, f'c > 2500 psi, P/(A*f'c) <= 0.2 | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 206 | SF 900 | NO | NO | Crushed core concrete; localized concrete cracking with widths greater than 0.12 in; buckling of vertical rebar. | Sliding of the wall resulting in large residual displacement; distributed concrete cracking with widths greater than 0.12 in; fracture of rebar. |  |  |  | 1 | 1 |  |  |  | 0.0033 | 0.0087 |  |  |  | 0.33 | 0.18 |  |  |  | 0.1 | 0.1 |  |  |  | 0.35 | 0.2 |  |  |  | NO | YES | Average | Average | Superior | Superior | Remove furnishings, ceilings and mechanical, electrical and plumping systems (as necessary) 5 feet either side of damaged area. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumping systems (as necessary). | (1) Relocate eqpt.& furniture within 10 ft. of wall, both sides. Install protection on floor & adjacent walls. (2) Remove wall finishes, both sides. (3) Relocate MEP within 10 ft. of wall. (4) Remove damaged wall in 5-ft.lengths. (5) Install bars: a. 12#9 A706 bars in bz ea. end; mech splices to (E) ; b. #4 A706 dbl sets of seismic ties at 4 in. oc ea bz; c. #4 A706 bar at 6 in. oc, ewef; lap new vert. bars to (E) at top of wall; drill & epoxy bars into wall/fdn at 6 in. oc to match new rebar above. Anchor horiz. Bars in bz with seismic hks or lap 24 in. with (E) horiz. bars. (6) Form wall. Cast 5ksi concrete in 3-ft. lifts; with 1-in. top gap for grout day after casting. (7) Remove forms, clean-up & reinstall/return eqpt, finishes, furniture & MEP. |  |  |  | NO | NO |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | YES | YES |  |  |  | 50% | 25% |  |  |  | 0.5 | 0.5 |  |  |  | Full repair description does not fully fit on sheet - consider shortening. Description will fit in PACT. | Not Given | By User | By User | Andrew Whittaker | B1044.061-DS1-1.JPG | B1044.061-DS2-1.JPG |  |  |  | No | None | YES
B1044.071 | B1044.071 | Low rise reinforced concrete walls with boundary columns, 8" to 16" thick, height <15' | Costing for each 144 ft^2 Wall Panel, Orthogonal web reinforcement, f'c > 2500 psi, P/(A*f'c) <= 0.2 | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 207 | SF 144 | NO | NO | Crushed core concrete; localized concrete cracking with widths greater than 0.12 in; buckling of vertical rebar. | Sliding of the wall resulting in large residual displacement; distributed concrete cracking with widths greater than 0.12 in; fracture of rebar. |  |  |  | 1 | 1 |  |  |  | 0.0033 | 0.0087 |  |  |  | 0.33 | 0.18 |  |  |  | 0.1 | 0.1 |  |  |  | 0.35 | 0.2 |  |  |  | NO | YES | Average | Average | Superior | Superior | Remove furnishings, ceilings and mechanical, electrical and plumping systems (as necessary) 5 feet either side of damaged area. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumping systems (as necessary). | (1) Relocate eqpt.& furniture within 10 ft. of wall, both sides. Install protection on floor & adjacent walls. (2) Remove wall finishes, both sides. (3) Relocate MEP within 10 ft. of wall. (4) Remove damaged wall in 5-ft.lengths. (5) Install bars: a. 12#9 A706 bars in bz ea. end; mech splices to (E) ; b. #4 A706 dbl sets of seismic ties at 4 in. oc ea bz; c. #4 A706 bar at 6 in. oc, ewef; lap new vert. bars to (E) at top of wall; drill & epoxy bars into wall/fdn at 6 in. oc to match new rebar above. Anchor horiz. Bars in bz with seismic hks or lap 24 in. with (E) horiz. bars. (6) Form wall. Cast 5ksi concrete in 3-ft. lifts; with 1-in. top gap for grout day after casting. (7) Remove forms, clean-up & reinstall/return eqpt, finishes, furniture & MEP. |  |  |  | NO | NO |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | YES | YES |  |  |  | 50% | 25% |  |  |  | 0.5 | 0.5 |  |  |  | Full repair description does not fully fit on sheet - consider shortening. Description will fit in PACT. | Not Given | By User | By User | Andrew Whittaker | B1044.061-DS1-1.JPG | B1044.061-DS2-1.JPG |  |  |  | No | None | YES
B1044.072 | B1044.072 | Low rise reinforced concrete walls with boundary columns, 8" to 16" thick, height between 16'-24' | Costing for each 400 ft^2 Wall Panel, Orthogonal web reinforcement, f'c > 2500 psi, P/(A*f'c) <= 0.2 | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 208 | SF 400 | NO | NO | Crushed core concrete; localized concrete cracking with widths greater than 0.12 in; buckling of vertical rebar. | Sliding of the wall resulting in large residual displacement; distributed concrete cracking with widths greater than 0.12 in; fracture of rebar. |  |  |  | 1 | 1 |  |  |  | 0.0033 | 0.0087 |  |  |  | 0.33 | 0.18 |  |  |  | 0.1 | 0.1 |  |  |  | 0.35 | 0.2 |  |  |  | NO | YES | Average | Average | Superior | Superior | Remove furnishings, ceilings and mechanical, electrical and plumping systems (as necessary) 5 feet either side of damaged area. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumping systems (as necessary). | (1) Relocate eqpt.& furniture within 10 ft. of wall, both sides. Install protection on floor & adjacent walls. (2) Remove wall finishes, both sides. (3) Relocate MEP within 10 ft. of wall. (4) Remove damaged wall in 5-ft.lengths. (5) Install bars: a. 12#9 A706 bars in bz ea. end; mech splices to (E) ; b. #4 A706 dbl sets of seismic ties at 4 in. oc ea bz; c. #4 A706 bar at 6 in. oc, ewef; lap new vert. bars to (E) at top of wall; drill & epoxy bars into wall/fdn at 6 in. oc to match new rebar above. Anchor horiz. Bars in bz with seismic hks or lap 24 in. with (E) horiz. bars. (6) Form wall. Cast 5ksi concrete in 3-ft. lifts; with 1-in. top gap for grout day after casting. (7) Remove forms, clean-up & reinstall/return eqpt, finishes, furniture & MEP. |  |  |  | NO | NO |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | YES | YES |  |  |  | 50% | 25% |  |  |  | 0.5 | 0.5 |  |  |  | Full repair description does not fully fit on sheet - consider shortening. Description will fit in PACT. | Not Given | By User | By User | Andrew Whittaker | B1044.061-DS1-1.JPG | B1044.061-DS2-1.JPG |  |  |  | No | None | YES
B1044.073 | B1044.073 | Low rise reinforced concrete walls with boundary columns, 8" to 16" thick, height between 24'-40' | Costing for each 900 ft^2 Wall Panel, Orthogonal web reinforcement, f'c > 2500 psi, P/(A*f'c) <= 0.2 | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 209 | SF 900 | NO | NO | Crushed core concrete; localized concrete cracking with widths greater than 0.12 in; buckling of vertical rebar. | Sliding of the wall resulting in large residual displacement; distributed concrete cracking with widths greater than 0.12 in; fracture of rebar. |  |  |  | 1 | 1 |  |  |  | 0.0033 | 0.0087 |  |  |  | 0.33 | 0.18 |  |  |  | 0.1 | 0.1 |  |  |  | 0.35 | 0.2 |  |  |  | NO | YES | Average | Average | Superior | Superior | Remove furnishings, ceilings and mechanical, electrical and plumping systems (as necessary) 5 feet either side of damaged area. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumping systems (as necessary). | (1) Relocate eqpt.& furniture within 10 ft. of wall, both sides. Install protection on floor & adjacent walls. (2) Remove wall finishes, both sides. (3) Relocate MEP within 10 ft. of wall. (4) Remove damaged wall in 5-ft.lengths. (5) Install bars: a. 12#9 A706 bars in bz ea. end; mech splices to (E) ; b. #4 A706 dbl sets of seismic ties at 4 in. oc ea bz; c. #4 A706 bar at 6 in. oc, ewef; lap new vert. bars to (E) at top of wall; drill & epoxy bars into wall/fdn at 6 in. oc to match new rebar above. Anchor horiz. Bars in bz with seismic hks or lap 24 in. with (E) horiz. bars. (6) Form wall. Cast 5ksi concrete in 3-ft. lifts; with 1-in. top gap for grout day after casting. (7) Remove forms, clean-up & reinstall/return eqpt, finishes, furniture & MEP. |  |  |  | NO | NO |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | YES | YES |  |  |  | 50% | 25% |  |  |  | 0.5 | 0.5 |  |  |  | Full repair description does not fully fit on sheet - consider shortening. Description will fit in PACT. | Not Given | By User | By User | Andrew Whittaker | B1044.061-DS1-1.JPG | B1044.061-DS2-1.JPG |  |  |  | No | None | YES
B1044.081 | B1044.081 | Low rise reinforced concrete walls with boundary columns, 17"-24" thick, height <15' | Costing for each 144 ft^2 Wall Panel, Orthogonal web reinforcement, f'c > 2500 psi, P/(A*f'c) <= 0.2 | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 210 | SF 144 | NO | NO | Crushed core concrete; localized concrete cracking with widths greater than 0.12 in; buckling of vertical rebar. | Sliding of the wall resulting in large residual displacement; distributed concrete cracking with widths greater than 0.12 in; fracture of rebar. |  |  |  | 1 | 1 |  |  |  | 0.0033 | 0.0087 |  |  |  | 0.33 | 0.18 |  |  |  | 0.1 | 0.1 |  |  |  | 0.35 | 0.2 |  |  |  | NO | YES | Average | Average | Superior | Superior | Remove furnishings, ceilings and mechanical, electrical and plumping systems (as necessary) 5 feet either side of damaged area. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumping systems (as necessary). | (1) Relocate eqpt.& furniture within 10 ft. of wall, both sides. Install protection on floor & adjacent walls. (2) Remove wall finishes, both sides. (3) Relocate MEP within 10 ft. of wall. (4) Remove damaged wall in 5-ft.lengths. (5) Install bars: a. 12#9 A706 bars in bz ea. end; mech splices to (E) ; b. #4 A706 dbl sets of seismic ties at 4 in. oc ea bz; c. #4 A706 bar at 6 in. oc, ewef; lap new vert. bars to (E) at top of wall; drill & epoxy bars into wall/fdn at 6 in. oc to match new rebar above. Anchor horiz. Bars in bz with seismic hks or lap 24 in. with (E) horiz. bars. (6) Form wall. Cast 5ksi concrete in 3-ft. lifts; with 1-in. top gap for grout day after casting. (7) Remove forms, clean-up & reinstall/return eqpt, finishes, furniture & MEP. |  |  |  | NO | NO |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | YES | YES |  |  |  | 50% | 25% |  |  |  | 0.5 | 0.5 |  |  |  | Full repair description does not fully fit on sheet - consider shortening. Description will fit in PACT. | Not Given | By User | By User | Andrew Whittaker | B1044.061-DS1-1.JPG | B1044.061-DS2-1.JPG |  |  |  | No | None | YES
B1044.082 | B1044.082 | Low rise reinforced concrete walls with boundary columns, 17"-24" thick, height between 16'-24' | Costing for each 400 ft^2 Wall Panel, Orthogonal web reinforcement, f'c > 2500 psi, P/(A*f'c) <= 0.2 | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 211 | SF 400 | NO | NO | Crushed core concrete; localized concrete cracking with widths greater than 0.12 in; buckling of vertical rebar. | Sliding of the wall resulting in large residual displacement; distributed concrete cracking with widths greater than 0.12 in; fracture of rebar. |  |  |  | 1 | 1 |  |  |  | 0.0033 | 0.0087 |  |  |  | 0.33 | 0.18 |  |  |  | 0.1 | 0.1 |  |  |  | 0.35 | 0.2 |  |  |  | NO | YES | Average | Average | Superior | Superior | Remove furnishings, ceilings and mechanical, electrical and plumping systems (as necessary) 5 feet either side of damaged area. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumping systems (as necessary). | (1) Relocate eqpt.& furniture within 10 ft. of wall, both sides. Install protection on floor & adjacent walls. (2) Remove wall finishes, both sides. (3) Relocate MEP within 10 ft. of wall. (4) Remove damaged wall in 5-ft.lengths. (5) Install bars: a. 12#9 A706 bars in bz ea. end; mech splices to (E) ; b. #4 A706 dbl sets of seismic ties at 4 in. oc ea bz; c. #4 A706 bar at 6 in. oc, ewef; lap new vert. bars to (E) at top of wall; drill & epoxy bars into wall/fdn at 6 in. oc to match new rebar above. Anchor horiz. Bars in bz with seismic hks or lap 24 in. with (E) horiz. bars. (6) Form wall. Cast 5ksi concrete in 3-ft. lifts; with 1-in. top gap for grout day after casting. (7) Remove forms, clean-up & reinstall/return eqpt, finishes, furniture & MEP. |  |  |  | NO | NO |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | YES | YES |  |  |  | 50% | 25% |  |  |  | 0.5 | 0.5 |  |  |  | Full repair description does not fully fit on sheet - consider shortening. Description will fit in PACT. | Not Given | By User | By User | Andrew Whittaker | B1044.061-DS1-1.JPG | B1044.061-DS2-1.JPG |  |  |  | No | None | YES
B1044.083 | B1044.083 | Low rise reinforced concrete walls with boundary columns, 17"-24" thick, height between 24'-40' | Costing for each 900 ft^2 Wall Panel, Orthogonal web reinforcement, f'c > 2500 psi, P/(A*f'c) <= 0.2 | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 212 | SF 900 | NO | NO | Crushed core concrete; localized concrete cracking with widths greater than 0.12 in; buckling of vertical rebar. | Sliding of the wall resulting in large residual displacement; distributed concrete cracking with widths greater than 0.12 in; fracture of rebar. |  |  |  | 1 | 1 |  |  |  | 0.0033 | 0.0087 |  |  |  | 0.33 | 0.18 |  |  |  | 0.1 | 0.1 |  |  |  | 0.35 | 0.2 |  |  |  | NO | YES | Average | Average | Superior | Superior | Remove furnishings, ceilings and mechanical, electrical and plumping systems (as necessary) 5 feet either side of damaged area. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumping systems (as necessary). | (1) Relocate eqpt.& furniture within 10 ft. of wall, both sides. Install protection on floor & adjacent walls. (2) Remove wall finishes, both sides. (3) Relocate MEP within 10 ft. of wall. (4) Remove damaged wall in 5-ft.lengths. (5) Install bars: a. 12#9 A706 bars in bz ea. end; mech splices to (E) ; b. #4 A706 dbl sets of seismic ties at 4 in. oc ea bz; c. #4 A706 bar at 6 in. oc, ewef; lap new vert. bars to (E) at top of wall; drill & epoxy bars into wall/fdn at 6 in. oc to match new rebar above. Anchor horiz. Bars in bz with seismic hks or lap 24 in. with (E) horiz. bars. (6) Form wall. Cast 5ksi concrete in 3-ft. lifts; with 1-in. top gap for grout day after casting. (7) Remove forms, clean-up & reinstall/return eqpt, finishes, furniture & MEP. |  |  |  | NO | NO |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | YES | YES |  |  |  | 50% | 25% |  |  |  | 0.5 | 0.5 |  |  |  | Full repair description does not fully fit on sheet - consider shortening. Description will fit in PACT. | Not Given | By User | By User | Andrew Whittaker | B1044.061-DS1-1.JPG | B1044.061-DS2-1.JPG |  |  |  | No | None | YES
B1044.091 | B1044.091 | Slender Concrete Wall, 12" thick, 12' high, 15' long | Slender concrete shear wall with aspect ratio greater than or equal to 2.0. Costing assumes a 144 ft^2 wall panel. | Not Specified | Not applicable | Each | Each | Effective Drift | Unit less | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 213 | SF 144 | NO | NO | Spalling of cover, vertical cracks greater than 1/16 inch. | Exposed longitudinal reinforcing. | Core concrete damage, buckled reinforcing, fractured reinforcing, shear failure, web failure, bond slip |  |  | 1 | 1 | 1 |  |  | 0.0093 | 0.0128 | 0.0186 |  |  | 0.465 | 0.326 | 0.43 |  |  | 0.1 | 0.1 | 0.1 |  |  | 0.5 | 0.35 | 0.45 |  |  | NO | YES | Superior | Superior | Superior | Superior | Epoxy inject cracks and patch spalled concrete. | Shore wall, remove all concrete in damaged regions, replace concrete. | Replace wall or reinforce with R/C jacket if possible. Shore floor and wall, remove damaged concrete and steel within one development length of damaged region, replace removed concrete and steel. |  |  | NO | NO | NO |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | YES | YES |  |  | 0% | 25% | 10% |  |  | 0 | 0.5 | 0.5 |  |  | None | Not Given | By User | By User | Not Given | B1044.091-DS1-1.JPG | B1044.091-DS2-1.JPG | B1044.091-DS3-1.JPG |  |  | No | 2011-08-24 Negative probability below 0.5% drift - overlap deemed acceptable. | YES
B1044.092 | B1044.092 | Slender Concrete Wall, 12" thick, 12' high, 20' long | Slender concrete shear wall with aspect ratio greater than or equal to 2.0. Costing assumes a 144 ft^2 wall panel. | Not Specified | Not applicable | Each | Each | Effective Drift | Unit less | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 214 | SF 144 | NO | NO | Spalling of cover, vertical cracks greater than 1/16 inch. | Exposed longitudinal reinforcing. | Core concrete damage, buckled reinforcing, fractured reinforcing, shear failure, web failure, bond slip |  |  | 1 | 1 | 1 |  |  | 0.0093 | 0.0128 | 0.0186 |  |  | 0.465 | 0.326 | 0.43 |  |  | 0.1 | 0.1 | 0.1 |  |  | 0.5 | 0.35 | 0.45 |  |  | NO | YES | Superior | Superior | Superior | Superior | Epoxy inject cracks and patch spalled concrete. | Shore wall, remove all concrete in damaged regions, replace concrete. | Replace wall or reinforce with R/C jacket if possible. Shore floor and wall, remove damaged concrete and steel within one development length of damaged region, replace removed concrete and steel. |  |  | NO | NO | NO |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | YES | YES |  |  | 0% | 25% | 10% |  |  | 0 | 0.5 | 0.5 |  |  | None | Not Given | By User | By User | Not Given | B1044.091-DS1-1.JPG | B1044.091-DS2-1.JPG | B1044.091-DS3-1.JPG |  |  | No | 2011-08-24 Negative probability below 0.5% drift - overlap deemed acceptable. | YES
B1044.093 | B1044.093 | Slender Concrete Wall, 12" thick, 12' high, 30' long | Slender concrete shear wall with aspect ratio greater than or equal to 2.0. Costing assumes a 144 ft^2 wall panel. | Not Specified | Not applicable | Each | Each | Effective Drift | Unit less | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 215 | SF 144 | NO | NO | Spalling of cover, vertical cracks greater than 1/16 inch. | Exposed longitudinal reinforcing. | Core concrete damage, buckled reinforcing, fractured reinforcing, shear failure, web failure, bond slip |  |  | 1 | 1 | 1 |  |  | 0.0093 | 0.0128 | 0.0186 |  |  | 0.465 | 0.326 | 0.43 |  |  | 0.1 | 0.1 | 0.1 |  |  | 0.5 | 0.35 | 0.45 |  |  | NO | YES | Superior | Superior | Superior | Superior | Epoxy inject cracks and patch spalled concrete. | Shore wall, remove all concrete in damaged regions, replace concrete. | Replace wall or reinforce with R/C jacket if possible. Shore floor and wall, remove damaged concrete and steel within one development length of damaged region, replace removed concrete and steel. |  |  | NO | NO | NO |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | YES | YES |  |  | 0% | 25% | 10% |  |  | 0 | 0.5 | 0.5 |  |  | None | Not Given | By User | By User | Not Given | B1044.091-DS1-1.JPG | B1044.091-DS2-1.JPG | B1044.091-DS3-1.JPG |  |  | No | 2011-08-24 Negative probability below 0.5% drift - overlap deemed acceptable. | YES
B1044.101 | B1044.101 | Slender Concrete Wall, 18" thick, 12' high, 15' long | Slender concrete shear wall with aspect ratio greater than or equal to 2.0. Costing assumes a 144 ft^2 wall panel. | Not Specified | Not applicable | Each | Each | Effective Drift | Unit less | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 216 | SF 144 | NO | NO | Spalling of cover, vertical cracks greater than 1/16 inch. | Exposed longitudinal reinforcing. | Core concrete damage, buckled reinforcing, fractured reinforcing, shear failure, web failure, bond slip |  |  | 1 | 1 | 1 |  |  | 0.0093 | 0.0128 | 0.0186 |  |  | 0.465 | 0.326 | 0.43 |  |  | 0.1 | 0.1 | 0.1 |  |  | 0.5 | 0.35 | 0.45 |  |  | NO | YES | Superior | Superior | Superior | Superior | Epoxy inject cracks and patch spalled concrete. | Shore wall, remove all concrete in damaged regions, replace concrete. | Replace wall or reinforce with R/C jacket if possible. Shore floor and wall, remove damaged concrete and steel within one development length of damaged region, replace removed concrete and steel. |  |  | NO | NO | NO |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | YES | YES |  |  | 0% | 25% | 10% |  |  | 0 | 0.5 | 0.5 |  |  | None | Not Given | By User | By User | Not Given | B1044.091-DS1-1.JPG | B1044.091-DS2-1.JPG | B1044.091-DS3-1.JPG |  |  | No | 2011-08-24 Negative probability below 0.5% drift - overlap deemed acceptable. | YES
B1044.102 | B1044.102 | Slender Concrete Wall, 18" thick, 12' high, 20' long | Slender concrete shear wall with aspect ratio greater than or equal to 2.0. Costing assumes a 144 ft^2 wall panel. | Not Specified | Not applicable | Each | Each | Effective Drift | Unit less | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 217 | SF 144 | NO | NO | Spalling of cover, vertical cracks greater than 1/16 inch. | Exposed longitudinal reinforcing. | Core concrete damage, buckled reinforcing, fractured reinforcing, shear failure, web failure, bond slip |  |  | 1 | 1 | 1 |  |  | 0.0093 | 0.0128 | 0.0186 |  |  | 0.465 | 0.326 | 0.43 |  |  | 0.1 | 0.1 | 0.1 |  |  | 0.5 | 0.35 | 0.45 |  |  | NO | YES | Superior | Superior | Superior | Superior | Epoxy inject cracks and patch spalled concrete. | Shore wall, remove all concrete in damaged regions, replace concrete. | Replace wall or reinforce with R/C jacket if possible. Shore floor and wall, remove damaged concrete and steel within one development length of damaged region, replace removed concrete and steel. |  |  | NO | NO | NO |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | YES | YES |  |  | 0% | 25% | 10% |  |  | 0 | 0.5 | 0.5 |  |  | None | Not Given | By User | By User | Not Given | B1044.091-DS1-1.JPG | B1044.091-DS2-1.JPG | B1044.091-DS3-1.JPG |  |  | No | 2011-08-24 Negative probability below 0.5% drift - overlap deemed acceptable. | YES
B1044.103 | B1044.103 | Slender Concrete Wall, 18" thick, 12' high, 30' long | Slender concrete shear wall with aspect ratio greater than or equal to 2.0. Costing assumes a 144 ft^2 wall panel. | Not Specified | Not applicable | Each | Each | Effective Drift | Unit less | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 218 | SF 144 | NO | NO | Spalling of cover, vertical cracks greater than 1/16 inch. | Exposed longitudinal reinforcing. | Core concrete damage, buckled reinforcing, fractured reinforcing, shear failure, web failure, bond slip |  |  | 1 | 1 | 1 |  |  | 0.0093 | 0.0128 | 0.0186 |  |  | 0.465 | 0.326 | 0.43 |  |  | 0.1 | 0.1 | 0.1 |  |  | 0.5 | 0.35 | 0.45 |  |  | NO | YES | Superior | Superior | Superior | Superior | Epoxy inject cracks and patch spalled concrete. | Shore wall, remove all concrete in damaged regions, replace concrete. | Replace wall or reinforce with R/C jacket if possible. Shore floor and wall, remove damaged concrete and steel within one development length of damaged region, replace removed concrete and steel. |  |  | NO | NO | NO |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | YES | YES |  |  | 0% | 25% | 10% |  |  | 0 | 0.5 | 0.5 |  |  | None | Not Given | By User | By User | Not Given | B1044.091-DS1-1.JPG | B1044.091-DS2-1.JPG | B1044.091-DS3-1.JPG |  |  | No | 2011-08-24 Negative probability below 0.5% drift - overlap deemed acceptable. | YES
B1044.111 | B1044.111 | Slender Concrete Wall, 30" thick, 12' high, 15' long | Slender concrete shear wall with aspect ratio greater than or equal to 2.0. Costing assumes a 144 ft^2 wall panel. | Not Specified | Not applicable | Each | Each | Effective Drift | Unit less | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 219 | SF 144 | NO | NO | Spalling of cover, vertical cracks greater than 1/16 inch. | Exposed longitudinal reinforcing. | Core concrete damage, buckled reinforcing, fractured reinforcing, shear failure, web failure, bond slip |  |  | 1 | 1 | 1 |  |  | 0.0093 | 0.0128 | 0.0186 |  |  | 0.465 | 0.326 | 0.43 |  |  | 0.1 | 0.1 | 0.1 |  |  | 0.5 | 0.35 | 0.45 |  |  | NO | YES | Superior | Superior | Superior | Superior | Epoxy inject cracks and patch spalled concrete. | Shore wall, remove all concrete in damaged regions, replace concrete. | Replace wall or reinforce with R/C jacket if possible. Shore floor and wall, remove damaged concrete and steel within one development length of damaged region, replace removed concrete and steel. |  |  | NO | NO | NO |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | YES | YES |  |  | 0% | 25% | 10% |  |  | 0 | 0.5 | 0.5 |  |  | None | Not Given | By User | By User | Not Given | B1044.091-DS1-1.JPG | B1044.091-DS2-1.JPG | B1044.091-DS3-1.JPG |  |  | No | 2011-08-24 Negative probability below 0.5% drift - overlap deemed acceptable. | YES
B1044.112 | B1044.112 | Slender Concrete Wall, 30" thick, 12' high, 20' long | Slender concrete shear wall with aspect ratio greater than or equal to 2.0. Costing assumes a 144 ft^2 wall panel. | Not Specified | Not applicable | Each | Each | Effective Drift | Unit less | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 220 | SF 144 | NO | NO | Spalling of cover, vertical cracks greater than 1/16 inch. | Exposed longitudinal reinforcing. | Core concrete damage, buckled reinforcing, fractured reinforcing, shear failure, web failure, bond slip |  |  | 1 | 1 | 1 |  |  | 0.0093 | 0.0128 | 0.0186 |  |  | 0.465 | 0.326 | 0.43 |  |  | 0.1 | 0.1 | 0.1 |  |  | 0.5 | 0.35 | 0.45 |  |  | NO | YES | Superior | Superior | Superior | Superior | Epoxy inject cracks and patch spalled concrete. | Shore wall, remove all concrete in damaged regions, replace concrete. | Replace wall or reinforce with R/C jacket if possible. Shore floor and wall, remove damaged concrete and steel within one development length of damaged region, replace removed concrete and steel. |  |  | NO | NO | NO |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | YES | YES |  |  | 0% | 25% | 10% |  |  | 0 | 0.5 | 0.5 |  |  | None | Not Given | By User | By User | Not Given | B1044.091-DS1-1.JPG | B1044.091-DS2-1.JPG | B1044.091-DS3-1.JPG |  |  | No | 2011-08-24 Negative probability below 0.5% drift - overlap deemed acceptable. | YES
B1044.113 | B1044.113 | Slender Concrete Wall, 30" thick, 12' high, 30' long | Slender concrete shear wall with aspect ratio greater than or equal to 2.0. Costing assumes a 144 ft^2 wall panel. | Not Specified | Not applicable | Each | Each | Effective Drift | Unit less | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 221 | SF 144 | NO | NO | Spalling of cover, vertical cracks greater than 1/16 inch. | Exposed longitudinal reinforcing. | Core concrete damage, buckled reinforcing, fractured reinforcing, shear failure, web failure, bond slip |  |  | 1 | 1 | 1 |  |  | 0.0093 | 0.0128 | 0.0186 |  |  | 0.465 | 0.326 | 0.43 |  |  | 0.1 | 0.1 | 0.1 |  |  | 0.5 | 0.35 | 0.45 |  |  | NO | YES | Superior | Superior | Superior | Superior | Epoxy inject cracks and patch spalled concrete. | Shore wall, remove all concrete in damaged regions, replace concrete. | Replace wall or reinforce with R/C jacket if possible. Shore floor and wall, remove damaged concrete and steel within one development length of damaged region, replace removed concrete and steel. |  |  | NO | NO | NO |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | YES | YES |  |  | 0% | 25% | 10% |  |  | 0 | 0.5 | 0.5 |  |  | None | Not Given | By User | By User | Not Given | B1044.091-DS1-1.JPG | B1044.091-DS2-1.JPG | B1044.091-DS3-1.JPG |  |  | No | 2011-08-24 Negative probability below 0.5% drift - overlap deemed acceptable. | YES
B1049.001a | B1049.001a | Reinforced concrete flat slabs- columns without shear reinforcing 0<Vg/Vo<.2, no continuity reinf | Costing per joint, minimum of 6" thick slab, maximum of 12" thick slab. | Not Specified | Not applicable | Each | Each | Story Drift Ratio | Unit less | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 222 | EA 1 | YES | NO | Yield strain of the slab flexural reinforcement has been exceeded, spalling of concrete may/may not occur, slab exhibits large enough crack widths to allow epoxy injection. | Punching occurs, causing significant spalling of concrete. Epoxy injection is no longer expected to be sufficient to restore the required strength and stiffness to the slab and the slab-column connection. |  |  |  | 1 | 1 |  |  |  | 0.025 | 0.04 |  |  |  | 0.2 | 0.2 |  |  |  | 0.2 | 0.2 |  |  |  | 0.25 | 0.25 |  |  |  | NO | NO | Average | Average | Average | Superior | Remove furnishings, ceilings and mechanical, electrical and plumping systems (as necessary) 5 feet either side of damaged area. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumping systems (as necessary). | Shore damaged area in the two stories below. Remove 100 square feet of concrete slab per column, preserving the slab reinforcement; lap splice 30 new 10 foot long rebar with existing rebar; place formwork; recast concrete slab; remove forms, replace and repair finishes; replace furnishings, ceilings, mechanical, electrical, and plumbing systems. Cracks wide enough to be grouted are included in the portion of slab to be demolished and recast. |  |  |  | NO | NO |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | YES |  |  |  | 0% | 10% |  |  |  | 0 | 0.5 |  |  |  | None | Not Given | By User | By User | John Wallace | B1049.001a-DS1-1.JPG | B1049.001a-DS2-1.JPG |  |  |  | No | None | YES
B1049.001b | B1049.001b | Reinforced concrete flat slabs- columns without shear reinforcing 0<Vg/Vo<.2, with continuity reinf | Costing per joint, minimum of 6" thick slab, maximum of 12" thick slab. | Not Specified | Not applicable | Each | Each | Story Drift Ratio | Unit less | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 223 | EA 1 | YES | NO | Yield strain of the slab flexural reinforcement has been exceeded, spalling of concrete may/may not occur, slab exhibits large enough crack widths to allow epoxy injection. | Punching occurs, causing significant spalling of concrete. Epoxy injection is no longer expected to be sufficient to restore the required strength and stiffness to the slab and the slab-column connection. |  |  |  | 1 | 1 |  |  |  | 0.025 | 0.04 |  |  |  | 0.2 | 0.2 |  |  |  | 0.2 | 0.2 |  |  |  | 0.25 | 0.25 |  |  |  | NO | NO | Average | Average | Average | Superior | Remove furnishings, ceilings and mechanical, electrical and plumping systems (as necessary) 5 feet either side of damaged area. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumping systems (as necessary). | Prepare work area for epoxy injection, inject epoxy into 40 feet of crack (30 feet top, 10 bottom of slab) of crack per 100 square feet of floor panel. Fabricate new structural steel shear head (column capital) that attaches to the column beneath the slab. |  |  |  | NO | NO |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | YES |  |  |  | 0% | 20% |  |  |  | 0 | 0.5 |  |  |  | None | Not Given | By User | By User | John Wallace | B1049.001a-DS1-1.JPG | B1049.001a-DS2-1.JPG |  |  |  | No | None | YES
B1049.002a | B1049.002a | Reinforced concrete flat slabs- columns without shear reinforcing .2<Vg/Vo<.4, no continuity reinf | Costing is on a per joint basis. | ACI 318-56, ACI 318-63, ACI 318-89, ACI 318-95, ACI 318-99, ACI 318-05 | Not applicable | Each | Each | Story Drift Ratio | Unit less | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 224 | EA 1 | YES | NO | Yield strain of the slab flexural reinforcement has been exceeded, spalling of concrete may/may not occur, slab exhibits large enough crack widths to allow epoxy injection. | Punching occurs, causing significant spalling of concrete. Epoxy injection is no longer expected to be sufficient to restore the required strength and stiffness to the slab and the slab-column connection. |  |  |  | 1 | 1 |  |  |  | 0.02 | 0.035 |  |  |  | 0.4 | 0.4 |  |  |  | 0.1 | 0.1 |  |  |  | 0.4 | 0.4 |  |  |  | NO | NO | Average | Average | Average | Superior | Remove furnishings, ceilings and mechanical, electrical and plumping systems (as necessary) 5 feet either side of damaged area. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumping systems (as necessary). | Shore damaged area in the two stories below. Remove 100 square feet of concrete slab per column, preserving the slab reinforcement; lap splice 30 new 10 foot long rebar with existing rebar; place formwork; recast concrete slab; remove forms, replace and repair finishes; replace furnishings, ceilings, mechanical, electrical, and plumbing systems Cracks wide enough to be grouted are included in the portion of slab to be demolished and recast. |  |  |  | NO | NO |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | YES |  |  |  | 0% | 10% |  |  |  | 0 | 0.5 |  |  |  | None | Not Given | By User | By User | John Wallace | B1049.001a-DS1-1.JPG | B1049.001a-DS2-1.JPG |  |  |  | No | None | YES
B1049.002b | B1049.002b | Reinforced concrete flat slabs- columns without shear reinforcing .2<Vg/Vo<.4, with continuity reinf | Costing is on a per joint basis. | ACI 318-56, ACI 318-63, ACI 318-89, ACI 318-95, ACI 318-99, ACI 318-05 | Not applicable | Each | Each | Story Drift Ratio | Unit less | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 225 | EA 1 | YES | NO | Yield strain of the slab flexural reinforcement has been exceeded, spalling of concrete may/may not occur, slab exhibits large enough crack widths to allow epoxy injection. | Punching occurs, causing significant spalling of concrete. Epoxy injection is no longer expected to be sufficient to restore the required strength and stiffness to the slab and the slab-column connection. |  |  |  | 1 | 1 |  |  |  | 0.02 | 0.035 |  |  |  | 0.4 | 0.4 |  |  |  | 0.1 | 0.1 |  |  |  | 0.4 | 0.4 |  |  |  | NO | NO | Average | Average | Average | Superior | Remove furnishings, ceilings and mechanical, electrical and plumping systems (as necessary) 5 feet either side of damaged area. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumping systems (as necessary). | Prepare work area for epoxy injection, inject epoxy into 40 feet of crack (30 feet top, 10 feet bottom of slab) per 100 square feet of floor panel. Fabricate new structural steel shear head (column capital) that attaches to the column beneath the slab. |  |  |  | NO | NO |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | YES |  |  |  | 0% | 20% |  |  |  | 0 | 0.5 |  |  |  | None | Not Given | By User | By User | John Wallace | B1049.001a-DS1-1.JPG | B1049.001a-DS2-1.JPG |  |  |  | No | None | YES
B1049.003a | B1049.003a | Reinforced concrete flat slabs- columns without shear reinforcing .4<Vg/Vo<.6, no continuity reinf | Costing is on a per joint basis. | ACI 318-63, ACI 318-83, ACI 318-99, ACI 318-02, CAN3-A23.2-M84, A23.3 & MC-90 | Not applicable | Each | Each | Story Drift Ratio | Unit less | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 226 | EA 1 | YES | NO | Yield strain of the slab flexural reinforcement has been exceeded, spalling of concrete may/may not occur, slab exhibits large enough crack widths to allow epoxy injection. | Punching occurs, causing significant spalling of concrete. Epoxy injection is no longer expected to be sufficient to restore the required strength and stiffness to the slab and the slab-column connection. |  |  |  | 1 | 1 |  |  |  | 0.012 | 0.016 |  |  |  | 0.4 | 0.4 |  |  |  | 0.1 | 0.1 |  |  |  | 0.4 | 0.4 |  |  |  | NO | NO | Average | Average | Average | Superior | Remove furnishings, ceilings and mechanical, electrical and plumping systems (as necessary) 5 feet either side of damaged area. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumping systems (as necessary). | Shore damaged area in the two stories below. Remove 100 square feet of concrete slab per column, preserving the slab reinforcement; lap splice 30 new 10 foot long rebar with existing rebar; place formwork; recast concrete slab; remove forms, replace and repair finishes; replace furnishings, ceilings, mechanical, electrical, and plumbing systems. Cracks wide enough to be grouted are included in the portion of slab to be demolished and recast. |  |  |  | NO | NO |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | YES |  |  |  | 0% | 10% |  |  |  | 0 | 0.5 |  |  |  | None | Not Given | By User | By User | John Wallace | B1049.001a-DS1-1.JPG | B1049.001a-DS2-1.JPG |  |  |  | No | None | YES
B1049.003b | B1049.003b | Reinforced concrete flat slabs- columns without shear reinforcing .4<Vg/Vo<.6, with continuity reinf | Costing is on a per joint basis. | ACI 318-63, ACI 318-83, ACI 318-99, ACI 318-02, CAN3-A23.2-M84, A23.3 & MC-90 | Not applicable | Each | Each | Story Drift Ratio | Unit less | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 227 | EA 1 | YES | NO | Yield strain of the slab flexural reinforcement has been exceeded, spalling of concrete may/may not occur, slab exhibits large enough crack widths to allow epoxy injection. | Punching occurs, causing significant spalling of concrete. Epoxy injection is no longer expected to be sufficient to restore the required strength and stiffness to the slab and the slab-column connection. |  |  |  | 1 | 1 |  |  |  | 0.012 | 0.016 |  |  |  | 0.4 | 0.4 |  |  |  | 0.1 | 0.1 |  |  |  | 0.4 | 0.4 |  |  |  | NO | NO | Average | Average | Average | Superior | Remove furnishings, ceilings and mechanical, electrical and plumping systems (as necessary) 5 feet either side of damaged area. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumping systems (as necessary). | Prepare work area for epoxy injection, inject epoxy into 55 feet of crack (40 feet top, 15 feet bottom of slab) per 100 square feet of floor panel. Fabricate new structural steel shear head (column capital) that attaches to the column beneath the slab. |  |  |  | NO | NO |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | YES |  |  |  | 0% | 20% |  |  |  | 0 | 0.5 |  |  |  | None | Not Given | By User | By User | John Wallace | B1049.001a-DS1-1.JPG | B1049.001a-DS2-1.JPG |  |  |  | No | None | YES
B1049.011 | B1049.011 | Reinforced concrete flat slabs- columns with shear reinforcing 0.2<Vg/Vo<0.4 | Costing is on a per joint basis. | ACI 318-71, ACI 318-95, ACI 318-99, ACI 318-05 | Not applicable | Each | Each | Story Drift Ratio | Unit less | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 228 | EA 1 | YES | NO | Yield strain of the slab flexural reinforcement has been exceeded, spalling of concrete may/may not occur, slab exhibits large enough crack widths to allow epoxy injection. | Punching occurs, causing significant spalling of concrete. Epoxy injection is no longer expected to be sufficient to restore the required strength and stiffness to the slab and the slab-column connection. |  |  |  | 1 | 1 |  |  |  | 0.03 | 0.048 |  |  |  | 0.35 | 0.46 |  |  |  | 0.1 | 0.1 |  |  |  | 0.4 | 0.4 |  |  |  | NO | NO | Average | Average | Average | Superior | Remove furnishings, ceilings and mechanical, electrical and plumping systems (as necessary) 5 feet either side of damaged area. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumping systems (as necessary). | Prepare work area for epoxy injection, inject epoxy into 70 feet of crack (50 feet top, 20 feet bottom of slab) per 100 square feet of floor panel. Fabricate new structural steel shear head (column capital) that attaches to the column beneath the slab. |  |  |  | NO | NO |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | YES |  |  |  | 0% | 20% |  |  |  | 0 | 0.5 |  |  |  | None | Not Given | By User | By User | John Wallace | B1049.001a-DS1-1.JPG | B1049.001a-DS2-1.JPG |  |  |  | No | 2011-08-24 DS 2 beta changed from 0.5 to 0.4 to avoid negative probability. | YES
B1049.012 | B1049.012 | Reinforced concrete flat slabs- columns with shear reinforcing 0.4<Vg/Vo<.6 | Costing is on a per joint basis. | ACI-318-63, ACI-318-05, A23.3 & MC-90 | Not applicable | Each | Each | Story Drift Ratio | Unit less | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 229 | EA 1 | YES | NO | Yield strain of the slab flexural reinforcement has been exceeded, spalling of concrete may/may not occur, slab exhibits large enough crack widths to allow epoxy injection. | Punching occurs, causing significant spalling of concrete. Epoxy injection is no longer expected to be sufficient to restore the required strength and stiffness to the slab and the slab-column connection. |  |  |  | 1 | 1 |  |  |  | 0.022 | 0.03 |  |  |  | 0.4 | 0.5 |  |  |  | 0.1 | 0.1 |  |  |  | 0.4 | 0.4 |  |  |  | NO | NO | Average | Average | Average | Superior | Remove furnishings, ceilings and mechanical, electrical and plumping systems (as necessary) 5 feet either side of damaged area. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumping systems (as necessary). | Prepare work area for epoxy injection, inject epoxy into 85 feet of crack (60 feet top, 25 feet bottom of slab) per 100 square feet of floor panel. Fabricate new structural steel shear head (column capital) that attaches to the column beneath the slab. |  |  |  | NO | NO |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | YES |  |  |  | 0% | 20% |  |  |  | 0 | 0.5 |  |  |  | None | Not Given | By User | By User | John Wallace | B1049.001a-DS1-1.JPG | B1049.001a-DS2-1.JPG |  |  |  | No | 2011-08-24 DS 2 beta changed from 0.5 to 0.4 to avoid negative probability. | YES
B1049.021a | B1049.021a | Post-tensioned concrete flat slabs- columns without shear reinforcing 0.2<Vg/Vo<.0.4, no continuity reinf | Costing is on a per joint basis. | ACI-318-77, ACI-318-89, ACI-318-05, IBC-03 | Not applicable | Each | Each | Story Drift Ratio | Unit less | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 230 | EA 1 | YES | NO | Yield strain of the slab flexural reinforcement has been exceeded, spalling of concrete may/may not occur, slab exhibits large enough crack widths to allow epoxy injection. | Punching occurs, causing significant spalling of concrete. Epoxy injection is no longer expected to be sufficient to restore the required strength and stiffness to the slab and the slab-column connection. |  |  |  | 1 | 1 |  |  |  | 0.018 | 0.03 |  |  |  | 0.39 | 0.34 |  |  |  | 0.1 | 0.1 |  |  |  | 0.4 | 0.4 |  |  |  | NO | NO | Average | Average | Average | Superior | Remove furnishings, ceilings and mechanical, electrical and plumping systems (as necessary) 5 feet either side of damaged area. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumping systems (as necessary). | Shore damaged area in the two stories below. Remove 100 square feet of concrete slab per column, preserving the slab reinforcement; lap splice 30 new 10 foot long rebar with existing rebar; place formwork; recast concrete slab; remove forms, replace and repair finishes; replace furnishings, ceilings, mechanical, electrical, and plumbing systems. Cracks wide enough to be grouted are included in the portion of slab to be demolished and recast. |  |  |  | NO | NO |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | YES |  |  |  | 0% | 10% |  |  |  | 0 | 0.5 |  |  |  | None | Not Given | By User | By User | John Wallace | B1049.001a-DS1-1.JPG | B1049.001a-DS2-1.JPG |  |  |  | No | None | YES
B1049.021b | B1049.021b | Post-tensioned concrete flat slabs- columns without shear reinforcing 0.2<Vg/Vo<.0.4, with continuity reinf | Costing is on a per joint basis. | ACI-318-77, ACI-318-89, ACI-318-05, IBC-03 | Not applicable | Each | Each | Story Drift Ratio | Unit less | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 231 | EA 1 | YES | NO | Yield strain of the slab flexural reinforcement has been exceeded, spalling of concrete may/may not occur, slab exhibits large enough crack widths to allow epoxy injection. | Punching occurs, causing significant spalling of concrete. Epoxy injection is no longer expected to be sufficient to restore the required strength and stiffness to the slab and the slab-column connection. |  |  |  | 1 | 1 |  |  |  | 0.018 | 0.03 |  |  |  | 0.39 | 0.34 |  |  |  | 0.1 | 0.1 |  |  |  | 0.4 | 0.4 |  |  |  | NO | NO | Average | Average | Average | Superior | Remove furnishings, ceilings and mechanical, electrical and plumping systems (as necessary) 5 feet either side of damaged area. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumping systems (as necessary). | Prepare work area for epoxy injection, inject epoxy into 25 feet of crack (20 feet top, 5 feet bottom of slab) per 100 square feet of floor panel. Fabricate new structural steel shear head (column capital) that attaches to the column beneath the slab. |  |  |  | NO | NO |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | YES |  |  |  | 0% | 20% |  |  |  | 0 | 0.5 |  |  |  | None | Not Given | By User | By User | John Wallace | B1049.001a-DS1-1.JPG | B1049.001a-DS2-1.JPG |  |  |  | No | None | YES
B1049.022a | B1049.022a | Post-tensioned concrete flat slabs- columns without shear reinforcing 0.4<Vg/Vo<.0.6, no continuity reinf | Costing is on a per joint basis. | ACI-318-77, ACI-318-83, ACI-318-89, ACI-318-05 | Not applicable | Each | Each | Story Drift Ratio | Unit less | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 232 | EA 1 | YES | NO | Yield strain of the slab flexural reinforcement has been exceeded, spalling of concrete may/may not occur, slab exhibits large enough crack widths to allow epoxy injection. | Punching occurs, causing significant spalling of concrete. Epoxy injection is no longer expected to be sufficient to restore the required strength and stiffness to the slab and the slab-column connection. |  |  |  | 1 | 1 |  |  |  | 0.013 | 0.019 |  |  |  | 0.45 | 0.53 |  |  |  | 0.2 | 0.2 |  |  |  | 0.5 | 0.55 |  |  |  | NO | NO | Average | Average | Average | Superior | Remove furnishings, ceilings and mechanical, electrical and plumping systems (as necessary) 5 feet either side of damaged area. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumping systems (as necessary). | Shore damaged area in the two stories below. Remove 100 square feet of concrete slab per column, preserving the slab reinforcement; lap splice 30 new 10 foot long rebar with existing rebar; place formwork; recast concrete slab; remove forms, replace and repair finishes; replace furnishings, ceilings, mechanical, electrical, and plumbing systems. . Cracks wide enough to be grouted are included in the portion of slab to be demolished and recast. |  |  |  | NO | NO |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | YES |  |  |  | 0% | 10% |  |  |  | 0 | 0.5 |  |  |  | None | Not Given | By User | By User | John Wallace | B1049.001a-DS1-1.JPG | B1049.001a-DS2-1.JPG |  |  |  | No | 2011-08-24 Negative probability below 0.5% drift - overlap deemed acceptable. | YES
B1049.022b | B1049.022b | Post-tensioned concrete flat slabs- columns without shear reinforcing 0.4<Vg/Vo<.0.6, with continuity reinf | Costing is on a per joint basis. | ACI-318-77, ACI-318-83, ACI-318-89, ACI-318-05 | Not applicable | Each | Each | Story Drift Ratio | Unit less | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 233 | EA 1 | YES | NO | Yield strain of the slab flexural reinforcement has been exceeded, spalling of concrete may/may not occur, slab exhibits large enough crack widths to allow epoxy injection. | Punching occurs, causing significant spalling of concrete. Epoxy injection is no longer expected to be sufficient to restore the required strength and stiffness to the slab and the slab-column connection. |  |  |  | 1 | 1 |  |  |  | 0.013 | 0.019 |  |  |  | 0.45 | 0.53 |  |  |  | 0.2 | 0.2 |  |  |  | 0.5 | 0.55 |  |  |  | NO | NO | Average | Average | Average | Superior | Remove furnishings, ceilings and mechanical, electrical and plumping systems (as necessary) 5 feet either side of damaged area. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumping systems (as necessary). | Prepare work area for epoxy injection, inject epoxy into 40 feet of crack (30 feet top, 10 feet bottom of slab) per 100 square feet of floor panel. Fabricate new structural steel shear head (column capital) that attaches to the column beneath the slab. |  |  |  | NO | NO |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | YES |  |  |  | 0% | 20% |  |  |  | 0 | 0.5 |  |  |  | None | Not Given | By User | By User | John Wallace | B1049.001a-DS1-1.JPG | B1049.001a-DS2-1.JPG |  |  |  | No | 2011-08-24 Negative probability below 0.5% drift - overlap deemed acceptable. | YES
B1049.031 | B1049.031 | Post-tensioned concrete flat slabs- columns with shear reinforcing 0<Vg/Vo<.0.4 | Costing is on a per joint basis. | Not Specified | Not applicable | Each | Each | Story Drift Ratio | Unit less | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 234 | EA 1 | YES | NO | Yield strain of the slab flexural reinforcement has been exceeded, spalling of concrete may/may not occur, slab exhibits large enough crack widths to allow epoxy injection. | Punching occurs, causing significant spalling of concrete. Epoxy injection is no longer expected to be sufficient to restore the required strength and stiffness to the slab and the slab-column connection. |  |  |  | 1 | 1 |  |  |  | 0.028 | 0.04 |  |  |  | Not Specified | Not Specified |  |  |  | 0.5 | 0.5 |  |  |  | 0.5 | 0.5 |  |  |  | NO | NO | Average | Average | Superior | Superior | Remove furnishings, ceilings and mechanical, electrical and plumping systems (as necessary) 5 feet either side of damaged area. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumping systems (as necessary). | Prepare work area for epoxy injection, inject epoxy into 45 feet of crack (35 feet top, 10 feet bottom of slab) per 100 square feet of floor panel. Fabricate new structural steel shear head (column capital) that attaches to the column beneath the slab. |  |  |  | NO | NO |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | YES |  |  |  | 0% | 20% |  |  |  | 0 | 0.5 |  |  |  | Fragilities were based on judgment due to lack of test data. | Not Given | By User | By User | John Wallace | B1049.001a-DS1-1.JPG | B1049.001a-DS2-1.JPG |  |  |  | No | None | YES
B1049.032 | B1049.032 | Post-tensioned concrete flat slabs- columns with shear reinforcing 0.4<Vg/Vo<.0.6 | Costing is on a per joint basis. | Not Specified | Not applicable | Each | Each | Story Drift Ratio | Unit less | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 235 | EA 1 | YES | NO | Yield strain of the slab flexural reinforcement has been exceeded, spalling of concrete may/may not occur, slab exhibits large enough crack widths to allow epoxy injection. | Punching occurs, causing significant spalling of concrete. Epoxy injection is no longer expected to be sufficient to restore the required strength and stiffness to the slab and the slab-column connection. |  |  |  | 1 | 1 |  |  |  | 0.023 | 0.032 |  |  |  | Not Specified | Not Specified |  |  |  | 0.5 | 0.5 |  |  |  | 0.5 | 0.5 |  |  |  | NO | NO | Not Rated | Marginal | Average | Superior | Remove furnishings, ceilings and mechanical, electrical and plumping systems (as necessary) 5 feet either side of damaged area. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumping systems (as necessary). | Prepare work area for epoxy injection, inject epoxy into 60 feet of crack (45 feet top, 15 feet bottom of slab) per 100 square feet of floor panel. Fabricate new structural steel shear head (column capital) that attaches to the column beneath the slab. |  |  |  | NO | NO |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | YES |  |  |  | 0% | 20% |  |  |  | 0 | 0.5 |  |  |  | Fragilities were based on judgment due to lack of test data. | Not Given | By User | By User | John Wallace | B1049.001a-DS1-1.JPG | B1049.001a-DS2-1.JPG |  |  |  | No | None | YES
B1049.041a | B1049.041a | Reinforced concrete flat slabs drop panel or drop capital- columns without shear reinforcing 0<Vg/Vo<0.4, no continuity reinf | Costing is on a per joint basis. | Not Specified | Not applicable | Each | Each | Story Drift Ratio | Unit less | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 236 | EA 1 | YES | NO | Yield strain of the slab flexural reinforcement has been exceeded. Spalling of concrete may or may not occur. Slab exhibits large enough crack widths to allow epoxy injection. | Punching occurs causing significant spalling of concrete. |  |  |  | 1 | 1 |  |  |  | 0.025 | 0.042 |  |  |  | Not Specified | Not Specified |  |  |  | 0.5 | 0.5 |  |  |  | 0.5 | 0.5 |  |  |  | NO | NO | Marginal | Marginal | Average | Superior | Remove furnishings, ceilings and mechanical, electrical and plumping systems (as necessary) 5 feet either side of damaged area. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumping systems (as necessary). | Shore damaged area in the two stories below. Remove 100 square feet of concrete slab per column, preserving the slab reinforcement; lap splice 30 new 10 foot long rebar with existing rebar; place formwork; recast concrete slab; remove forms, replace and repair finishes; replace furnishings, ceilings, mechanical, electrical, and plumbing systems. Cracks wide enough to be grouted are included in the portion of slab to be demolished and recast. |  |  |  | NO | NO |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | YES |  |  |  | 0% | 10% |  |  |  | 0 | 0.5 |  |  |  | Fragilities were based on judgment due to lack of test data. The only available data were from a specimen that was constructed using ACI 318-89 | Not Given | By User | By User | John Wallace | B1049.041a-DS1-1.JPG | B1049.041a-DS2-1.JPG |  |  |  | No | None | YES
B1049.041b | B1049.041b | Reinforced concrete flat slabs drop panel or drop capital- columns without shear reinforcing 0<Vg/Vo<0.4, with continuity reinf | Costing is on a per joint basis. | Not Specified | Not applicable | Each | Each | Story Drift Ratio | Unit less | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 237 | EA 1 | YES | NO | Yield strain of the slab flexural reinforcement has been exceeded. Spalling of concrete may or may not occur. Slab exhibits large enough crack widths to allow epoxy injection. | Punching occurs causing significant spalling of concrete. |  |  |  | 1 | 1 |  |  |  | 0.025 | 0.042 |  |  |  | Not Specified | Not Specified |  |  |  | 0.5 | 0.5 |  |  |  | 0.5 | 0.5 |  |  |  | NO | NO | Marginal | Marginal | Average | Superior | Remove furnishings, ceilings and mechanical, electrical and plumping systems (as necessary) 5 feet either side of damaged area. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumping systems (as necessary). | Prepare work area for epoxy injection, inject epoxy into 40 feet of crack (30 feet top, 10 feet bottom of slab) per 100 square feet of floor panel. Fabricate new structural steel shear head (column capital) that attaches to the column beneath the slab. |  |  |  | NO | NO |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | YES |  |  |  | 0% | 20% |  |  |  | 0 | 0.5 |  |  |  | Fragilities were based on judgment due to lack of test data. The only available data were from a specimen that was constructed using ACI 318-89 | Not Given | By User | By User | John Wallace | B1049.041a-DS1-1.JPG | B1049.041a-DS2-1.JPG |  |  |  | No | None | YES
B1049.042a | B1049.042a | Reinforced concrete flat slabs drop panel or drop capital- columns without shear reinforcing 0.4<Vg/Vo<0.6, no continuity reinf | Costing is on a per joint basis. | Not Specified | Not applicable | Each | Each | Story Drift Ratio | Unit less | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 238 | EA 1 | YES | NO | Yield strain of the slab flexural reinforcement has been exceeded. Spalling of concrete may or may not occur. Slab exhibits large enough crack widths to allow epoxy injection. | Punching occurs causing significant spalling of concrete. |  |  |  | 1 | 1 |  |  |  | 0.017 | 0.023 |  |  |  | Not Specified | Not Specified |  |  |  | 0.5 | 0.5 |  |  |  | 0.5 | 0.5 |  |  |  | NO | NO | Not Rated | Marginal | Average | Superior | Remove furnishings, ceilings and mechanical, electrical and plumping systems (as necessary) 5 feet either side of damaged area. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumping systems (as necessary). | Shore damaged area in the two stories below. Remove 100 square feet of concrete slab per column, preserving the slab reinforcement; lap splice 30 new 10 foot long rebar with existing rebar; place formwork; recast concrete slab; remove forms, replace and repair finishes; replace furnishings, ceilings, mechanical, electrical, and plumbing systems. Cracks wide enough to be grouted are included in the portion of slab to be demolished and recast. |  |  |  | NO | NO |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | YES |  |  |  | 0% | 10% |  |  |  | 0 | 0.5 |  |  |  | Fragilities were based on judgment due to lack of test data. | Not Given | By User | By User | John Wallace | B1049.042a-DS1-1.JPG | B1049.042a-DS2-1.JPG |  |  |  | No | None | YES
B1049.042b | B1049.042b | Reinforced concrete flat slabs drop panel or drop capital- columns without shear reinforcing 0.4<Vg/Vo<0.6, with continuity reinf | Costing is on a per joint basis. | Not Specified | Not applicable | Each | Each | Story Drift Ratio | Unit less | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 239 | EA 1 | YES | NO | Yield strain of the slab flexural reinforcement has been exceeded. Spalling of concrete may or may not occur. Slab exhibits large enough crack widths to allow epoxy injection. | Punching occurs causing significant spalling of concrete. |  |  |  | 1 | 1 |  |  |  | 0.017 | 0.023 |  |  |  | Not Specified | Not Specified |  |  |  | 0.5 | 0.5 |  |  |  | 0.5 | 0.5 |  |  |  | NO | NO | Not Rated | Marginal | Average | Superior | Remove furnishings, ceilings and mechanical, electrical and plumping systems (as necessary) 5 feet either side of damaged area. Replace and repair finishes. Replace furnishings, ceilings and mechanical, electrical and plumping systems (as necessary). | Prepare work area for epoxy injection, inject epoxy into 55 feet of crack (40 feet top, 15 feet bottom of slab) per 100 square feet of floor panel. Fabricate new structural steel shear head (column capital) that attaches to the column beneath the slab. |  |  |  | NO | NO |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | YES |  |  |  | 0% | 20% |  |  |  | 0 | 0.5 |  |  |  | Fragilities were based on judgment due to lack of test data. | Not Given | By User | By User | John Wallace | B1049.042a-DS1-1.JPG | B1049.042a-DS2-1.JPG |  |  |  | No | None | YES
B1042.001a | B1042.001a | Concrete link beam, diagonally reinforced, aspect ratio between 1.0 and 2.0, beam < 16" wide and depth < 30" | None | Not Specified | Not applicable | Each | Each | Link Beam Chord Rotation | Radians | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 240 | EA 1 | YES | NO | Residual cracks no greater than 1/16 inch. Cracks are mainly at the beam to wall interface, some limited flexural cracking. | Residual cracks greater than 1/8 inch and minor spalling of concrete. | Significant strength degradation (<0.8Vn), buckling or fracture of diagonal reinforcing, crushing of concrete. |  |  | 1 | 1 | 1 |  |  | 0.0179 | 0.0352 | 0.0543 |  |  | Not Specified | Not Specified | Not Specified |  |  | Not Specified | Not Specified | Not Specified |  |  | 0.38 | 0.44 | 0.95 |  |  | NO | YES | Not Rated | Not Rated | Not Rated | Not Rated | Epoxy inject cracks (200 to 240 inches in length). | Epoxy inject cracks (600 to 720 inches) and slab (300 inches), replace spalled concrete. | Chip away damaged concrete, attached mechanical couplers to the diagonal bars still embedded in the wall, replace damaged or fractured reinforcing. Replace damaged concrete. |  |  | NO | NO | NO |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | NO | YES |  |  | 0% | 0% | 25% |  |  | 0 | 0 | 0.5 |  |  | None | Not Given | By User | By User | John Wallace | none | none | none |  |  | No | None | YES
B1042.001b | B1042.001b | Concrete link beam, diagonally reinforced, aspect ratio between 2.0 and 4.0, beam < 16" wide and depth < 30" | None | Not Specified | Not applicable | Each | Each | Link Beam Chord Rotation | Radians | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 241 | EA 1 | YES | NO | Residual cracks no greater than 1/16 inch. Cracks are mainly at the beam to wall interface, some limited flexural cracking. | Residual cracks greater than 1/8 inch and minor spalling of concrete. | Significant strength degradation (<0.8Vn), buckling or fracture of diagonal reinforcing, crushing of concrete. |  |  | 1 | 1 | 1 |  |  | 0.0203 | 0.0394 | 0.0602 |  |  | Not Specified | Not Specified | Not Specified |  |  | Not Specified | Not Specified | Not Specified |  |  | 0.39 | 0.35 | 1 |  |  | NO | YES | Not Rated | Not Rated | Not Rated | Not Rated | Epoxy inject cracks (200 to 240 inches in length). | Epoxy inject cracks (600 to 720 inches) and slab (300 inches), replace spalled concrete. | Chip away damaged concrete, attached mechanical couplers to the diagonal bars still embedded in the wall, replace damaged or fractured reinforcing. Replace damaged concrete. |  |  | NO | NO | NO |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | NO | YES |  |  | 0% | 0% | 25% |  |  | 0 | 0 | 0.5 |  |  | None | Not Given | By User | By User | John Wallace | none | none | none |  |  | No | None | YES
B1042.002a | B1042.002a | Concrete link beam, conventionally reinforced, aspect ratio between 1.0 and 2.0, beam < 16" wide and depth < 30" | None | Not Specified | Not applicable | Each | Each | Link Beam Chord Rotation | Radians | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 242 | EA 1 | YES | NO | Residual cracks no greater than 1/16 inch. Cracks are mainly at the beam to wall interface, some limited flexural cracking. | Residual cracks greater than 1/8 inch and minor spalling of concrete. | Significant strength degradation (<0.8Vn), buckling or fracture of diagonal reinforcing, crushing of concrete. |  |  | 1 | 1 | 1 |  |  | 0.0137 | 0.0264 | 0.0428 |  |  | Not Specified | Not Specified | Not Specified |  |  | Not Specified | Not Specified | Not Specified |  |  | 0.21 | 0.33 | 0.74 |  |  | NO | YES | Not Rated | Not Rated | Not Rated | Not Rated | Epoxy inject cracks (200 to 240 inches in length). | Epoxy inject cracks (600 to 720 inches) and slab (300 inches), replace spalled concrete. | Chip away damaged concrete, attached mechanical couplers to the diagonal bars still embedded in the wall, replace damaged or fractured reinforcing. Replace damaged concrete. |  |  | NO | NO | NO |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | NO | YES |  |  | 0% | 0% | 25% |  |  | 0 | 0 | 0.5 |  |  | None | Not Given | By User | By User | John Wallace | none | none | none |  |  | No | None | YES
B1042.002b | B1042.002b | Concrete link beam, conventionally reinforced, aspect ratio between 2.0 and 4.0, beam < 16" wide and depth < 30" | None | Not Specified | Not applicable | Each | Each | Link Beam Chord Rotation | Radians | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 243 | EA 1 | YES | NO | Residual cracks no greater than 1/16 inch. Cracks are mainly at the beam to wall interface, some limited flexural cracking. | Residual cracks greater than 1/8 inch and minor spalling of concrete. | Significant strength degradation (<0.8Vn), buckling or fracture of diagonal reinforcing, crushing of concrete. |  |  | 1 | 1 | 1 |  |  | 0.0137 | 0.0264 | 0.0407 |  |  | Not Specified | Not Specified | Not Specified |  |  | Not Specified | Not Specified | Not Specified |  |  | 0.21 | 0.33 | 0.75 |  |  | NO | YES | Not Rated | Not Rated | Not Rated | Not Rated | Epoxy inject cracks (200 to 240 inches in length). | Epoxy inject cracks (600 to 720 inches) and slab (300 inches), replace spalled concrete. | Chip away damaged concrete, attached mechanical couplers to the diagonal bars still embedded in the wall, replace damaged or fractured reinforcing. Replace damaged concrete. |  |  | NO | NO | NO |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | NO | YES |  |  | 0% | 0% | 25% |  |  | 0 | 0 | 0.5 |  |  | None | Not Given | By User | By User | John Wallace | none | none | none |  |  | No | None | YES
B1042.011a | B1042.011a | Concrete link beam, diagonally reinforced, aspect ratio between 1.0 and 2.0, beam > 16" wide and depth < 30" | None | Not Specified | Not applicable | Each | Each | Link Beam Chord Rotation | Radians | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 244 | EA 1 | YES | NO | Residual cracks no greater than 1/16 inch. Cracks are mainly at the beam to wall interface, some limited flexural cracking. | Residual cracks greater than 1/8 inch and minor spalling of concrete. | Significant strength degradation (<0.8Vn), buckling or fracture of diagonal reinforcing, crushing of concrete. |  |  | 1 | 1 | 1 |  |  | 0.0179 | 0.0352 | 0.0543 |  |  | Not Specified | Not Specified | Not Specified |  |  | Not Specified | Not Specified | Not Specified |  |  | 0.38 | 0.44 | 0.95 |  |  | NO | YES | Not Rated | Not Rated | Not Rated | Not Rated | Epoxy inject cracks (200 to 240 inches in length). | Epoxy inject cracks (600 to 720 inches) and slab (300 inches), replace spalled concrete. | Chip away damaged concrete, attached mechanical couplers to the diagonal bars still embedded in the wall, replace damaged or fractured reinforcing. Replace damaged concrete. |  |  | NO | NO | NO |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | NO | YES |  |  | 0% | 0% | 25% |  |  | 0 | 0 | 0.5 |  |  | None | Not Given | By User | By User | John Wallace | none | none | none |  |  | No | None | YES
B1042.011b | B1042.011b | Concrete link beam, diagonally reinforced, aspect ratio between 2.0 and 4.0, beam > 16" wide and depth < 30" | None | Not Specified | Not applicable | Each | Each | Link Beam Chord Rotation | Radians | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 245 | EA 1 | YES | NO | Residual cracks no greater than 1/16 inch. Cracks are mainly at the beam to wall interface, some limited flexural cracking. | Residual cracks greater than 1/8 inch and minor spalling of concrete. | Significant strength degradation (<0.8Vn), buckling or fracture of diagonal reinforcing, crushing of concrete. |  |  | 1 | 1 | 1 |  |  | 0.0203 | 0.0394 | 0.0602 |  |  | Not Specified | Not Specified | Not Specified |  |  | Not Specified | Not Specified | Not Specified |  |  | 0.39 | 0.35 | 1 |  |  | NO | YES | Not Rated | Not Rated | Not Rated | Not Rated | Epoxy inject cracks (200 to 240 inches in length). | Epoxy inject cracks (600 to 720 inches) and slab (300 inches), replace spalled concrete. | Chip away damaged concrete, attached mechanical couplers to the diagonal bars still embedded in the wall, replace damaged or fractured reinforcing. Replace damaged concrete. |  |  | NO | NO | NO |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | NO | YES |  |  | 0% | 0% | 25% |  |  | 0 | 0 | 0.5 |  |  | None | Not Given | By User | By User | John Wallace | none | none | none |  |  | No | None | YES
B1042.012a | B1042.012a | Concrete link beam, conventionally reinforced, aspect ratio between 1.0 and 2.0, beam > 16" wide and depth < 30" | None | Not Specified | Not applicable | Each | Each | Link Beam Chord Rotation | Radians | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 246 | EA 1 | YES | NO | Residual cracks no greater than 1/16 inch. Cracks are mainly at the beam to wall interface, some limited flexural cracking. | Residual cracks greater than 1/8 inch and minor spalling of concrete. | Significant strength degradation (<0.8Vn), buckling or fracture of diagonal reinforcing, crushing of concrete. |  |  | 1 | 1 | 1 |  |  | 0.0137 | 0.0264 | 0.0428 |  |  | Not Specified | Not Specified | Not Specified |  |  | Not Specified | Not Specified | Not Specified |  |  | 0.21 | 0.33 | 0.74 |  |  | NO | YES | Not Rated | Not Rated | Not Rated | Not Rated | Epoxy inject cracks (200 to 240 inches in length). | Epoxy inject cracks (600 to 720 inches) and slab (300 inches), replace spalled concrete. | Chip away damaged concrete, attached mechanical couplers to the diagonal bars still embedded in the wall, replace damaged or fractured reinforcing. Replace damaged concrete. |  |  | NO | NO | NO |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | NO | YES |  |  | 0% | 0% | 25% |  |  | 0 | 0 | 0.5 |  |  | None | Not Given | By User | By User | John Wallace | none | none | none |  |  | No | None | YES
B1042.012b | B1042.012b | Concrete link beam, conventionally reinforced, aspect ratio between 2.0 and 4.0, beam > 16" wide and depth < 30" | None | Not Specified | Not applicable | Each | Each | Link Beam Chord Rotation | Radians | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 247 | EA 1 | YES | NO | Residual cracks no greater than 1/16 inch. Cracks are mainly at the beam to wall interface, some limited flexural cracking. | Residual cracks greater than 1/8 inch and minor spalling of concrete. | Significant strength degradation (<0.8Vn), buckling or fracture of diagonal reinforcing, crushing of concrete. |  |  | 1 | 1 | 1 |  |  | 0.0137 | 0.0264 | 0.0407 |  |  | Not Specified | Not Specified | Not Specified |  |  | Not Specified | Not Specified | Not Specified |  |  | 0.21 | 0.33 | 0.75 |  |  | NO | YES | Not Rated | Not Rated | Not Rated | Not Rated | Epoxy inject cracks (200 to 240 inches in length). | Epoxy inject cracks (600 to 720 inches) and slab (300 inches), replace spalled concrete. | Chip away damaged concrete, attached mechanical couplers to the diagonal bars still embedded in the wall, replace damaged or fractured reinforcing. Replace damaged concrete. |  |  | NO | NO | NO |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | NO | YES |  |  | 0% | 0% | 25% |  |  | 0 | 0 | 0.5 |  |  | None | Not Given | By User | By User | John Wallace | none | none | none |  |  | No | None | YES
B1042.021a | B1042.021a | Concrete link beam, diagonally reinforced, aspect ratio between 1.0 and 2.0, beam > 24" wide and depth < 30" | None | Not Specified | Not applicable | Each | Each | Link Beam Chord Rotation | Radians | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 248 | EA 1 | YES | NO | Residual cracks no greater than 1/16 inch. Cracks are mainly at the beam to wall interface, some limited flexural cracking. | Residual cracks greater than 1/8 inch and minor spalling of concrete. | Significant strength degradation (<0.8Vn), buckling or fracture of diagonal reinforcing, crushing of concrete. |  |  | 1 | 1 | 1 |  |  | 0.0179 | 0.0352 | 0.0543 |  |  | Not Specified | Not Specified | Not Specified |  |  | Not Specified | Not Specified | Not Specified |  |  | 0.38 | 0.44 | 0.95 |  |  | NO | YES | Not Rated | Not Rated | Not Rated | Not Rated | Epoxy inject cracks (200 to 240 inches in length). | Epoxy inject cracks (600 to 720 inches) and slab (300 inches), replace spalled concrete. | Chip away damaged concrete, attached mechanical couplers to the diagonal bars still embedded in the wall, replace damaged or fractured reinforcing. Replace damaged concrete. |  |  | NO | NO | NO |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | NO | YES |  |  | 0% | 0% | 25% |  |  | 0 | 0 | 0.5 |  |  | None | Not Given | By User | By User | John Wallace | none | none | none |  |  | No | None | YES
B1042.021b | B1042.021b | Concrete link beam, diagonally reinforced, aspect ratio between 2.0 and 4.0, beam > 24" wide and depth < 30" | None | Not Specified | Not applicable | Each | Each | Link Beam Chord Rotation | Radians | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 249 | EA 1 | YES | NO | Residual cracks no greater than 1/16 inch. Cracks are mainly at the beam to wall interface, some limited flexural cracking. | Residual cracks greater than 1/8 inch and minor spalling of concrete. | Significant strength degradation (<0.8Vn), buckling or fracture of diagonal reinforcing, crushing of concrete. |  |  | 1 | 1 | 1 |  |  | 0.0203 | 0.0394 | 0.0602 |  |  | Not Specified | Not Specified | Not Specified |  |  | Not Specified | Not Specified | Not Specified |  |  | 0.39 | 0.35 | 1 |  |  | NO | YES | Not Rated | Not Rated | Not Rated | Not Rated | Epoxy inject cracks (200 to 240 inches in length). | Epoxy inject cracks (600 to 720 inches) and slab (300 inches), replace spalled concrete. | Chip away damaged concrete, attached mechanical couplers to the diagonal bars still embedded in the wall, replace damaged or fractured reinforcing. Replace damaged concrete. |  |  | NO | NO | NO |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | NO | YES |  |  | 0% | 0% | 25% |  |  | 0 | 0 | 0.5 |  |  | None | Not Given | By User | By User | John Wallace | none | none | none |  |  | No | None | YES
B1042.022a | B1042.022a | Concrete link beam, conventionally reinforced, aspect ratio between 1.0 and 2.0, beam > 24" wide and depth < 30" | None | Not Specified | Not applicable | Each | Each | Link Beam Chord Rotation | Radians | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 250 | EA 1 | YES | NO | Residual cracks no greater than 1/16 inch. Cracks are mainly at the beam to wall interface, some limited flexural cracking. | Residual cracks greater than 1/8 inch and minor spalling of concrete. | Significant strength degradation (<0.8Vn), buckling or fracture of diagonal reinforcing, crushing of concrete. |  |  | 1 | 1 | 1 |  |  | 0.0137 | 0.0264 | 0.0428 |  |  | Not Specified | Not Specified | Not Specified |  |  | Not Specified | Not Specified | Not Specified |  |  | 0.21 | 0.33 | 0.74 |  |  | NO | YES | Not Rated | Not Rated | Not Rated | Not Rated | Epoxy inject cracks (200 to 240 inches in length). | Epoxy inject cracks (600 to 720 inches) and slab (300 inches), replace spalled concrete. | Chip away damaged concrete, attached mechanical couplers to the diagonal bars still embedded in the wall, replace damaged or fractured reinforcing. Replace damaged concrete. |  |  | NO | NO | NO |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | NO | YES |  |  | 0% | 0% | 25% |  |  | 0 | 0 | 0.5 |  |  | None | Not Given | By User | By User | John Wallace | none | none | none |  |  | No | None | YES
B1042.022b | B1042.022b | Concrete link beam, conventionally reinforced, aspect ratio between 2.0 and 4.0, beam > 24" wide and depth < 30" | None | Not Specified | Not applicable | Each | Each | Link Beam Chord Rotation | Radians | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 251 | EA 1 | YES | NO | Residual cracks no greater than 1/16 inch. Cracks are mainly at the beam to wall interface, some limited flexural cracking. | Residual cracks greater than 1/8 inch and minor spalling of concrete. | Significant strength degradation (<0.8Vn), buckling or fracture of diagonal reinforcing, crushing of concrete. |  |  | 1 | 1 | 1 |  |  | 0.0137 | 0.0264 | 0.0407 |  |  | Not Specified | Not Specified | Not Specified |  |  | Not Specified | Not Specified | Not Specified |  |  | 0.21 | 0.33 | 0.75 |  |  | NO | YES | Not Rated | Not Rated | Not Rated | Not Rated | Epoxy inject cracks (200 to 240 inches in length). | Epoxy inject cracks (600 to 720 inches) and slab (300 inches), replace spalled concrete. | Chip away damaged concrete, attached mechanical couplers to the diagonal bars still embedded in the wall, replace damaged or fractured reinforcing. Replace damaged concrete. |  |  | NO | NO | NO |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | NO | YES |  |  | 0% | 0% | 25% |  |  | 0 | 0 | 0.5 |  |  | None | Not Given | By User | By User | John Wallace | none | none | none |  |  | No | None | YES
B1051.001 | B1051.001 | Ordinary reinforced masonry walls with partially grouted cells, shear dominated, 4" to 6"' thick, up to 12 foot tall | Costing for each 100 ft^2 Wall Panel | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 252 | SF 100 | NO | NO | First occurrence of major diagonal cracks. Cracks remain closed with hardly noticeable residual crack widths after load removal. | Wide diagonal cracks with typically one or more cracks in each direction. Crushing or spalling at wall toes. |  |  |  | 1 | 1 |  |  |  | 0.002 | 0.0033 |  |  |  | Not Specified | Not Specified |  |  |  | 0.86 | 0.77 |  |  |  | 0.86 | 0.77 |  |  |  | NO | YES | Marginal | Average | Superior | Superior | Grout wall. Epoxy injection. Paint each side. | Shore. Demolish existing wall. Construct new wall. |  |  |  | NO | NO |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | YES |  |  |  | 0% | 25% |  |  |  | 0 | 0.5 |  |  |  | None | Not Given | By User | By User | Benson Shing | B1051.001-DS1-1.JPG | B1051.001-DS2-1.JPG |  |  |  | No | None | YES
B1051.002 | B1051.002 | Ordinary reinforced masonry walls with partially grouted cells, shear dominated, 4" to 6"' thick, greater than 12 foot tall | Costing for each 225 ft^2 Wall Panel | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 253 | SF 225 | NO | NO | First occurrence of major diagonal cracks. Cracks remain closed with hardly noticeable residual crack widths after load removal. | Wide diagonal cracks with typically one or more cracks in each direction. Crushing or spalling at wall toes. |  |  |  | 1 | 1 |  |  |  | 0.002 | 0.0033 |  |  |  | Not Specified | Not Specified |  |  |  | 0.86 | 0.77 |  |  |  | 0.86 | 0.77 |  |  |  | NO | YES | Marginal | Average | Superior | Superior | Grout wall. Epoxy injection. Paint each side. | Shore. Demolish existing wall. Construct new wall. |  |  |  | NO | NO |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | YES |  |  |  | 0% | 25% |  |  |  | 0 | 0.5 |  |  |  | None | Not Given | By User | By User | Benson Shing | B1051.001-DS1-1.JPG | B1051.001-DS2-1.JPG |  |  |  | No | None | YES
B1051.003 | B1051.003 | Ordinary reinforced masonry walls with partially grouted cells, 4" to 6" thick, flexure dominated up to 12' tall | Costing for each 100 ft^2 Wall Panel | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 254 | SF 100 | NO | NO | A few flexural and shear cracks with hardly noticeable residual crack widths. Slight yielding of extreme vertical reinforcement. No spalling. No fracture or buckling of vertical reinforcement. No structurally significant damage. | Numerous flexural and diagonal cracks with residual crack widths less than 1/64 in. Mild toe crushing with vertical cracks or light spalling at wall toes. No fracture or buckling of reinforcement. Small residual deformation. | Severe flexural cracks with residual crack widths greater than 1/32 in. Severe toe crushing and spalling. Fracture or buckling of vertical reinforcement. Significant residual deformation. |  |  | 1 | 1 | 1 |  |  | 0.0018 | 0.0051 | 0.0086 |  |  | Not Specified | Not Specified | Not Specified |  |  | 0.73 | 0.65 | 0.56 |  |  | 0.73 | 0.65 | 0.56 |  |  | NO | YES | Not Rated | Marginal | Average | Superior | Cosmetic repair. Patch cracks and paint each side. | Remove loose masonry. Patch spalls with non-shrink grout. Grout wall. Epoxy injection. Paint each side. | Shore. - Demolish existing wall. - Construct new wall. |  |  | NO | NO | NO |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | NO | YES |  |  | 0% | 0% | 25% |  |  | 0 | 0 | 0.5 |  |  | None | Not Given | By User | By User | Benson Shing | none | B1051.003-DS2-1.JPG | B1051.003-DS3-1.JPG |  |  | No | None | YES
B1051.004 | B1051.004 | Ordinary reinforced masonry walls with partially grouted cells, 4" to 6" thick, flexure dominated greater than 12' tall | Costing for each 225 ft^2 Wall Panel | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 255 | SF 225 | NO | NO | A few flexural and shear cracks with hardly noticeable residual crack widths. Slight yielding of extreme vertical reinforcement. No spalling. No fracture or buckling of vertical reinforcement. No structurally significant damage. | Numerous flexural and diagonal cracks with residual crack widths less than 1/64 in. Mild toe crushing with vertical cracks or light spalling at wall toes. No fracture or buckling of reinforcement. Small residual deformation. | Severe flexural cracks with residual crack widths greater than 1/32 in. Severe toe crushing and spalling. Fracture or buckling of vertical reinforcement. Significant residual deformation. |  |  | 1 | 1 | 1 |  |  | 0.0018 | 0.0051 | 0.0086 |  |  | Not Specified | Not Specified | Not Specified |  |  | 0.73 | 0.65 | 0.56 |  |  | 0.73 | 0.65 | 0.56 |  |  | NO | YES | Not Rated | Marginal | Average | Superior | Cosmetic repair. Patch cracks and paint each side. | Remove loose masonry. Patch spalls with non-shrink grout. Grout wall. Epoxy injection. Paint each side. | Shore. - Demolish existing wall. - Construct new wall. |  |  | NO | NO | NO |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | NO | YES |  |  | 0% | 0% | 25% |  |  | 0 | 0 | 0.5 |  |  | None | Not Given | By User | By User | Benson Shing | none | B1051.003-DS2-1.JPG | B1051.003-DS3-1.JPG |  |  | No | None | YES
B1051.011 | B1051.011 | Ordinary reinforced masonry walls with partially grouted cells, shear dominated, 8" to 12"' thick, up to 12 foot tall | Costing for each 100 ft^2 Wall Panel | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 256 | SF 100 | NO | NO | First occurrence of major diagonal cracks. Cracks remain closed with hardly noticeable residual crack widths after load removal. | Wide diagonal cracks with typically one or more cracks in each direction. Crushing or spalling at wall toes. |  |  |  | 1 | 1 |  |  |  | 0.002 | 0.0033 |  |  |  | Not Specified | Not Specified |  |  |  | 0.86 | 0.77 |  |  |  | 0.86 | 0.77 |  |  |  | NO | YES | Not Rated | Marginal | Average | Superior | Grout wall. Epoxy injection. Paint each side. | Shore. Demolish existing wall. Construct new wall. |  |  |  | NO | NO |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | YES |  |  |  | 0% | 25% |  |  |  | 0 | 0.5 |  |  |  | None | Not Given | By User | By User | Benson Shing | B1051.001-DS1-1.JPG | B1051.001-DS2-1.JPG |  |  |  | No | None | YES
B1051.012 | B1051.012 | Ordinary reinforced masonry walls with partially grouted cells, shear dominated, 8" to 12"' thick, greater than 12 foot tall | Costing for each 225 ft^2 Wall Panel | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 257 | SF 225 | NO | NO | First occurrence of major diagonal cracks. Cracks remain closed with hardly noticeable residual crack widths after load removal. | Wide diagonal cracks with typically one or more cracks in each direction. Crushing or spalling at wall toes. |  |  |  | 1 | 1 |  |  |  | 0.002 | 0.0033 |  |  |  | Not Specified | Not Specified |  |  |  | 0.86 | 0.77 |  |  |  | 0.86 | 0.77 |  |  |  | NO | YES | Not Rated | Marginal | Average | Superior | Grout wall. Epoxy injection. Paint each side. | Shore. Demolish existing wall. Construct new wall. |  |  |  | NO | NO |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | YES |  |  |  | 0% | 25% |  |  |  | 0 | 0.5 |  |  |  | None | Not Given | By User | By User | Benson Shing | B1051.001-DS1-1.JPG | B1051.001-DS2-1.JPG |  |  |  | No | None | YES
B1051.013 | B1051.013 | Ordinary reinforced masonry walls with partially grouted cells, 8" to 12" thick, flexure dominated up to 12' tall | Costing for each 100 ft^2 Wall Panel, | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 258 | SF 100 | NO | NO | A few flexural and shear cracks with hardly noticeable residual crack widths. Slight yielding of extreme vertical reinforcement. No spalling. No fracture or buckling of vertical reinforcement. No structurally significant damage. | Numerous flexural and diagonal cracks with residual crack widths less than 1/64 in. Mild toe crushing with vertical cracks or light spalling at wall toes. No fracture or buckling of reinforcement. Small residual deformation. | Severe flexural cracks with residual crack widths greater than 1/32 in. Severe toe crushing and spalling. Fracture or buckling of vertical reinforcement. Significant residual deformation. |  |  | 1 | 1 | 1 |  |  | 0.0018 | 0.0051 | 0.0086 |  |  | Not Specified | Not Specified | Not Specified |  |  | 0.73 | 0.65 | 0.56 |  |  | 0.73 | 0.65 | 0.56 |  |  | NO | YES | Not Rated | Marginal | Average | Superior | Cosmetic repair. Patch cracks and paint each side. | Remove loose masonry. Patch spalls with non-shrink grout. Grout wall. Epoxy injection. Paint each side. | Shore. - Demolish existing wall. - Construct new wall. |  |  | NO | NO | NO |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | NO | YES |  |  | 0% | 0% | 25% |  |  | 0 | 0 | 0.5 |  |  | None | Not Given | By User | By User | Benson Shing | none | B1051.003-DS2-1.JPG | B1051.003-DS3-1.JPG |  |  | No | None | YES
B1051.014 | B1051.014 | Ordinary reinforced masonry walls with partially grouted cells, 8" to 12" thick, flexure dominated greater than 12' tall | Costing for each 225 ft^2 Wall Panel | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 259 | SF 225 | NO | NO | A few flexural and shear cracks with hardly noticeable residual crack widths. Slight yielding of extreme vertical reinforcement. No spalling. No fracture or buckling of vertical reinforcement. No structurally significant damage. | Numerous flexural and diagonal cracks with residual crack widths less than 1/64 in. Mild toe crushing with vertical cracks or light spalling at wall toes. No fracture or buckling of reinforcement. Small residual deformation. | Severe flexural cracks with residual crack widths greater than 1/32 in. Severe toe crushing and spalling. Fracture or buckling of vertical reinforcement. Significant residual deformation. |  |  | 1 | 1 | 1 |  |  | 0.0018 | 0.0051 | 0.0086 |  |  | Not Specified | Not Specified | Not Specified |  |  | 0.73 | 0.65 | 0.56 |  |  | 0.73 | 0.65 | 0.56 |  |  | NO | YES | Not Rated | Marginal | Average | Superior | Cosmetic repair. Patch cracks and paint each side. | Remove loose masonry. Patch spalls with non-shrink grout. Grout wall. Epoxy injection. Paint each side. | Shore. - Demolish existing wall. - Construct new wall. |  |  | NO | NO | NO |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | NO | YES |  |  | 0% | 0% | 25% |  |  | 0 | 0 | 0.5 |  |  | None | Not Given | By User | By User | Benson Shing | none | B1051.003-DS2-1.JPG | B1051.003-DS3-1.JPG |  |  | No | None | YES
B1051.021 | B1051.021 | Ordinary reinforced masonry walls with partially grouted cells, shear dominated, 16" thick, up to 12 foot tall | Costing for each 100 ft^2 Wall Panel | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 260 | SF 100 | NO | NO | First occurrence of major diagonal cracks. Cracks remain closed with hardly noticeable residual crack widths after load removal. | Wide diagonal cracks with typically one or more cracks in each direction. Crushing or spalling at wall toes. |  |  |  | 1 | 1 |  |  |  | 0.002 | 0.0033 |  |  |  | Not Specified | Not Specified |  |  |  | 0.86 | 0.77 |  |  |  | 0.86 | 0.77 |  |  |  | NO | YES | Not Rated | Marginal | Average | Superior | Grout wall. Epoxy injection. Paint each side. | Shore. Demolish existing wall. Construct new wall. |  |  |  | NO | NO |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | YES |  |  |  | 0% | 25% |  |  |  | 0 | 0.5 |  |  |  | None | Not Given | By User | By User | Benson Shing | B1051.001-DS1-1.JPG | B1051.001-DS2-1.JPG |  |  |  | No | None | YES
B1051.022 | B1051.022 | Ordinary reinforced masonry walls with partially grouted cells, shear dominated,16"' thick, greater than 12 foot tall | Costing for each 225 ft^2 Wall Panel | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 261 | SF 225 | NO | NO | First occurrence of major diagonal cracks. Cracks remain closed with hardly noticeable residual crack widths after load removal. | Wide diagonal cracks with typically one or more cracks in each direction. Crushing or spalling at wall toes. |  |  |  | 1 | 1 |  |  |  | 0.002 | 0.0033 |  |  |  | Not Specified | Not Specified |  |  |  | 0.86 | 0.77 |  |  |  | 0.86 | 0.77 |  |  |  | NO | YES | Not Rated | Marginal | Average | Superior | Grout wall. Epoxy injection. Paint each side. | Shore. Demolish existing wall. Construct new wall. |  |  |  | NO | NO |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | YES |  |  |  | 0% | 25% |  |  |  | 0 | 0.5 |  |  |  | None | Not Given | By User | By User | Benson Shing | B1051.001-DS1-1.JPG | B1051.001-DS2-1.JPG |  |  |  | No | None | YES
B1051.023 | B1051.023 | Ordinary reinforced masonry walls with partially grouted cells, 16" thick, flexure dominated up to 12' tall | Costing for each 100 ft^2 Wall Panel | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 262 | SF 100 | NO | NO | A few flexural and shear cracks with hardly noticeable residual crack widths. Slight yielding of extreme vertical reinforcement. No spalling. No fracture or buckling of vertical reinforcement. No structurally significant damage. | Numerous flexural and diagonal cracks with residual crack widths less than 1/64 in. Mild toe crushing with vertical cracks or light spalling at wall toes. No fracture or buckling of reinforcement. Small residual deformation. | Severe flexural cracks with residual crack widths greater than 1/32 in. Severe toe crushing and spalling. Fracture or buckling of vertical reinforcement. Significant residual deformation. |  |  | 1 | 1 | 1 |  |  | 0.0018 | 0.0051 | 0.0086 |  |  | Not Specified | Not Specified | Not Specified |  |  | 0.73 | 0.65 | 0.56 |  |  | 0.73 | 0.65 | 0.56 |  |  | NO | YES | Not Rated | Marginal | Average | Superior | Cosmetic repair. Patch cracks and paint each side. | Remove loose masonry. Patch spalls with non-shrink grout. Grout wall. Epoxy injection. Paint each side. | Shore. - Demolish existing wall. - Construct new wall. |  |  | NO | NO | NO |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | NO | YES |  |  | 0% | 0% | 25% |  |  | 0 | 0 | 0.5 |  |  | None | Not Given | By User | By User | Benson Shing | none | B1051.003-DS2-1.JPG | B1051.003-DS3-1.JPG |  |  | No | None | YES
B1051.024 | B1051.024 | Ordinary reinforced masonry walls with partially grouted cells, 16" thick, flexure dominated greater than 12' tall | Costing for each 225 ft^2 Wall Panel | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 263 | SF 225 | NO | NO | A few flexural and shear cracks with hardly noticeable residual crack widths. Slight yielding of extreme vertical reinforcement. No spalling. No fracture or buckling of vertical reinforcement. No structurally significant damage. | Numerous flexural and diagonal cracks with residual crack widths less than 1/64 in. Mild toe crushing with vertical cracks or light spalling at wall toes. No fracture or buckling of reinforcement. Small residual deformation. | Severe flexural cracks with residual crack widths greater than 1/32 in. Severe toe crushing and spalling. Fracture or buckling of vertical reinforcement. Significant residual deformation. |  |  | 1 | 1 | 1 |  |  | 0.0018 | 0.0051 | 0.0086 |  |  | Not Specified | Not Specified | Not Specified |  |  | 0.73 | 0.65 | 0.56 |  |  | 0.73 | 0.65 | 0.56 |  |  | NO | YES | Not Rated | Marginal | Average | Superior | Cosmetic repair. Patch cracks and paint each side. | Remove loose masonry. Patch spalls with non-shrink grout. Grout wall. Epoxy injection. Paint each side. | Shore. - Demolish existing wall. - Construct new wall. |  |  | NO | NO | NO |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | NO | YES |  |  | 0% | 0% | 25% |  |  | 0 | 0 | 0.5 |  |  | None | Not Given | By User | By User | Benson Shing | none | B1051.003-DS2-1.JPG | B1051.003-DS3-1.JPG |  |  | No | None | YES
B1052.001 | B1052.001 | Special reinforced masonry walls with fully grouted cells, 8" or 12" thick, shear dominated, up t o12' tall | Costing for each 100 ft^2 Wall Panel | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 264 | SF 100 | NO | NO | First occurrence of major diagonal cracks. Cracks remain closed with hardly noticeable residual crack widths after load removal. | Wide diagonal cracks with typically one or more cracks in each direction. Crushing or spalling at wall toes. |  |  |  | 1 | 1 |  |  |  | 0.0036 | 0.0059 |  |  |  | 0.54 | 0.44 |  |  |  | 0.24 | 0.26 |  |  |  | 0.59 | 0.51 |  |  |  | NO | YES | Not Rated | Marginal | Average | Superior | Epoxy injection. Paint each side. | Shore. Demolish existing wall. Construct new wall. |  |  |  | NO | NO |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | YES |  |  |  | 0% | 25% |  |  |  | 0 | 0.5 |  |  |  | None | Not Given | By User | By User | Benson Shing | B1051.001-DS1-1.JPG | B1051.001-DS2-1.JPG |  |  |  | No | None | YES
B1052.002 | B1052.002 | Special reinforced masonry walls with fully grouted cells, 8" or 12" thick, shear dominated, greater than 12' tall | Costing for each 225 ft^2 Wall Panel | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 265 | SF 225 | NO | NO | First occurrence of major diagonal cracks. Cracks remain closed with hardly noticeable residual crack widths after load removal. | Wide diagonal cracks with typically one or more cracks in each direction. Crushing or spalling at wall toes. |  |  |  | 1 | 1 |  |  |  | 0.0036 | 0.0059 |  |  |  | 0.54 | 0.44 |  |  |  | 0.24 | 0.26 |  |  |  | 0.59 | 0.51 |  |  |  | NO | YES | Not Rated | Marginal | Average | Superior | Epoxy injection. Paint each side. | Shore. Demolish existing wall. Construct new wall. |  |  |  | NO | NO |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | YES |  |  |  | 0% | 25% |  |  |  | 0 | 0.5 |  |  |  | None | Not Given | By User | By User | Benson Shing | B1051.001-DS1-1.JPG | B1051.001-DS2-1.JPG |  |  |  | No | None | YES
B1052.003 | B1052.003 | Special reinforced masonry walls with fully grouted cells, 8" to 12" thick, flexure dominated up to 12' tall | Costing for each 100 ft^2 Wall Panel | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 266 | SF 100 | NO | NO | A few flexural and shear cracks with hardly noticeable residual crack widths. Slight yielding of extreme vertical reinforcement. No spalling. No fracture or buckling of vertical reinforcement. No structurally significant damage. | Numerous flexural and diagonal cracks with residual crack widths less than 1/64 in. Mild toe crushing with vertical cracks or light spalling at wall toes. No fracture or buckling of reinforcement. Small residual deformation. | Severe flexural cracks with residual crack widths greater than 1/32 in. Severe toe crushing and spalling. Fracture or buckling of vertical reinforcement. Significant residual deformation. |  |  | 1 | 1 | 1 |  |  | 0.0031 | 0.009 | 0.0151 |  |  | 0.4 | 0.27 | 0.2 |  |  | 0.25 | 0.25 | 0.25 |  |  | 0.47 | 0.4 | 0.32 |  |  | NO | YES | Not Rated | Marginal | Average | Superior | Cosmetic repair. Patch cracks and paint each side. | Epoxy injection to repair cracks. Remove loose masonry. Patch spalls with non-shrink grout. Paint each side. | Shore. - Demolish existing wall. - Construct new wall. |  |  | NO | NO | NO |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | NO | YES |  |  | 0% | 0% | 25% |  |  | 0 | 0 | 0.5 |  |  | None | Not Given | By User | By User | Benson Shing | none | B1051.003-DS2-1.JPG | B1051.003-DS3-1.JPG |  |  | No | None | YES
B1052.004 | B1052.004 | Special reinforced masonry walls with fully grouted cells, 8" to 12" thick, flexure dominated greater than 12' tall | Costing for each 225 ft^2 Wall Panel | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 267 | SF 225 | NO | NO | A few flexural and shear cracks with hardly noticeable residual crack widths. Slight yielding of extreme vertical reinforcement. No spalling. No fracture or buckling of vertical reinforcement. No structurally significant damage. | Numerous flexural and diagonal cracks with residual crack widths less than 1/64 in. Mild toe crushing with vertical cracks or light spalling at wall toes. No fracture or buckling of reinforcement. Small residual deformation. | Severe flexural cracks with residual crack widths greater than 1/32 in. Severe toe crushing and spalling. Fracture or buckling of vertical reinforcement. Significant residual deformation. |  |  | 1 | 1 | 1 |  |  | 0.0031 | 0.009 | 0.0151 |  |  | 0.4 | 0.27 | 0.2 |  |  | 0.25 | 0.25 | 0.25 |  |  | 0.47 | 0.4 | 0.32 |  |  | NO | YES | Not Rated | Marginal | Average | Superior | Cosmetic repair. Patch cracks and paint each side. | Epoxy injection to repair cracks. Remove loose masonry. Patch spalls with non-shrink grout. Paint each side. | Shore. - Demolish existing wall. - Construct new wall. |  |  | NO | NO | NO |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | NO | YES |  |  | 0% | 0% | 25% |  |  | 0 | 0 | 0.5 |  |  | None | Not Given | By User | By User | Benson Shing | none | B1051.003-DS2-1.JPG | B1051.003-DS3-1.JPG |  |  | No | None | YES
B1052.011 | B1052.011 | Special reinforced masonry walls with fully grouted cells, 16" thick, shear dominated, up to 12' tall | Costing for each 100 ft^2 Wall Panel | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 268 | SF 100 | NO | NO | First occurrence of major diagonal cracks. Cracks remain closed with hardly noticeable residual crack widths after load removal. | Wide diagonal cracks with typically one or more cracks in each direction. Crushing or spalling at wall toes. |  |  |  | 1 | 1 |  |  |  | 0.0036 | 0.0059 |  |  |  | 0.54 | 0.44 |  |  |  | 0.24 | 0.26 |  |  |  | 0.59 | 0.51 |  |  |  | NO | YES | Not Rated | Marginal | Average | Superior | Epoxy injection at cracks. Paint each side. | Shore. Demolish existing wall. Construct new wall. |  |  |  | NO | NO |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | YES |  |  |  | 0% | 25% |  |  |  | 0 | 0.5 |  |  |  | None | Not Given | By User | By User | Benson Shing | B1051.001-DS1-1.JPG | B1051.001-DS2-1.JPG |  |  |  | No | None | YES
B1052.012 | B1052.012 | Special reinforced masonry walls with fully grouted cells, 16" thick, shear dominated, greater than 12' tall | Costing for each 225 ft^2 Wall Panel | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 269 | SF 225 | NO | NO | First occurrence of major diagonal cracks. Cracks remain closed with hardly noticeable residual crack widths after load removal. | Wide diagonal cracks with typically one or more cracks in each direction. Crushing or spalling at wall toes. |  |  |  | 1 | 1 |  |  |  | 0.0036 | 0.0059 |  |  |  | 0.54 | 0.44 |  |  |  | 0.24 | 0.26 |  |  |  | 0.59 | 0.51 |  |  |  | NO | YES | Not Rated | Marginal | Average | Superior | Epoxy injection at cracks. Paint each side. | Shore. Demolish existing wall. Construct new wall. |  |  |  | NO | NO |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | YES |  |  |  | 0% | 25% |  |  |  | 0 | 0.5 |  |  |  | None | Not Given | By User | By User | Benson Shing | B1051.001-DS1-1.JPG | B1051.001-DS2-1.JPG |  |  |  | No | None | YES
B1052.013 | B1052.013 | Special reinforced masonry walls with fully grouted cells, 16" thick, flexure dominated up to 12' tall | Costing for each 100 ft^2 Wall Panel | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 270 | SF 100 | NO | NO | A few flexural and shear cracks with hardly noticeable residual crack widths. Slight yielding of extreme vertical reinforcement. No spalling. No fracture or buckling of vertical reinforcement. No structurally significant damage. | Numerous flexural and diagonal cracks with residual crack widths less than 1/64 in. Mild toe crushing with vertical cracks or light spalling at wall toes. No fracture or buckling of reinforcement. Small residual deformation. | Severe flexural cracks with residual crack widths greater than 1/32 in. Severe toe crushing and spalling. Fracture or buckling of vertical reinforcement. Significant residual deformation. |  |  | 1 | 1 | 1 |  |  | 0.0031 | 0.009 | 0.0151 |  |  | 0.4 | 0.27 | 0.2 |  |  | 0.25 | 0.25 | 0.25 |  |  | 0.47 | 0.4 | 0.32 |  |  | NO | YES | Not Rated | Marginal | Average | Superior | Cosmetic repair. Patch cracks and paint each side. | Epoxy injection to repair cracks. Remove loose masonry. Patch spalls with non-shrink grout. Paint each side. | Shore. - Demolish existing wall. - Construct new wall. |  |  | NO | NO | NO |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | NO | YES |  |  | 0% | 0% | 25% |  |  | 0 | 0 | 0.5 |  |  | None | Not Given | By User | By User | Benson Shing | none | B1051.003-DS2-1.JPG | B1051.003-DS3-1.JPG |  |  | No | None | YES
B1052.014 | B1052.014 | Special reinforced masonry walls with fully grouted cells, 16" thick, flexure dominated greater than 12' tall | Costing for each 225 ft^2 Wall Panel | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 271 | SF 225 | NO | NO | A few flexural and shear cracks with hardly noticeable residual crack widths. Slight yielding of extreme vertical reinforcement. No spalling. No fracture or buckling of vertical reinforcement. No structurally significant damage. | Numerous flexural and diagonal cracks with residual crack widths less than 1/64 in. Mild toe crushing with vertical cracks or light spalling at wall toes. No fracture or buckling of reinforcement. Small residual deformation. | Severe flexural cracks with residual crack widths greater than 1/32 in. Severe toe crushing and spalling. Fracture or buckling of vertical reinforcement. Significant residual deformation. |  |  | 1 | 1 | 1 |  |  | 0.0031 | 0.009 | 0.0151 |  |  | 0.4 | 0.27 | 0.2 |  |  | 0.25 | 0.25 | 0.25 |  |  | 0.47 | 0.4 | 0.32 |  |  | NO | YES | Not Rated | Marginal | Average | Superior | Cosmetic repair. Patch cracks and paint each side. | Epoxy injection to repair cracks. Remove loose masonry. Patch spalls with non-shrink grout. Paint each side. | Shore. - Demolish existing wall. - Construct new wall. |  |  | NO | NO | NO |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | NO | YES |  |  | 0% | 0% | 25% |  |  | 0 | 0 | 0.5 |  |  | None | Not Given | By User | By User | Benson Shing | none | B1051.003-DS2-1.JPG | B1051.003-DS3-1.JPG |  |  | No | None | YES
B1061.001a | B1061.001a | Cold formed steel walls with wood structural panel sheathing, interior - gypsum board | Costing for each 100 ft^2 Wall Panel. Assumed framing: 38 mil cold formed steel framing with 7/16 OSB and 3/8 plywood panel sheathing with overturning restraint at each end of the wall per AISI design standard. No. 8 screws 2" to 6" OC at perimeter and 12" OC EW in field. | High quality | Overturning restraint at each end of wall. | Each | Each | Story Drift Ratio | Unit less | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 272 | SF 100 | NO | NO | Sheathing faster pull through or tear out. (20% of fasteners.) | Failure of structural panels. | Failure of wall. |  |  | 1 | 1 | 1 |  |  | 0.004 | 0.0226 | 0.0267 |  |  | 0.4 | 0.3 | 0.25 |  |  | 0.1 | 0.1 | 0.1 |  |  | 0.4 | 0.3 | 0.25 |  |  | NO | YES | Superior | Superior | Superior | Superior | Remove damaged wall, ceilings, mechanical, electrical, and office furniture / equipment. Temporarily protect floor and provide dust curtains. Modify mechanical and electrical as required for repair work. Replace 20% of fasteners, replace gypsum wall board, tape and sand, repaint. | Remove damaged wall, ceilings, mechanical, electrical, and office furniture / equipment. Temporarily protect floor and provide dust curtains. Modify mechanical and electrical as required for repair work. Replace sheathing, replace gypsum wall board, tape and sand, repaint. | Remove damaged wall, ceilings, mechanical, electrical, and office furniture / equipment. Temporarily protect floor and provide dust curtains. Provide shoring. Modify mechanical and electrical as required for repair work. Replace metal stud framing, boundary elements, sheathing, replace gypsum wall board, tape and sand, repaint. |  |  | NO | NO | NO |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | YES | YES |  |  | 0% | 25% | 10% |  |  | 0 | 0.5 | 0.5 |  |  | None | Not Given | By User | By User | Not Given | B1061.001-DS1-1.JPG | B1061.001-DS2-1.JPG | B1061.001-DS3-1.JPG |  |  | No | None | NO
B1061.001b | B1061.001b | Cold formed steel walls with wood structural panel sheathing, exterior - stucco one side | Costing for each 100 ft^2 Wall Panel. Assumed framing: 38 mil cold formed steel framing with 7/16 OSB and 3/8 plywood panel sheathing with overturning restraint at each end of the wall per AISI design standard. No. 8 screws 2" to 6" OC at perimeter and 12" OC EW in field. | High quality | Overturning restraint at each end of wall. | Each | Each | Story Drift Ratio | Unit less | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 273 | SF 100 | NO | NO | Sheathing faster pull through or tear out. (20% of fasteners.) | Failure of structural panels. | Failure of wall. |  |  | 1 | 1 | 1 |  |  | 0.004 | 0.0226 | 0.0267 |  |  | 0.4 | 0.3 | 0.25 |  |  | 0.1 | 0.1 | 0.1 |  |  | 0.4 | 0.3 | 0.25 |  |  | NO | YES | Superior | Superior | Superior | Superior | Remove damaged wall, ceilings, mechanical, electrical, and office furniture / equipment. Temporarily protect floor and provide dust curtains. Modify mechanical and electrical as required for repair work. Replace 20% of fasteners, replace gypsum wall board, stucco, tape and sand, repaint. | Remove damaged wall, ceilings, mechanical, electrical, and office furniture / equipment. Temporarily protect floor and provide dust curtains. Modify mechanical and electrical as required for repair work. Replace sheathing, replace gypsum wall board, stucco, tape and sand, repaint. | Remove damaged wall, ceilings, mechanical, electrical, and office furniture / equipment. Temporarily protect floor and provide dust curtains. Provide shoring. Modify mechanical and electrical as required for repair work. Replace metal stud framing, boundary elements, sheathing, replace gypsum wall board, stucco, tape and sand, repaint. |  |  | NO | NO | NO |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | YES | YES |  |  | 0% | 25% | 10% |  |  | 0 | 0.5 | 0.5 |  |  | None | Not Given | By User | By User | Not Given | B1061.001-DS1-1.JPG | B1061.001-DS2-1.JPG | B1061.001-DS3-1.JPG |  |  | No | None | NO
B1061.011a | B1061.011a | Cold formed steel walls with flat strap X-bracing, interior - gypsum board | Costing for each 100 ft^2 Wall Panel. Assumed framing: 33 mil cold formed steel framing with 4.5 inch x 33 mil flat strap X-bracing on one side. Straps attached to gussets with No. 8 screws. | High quality | Overturning restrains required and sheathing screws driven flush with the surface of the strapping. | Each | Each | Story Drift Ratio | Unit less | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 274 | SF 100 | NO | NO | Local buckling of chord studs. | Failure of many framing members and collapse. |  |  |  | 1 | 1 |  |  |  | 0.0139 | 0.0179 |  |  |  | 0.25 | 0.25 |  |  |  | 0.1 | 0.1 |  |  |  | 0.25 | 0.25 |  |  |  | NO | YES | Average | Superior | Average | Superior | Remove damaged wall, ceilings, X bracing as necessary, mechanical, electrical, and office furniture / equipment. Temporarily protect floor and provide dust curtains. Modify mechanical and electrical as required for repair work. Replace gypsum wall board, metal stud framing as needed, reinstall X bracing as required, tape and sand, repaint. | Remove damaged wall, ceilings, X bracing as necessary, mechanical, electrical, and office furniture / equipment. Temporarily protect floor and provide dust curtains. Modify mechanical and electrical as required for repair work. Replace gypsum wall board, boundary elements, metal stud framing, install X bracing, tape and sand, repaint. |  |  |  | NO | NO |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | YES | YES |  |  |  | 20% | 10% |  |  |  | 0.5 | 0.5 |  |  |  | None | Not Given | By User | By User | Not Given | B1061.011-DS1-1.JPG | B1061.011-DS2-1.JPG |  |  |  | No | None | NO
B1061.011b | B1061.011b | Cold formed steel walls with flat strap X-bracing, exterior - stucco one side | Costing for each 100 ft^2 Wall Panel. Assumed framing: 33 mil cold formed steel framing with 4.5 inch x 33 mil flat strap X-bracing on one side. Straps attached to gussets with No. 8 screws. | High quality | Overturning restrains required and sheathing screws driven flush with the surface of the strapping. | Each | Each | Story Drift Ratio | Unit less | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 275 | SF 100 | NO | NO | Local buckling of chord studs. | Failure of many framing members and collapse. |  |  |  | 1 | 1 |  |  |  | 0.0139 | 0.0179 |  |  |  | 0.25 | 0.25 |  |  |  | 0.1 | 0.1 |  |  |  | 0.25 | 0.25 |  |  |  | NO | YES | Average | Superior | Average | Superior | Remove damaged wall, ceilings, X bracing as necessary, mechanical, electrical, and office furniture / equipment. Temporarily protect floor and provide dust curtains. Modify mechanical and electrical as required for repair work. Replace gypsum wall board, stucco, metal stud framing as needed, reinstall X bracing as required, tape and sand, repaint. | Remove damaged wall, ceilings, X bracing as necessary, mechanical, electrical, and office furniture / equipment. Temporarily protect floor and provide dust curtains. Modify mechanical and electrical as required for repair work. Replace gypsum wall board, stucco, boundary elements, metal stud framing, install X bracing, tape and sand, repaint. |  |  |  | NO | NO |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | YES | YES |  |  |  | 20% | 10% |  |  |  | 0.5 | 0.5 |  |  |  | None | Not Given | By User | By User | Not Given | B1061.011-DS1-1.JPG | B1061.011-DS2-1.JPG |  |  |  | No | None | NO
B1061.021a | B1061.021a | Cold formed steel walls with 22 or 31 mil steel sheathing, interior - gypsum board | Costing for each 100 ft^2 Wall Panel. Assumed framing: 33 mil cold formed steel framing with 22 or 31 mil steel sheathing attached with No. 8 screws spaced 2" or 6" OC at perimeter and 12" OC EW in the field. | High quality | Overturning restrains required and sheathing screws driven flush with the surface of the strapping. | Each | Each | Story Drift Ratio | Unit less | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 276 | SF 100 | NO | NO | Pull out of sheathing fasteners from studs. | Buckling of steel sheathing. Buckling of framing members. |  |  |  | 1 | 1 |  |  |  | 0.019 | 0.0253 |  |  |  | 0.25 | 0.25 |  |  |  | 0.1 | 0.1 |  |  |  | 0.25 | 0.25 |  |  |  | NO | YES | Average | Superior | Superior | Superior | Remove damaged wall, ceilings, wall finishes, mechanical, electrical, and office furniture / equipment. Temporarily protect floor and provide dust curtains. Modify mechanical and electrical as required for repair work. Replace 20% of fasteners, replace gypsum wall board, tape, sand, paint. | Remove damaged wall, ceilings, wall finishes, mechanical, electrical, and office furniture / equipment. Temporarily protect floor and provide dust curtains. Modify mechanical and electrical as required for repair work. Install new sheathing, new metal stud framing as needed, replace gypsum wall board, tape, sand, paint. |  |  |  | NO | NO |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | YES | YES |  |  |  | 20% | 10% |  |  |  | 0.5 | 0.5 |  |  |  | None | Not Given | By User | By User | Not Given | B1061.021-DS1-1.JPG | B1061.021-DS2-1.JPG |  |  |  | No | None | NO
B1061.021b | B1061.021b | Cold formed steel walls with 22 or 31 mil steel sheathing, exterior - stucco one side | Costing for each 100 ft^2 Wall Panel. Assumed framing: 33 mil cold formed steel framing with 22 or 31 mil steel sheathing attached with No. 8 screws spaced 2" or 6" OC at perimeter and 12" OC EW in the field. | High quality | Overturning restrains required and sheathing screws driven flush with the surface of the strapping. | Each | Each | Story Drift Ratio | Unit less | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 277 | SF 100 | NO | NO | Pull out of sheathing fasteners from studs. | Buckling of steel sheathing. Buckling of framing members. |  |  |  | 1 | 1 |  |  |  | 0.019 | 0.0253 |  |  |  | 0.25 | 0.25 |  |  |  | 0.1 | 0.1 |  |  |  | 0.25 | 0.25 |  |  |  | NO | YES | Average | Superior | Superior | Superior | Remove damaged wall, ceilings, wall finishes, mechanical, electrical, and office furniture / equipment. Temporarily protect floor and provide dust curtains. Modify mechanical and electrical as required for repair work. Replace 20% of fasteners, replace gypsum wall board, stucco, tape, sand, paint. | Remove damaged wall, ceilings, wall finishes, mechanical, electrical, and office furniture / equipment. Temporarily protect floor and provide dust curtains. Modify mechanical and electrical as required for repair work. Install new sheathing, new metal stud framing as needed, replace gypsum wall board, stucco,, tape, sand, paint. |  |  |  | NO | NO |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | YES | YES |  |  |  | 20% | 10% |  |  |  | 0.5 | 0.5 |  |  |  | None | Not Given | By User | By User | Not Given | B1061.021-DS1-1.JPG | B1061.021-DS2-1.JPG |  |  |  | No | None | NO
B1071.001 | B1071.001 | Light framed wood walls with structural panel sheathing, gypsum wallboard no hold-downs | Costing for each 100 ft^2 Wall Panel. Assumed framing: 1 SIDE: 3/8" OSB or 15/32 ply with 8d box nails at 4 to 6 inches along panel edges and 12 inches field nailing. DF #2, 2x4@16 studs. 1 SIDE: 1/2 gypsum board. Panel 8 feet tall, 8 or 16 feet long with or without door and window openings, double top plate, single bottom plate, no hold-downs. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 278 | SF 100 | NO | NO | Slight separation of sheathing or nails which come loose. | Permanent rotation of sheathing, tear out of nails or sheathing. | Fracture of studs, major sill plate cracking. |  |  | 1 | 1 | 1 |  |  | 0.01 | 0.0175 | 0.025 |  |  | Not Specified | Not Specified | Not Specified |  |  | 0.4 | 0.4 | 0.4 |  |  | 0.4 | 0.4 | 0.4 |  |  | NO | YES | Not Rated | Marginal | Average | Superior | Remove exterior pliable siding, replace loose nails, reinstall siding. | Remove exterior pliable siding, remove wood sheathing, install new sheathing, reinstall siding. | Remove and replace siding, sheathing, studs and plates. Provide shoring as required. |  |  | NO | NO | NO |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | YES | YES |  |  | 0% | 50% | 25% |  |  | 0 | 0.5 | 0.5 |  |  | None | Not Given | By User | By User | Andre Filiatrault | B1071.001-DS1-1.JPG | B1071.001-DS2-1.JPG | B1071.001-DS3-1.JPG |  |  | No | None | NO
B1071.012 | B1071.012 | Light framed wood walls with structural panel sheathing, stucco, hold-downs | Costing for each 100 ft^2 Wall Panel. Assumed framing: 1 SIDE: 3/8" OSB or 15/32 ply with 8d box nails at 4 to 6 inches along panel edges and 12 inches field nailing. DF #2, 2x4@16 studs. 1 SIDE: 1/2 gypsum board. Panel 8 feet tall, 8 or 16 feet long with or without door and window openings, double top plate, single bottom plate, with hold-downs. Three layer 7/8" stucco with 1/2-inch chop strand fibers applied over wire mesh fastened with 1.25 -inch long staples. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 279 | SF 100 | NO | NO | Cracking of stucco. | Spalling of stucco, separation of stucco and sheathing from studs. | Fracture of studs, major sill plate cracking. |  |  | 1 | 1 | 1 |  |  | 0.0025 | 0.0052 | 0.0252 |  |  | Not Specified | 0.28 | 0.12 |  |  | 0.1 | 0.1 | 0.1 |  |  | 0.44 | 0.3 | 0.16 |  |  | NO | YES | Superior | Superior | Superior | Superior | Clean stucco cracks. Fill cracks with cement compound. Repaint wall to hide cracks. | Remove loose stucco and patch spalled areas with stucco. Repaint to hide repairs. | Remove and replace studs, plates, sheathing, and stucco. Shore as required. |  |  | NO | NO | NO |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | YES | YES |  |  | 0% | 35% | 25% |  |  | 0 | 0.5 | 0.5 |  |  | None | Not Given | By User | By User | Andre Filiatrault | B1071.002-DS1-1.JPG | B1071.002-DS2-1.JPG | B1071.002-DS3-1.JPG |  |  | No | 2016-09-14 Renamed from B1071.002 | NO
B1071.011 | B1071.011 | Light framed wood walls with structural panel sheathing, stucco no hold-downs | Costing for each 100 ft^2 Wall Panel. Assumed framing: 1 SIDE: 3/8" OSB or 15/32 ply with 8d box nails at 4 to 6 inches along panel edges and 12 inches field nailing. DF #2, 2x4@16 studs. 1 SIDE: 1/2 gypsum board. Panel 8 feet tall, 8 or 16 feet long with or without door and window openings, double top plate, single bottom plate, with no hold-downs. Three layer 7/8" stucco with 1/2-inch chop strand fibers applied over wire mesh fastened with 1.25 -inch long staples. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 280 | SF 100 | NO | NO | Cracking of stucco. | Spalling of stucco, separation of stucco and sheathing from studs. | Fracture of studs, major sill plate cracking. |  |  | 1 | 1 | 1 |  |  | 0.0017 | 0.0035 | 0.017 |  |  | Not Specified | Not Specified | Not Specified |  |  | 0.5 | 0.4 | 0.4 |  |  | 0.5 | 0.4 | 0.4 |  |  | NO | YES | Not Rated | Marginal | Average | Superior | Clean stucco cracks. Fill cracks with cement compound. Repaint wall to hide cracks. | Remove loose stucco and patch spalled areas with stucco. Repaint to hide repairs. | Remove and replace studs, plates, sheathing, and stucco. Shore as required. |  |  | NO | NO | NO |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | YES | YES |  |  | 0% | 35% | 25% |  |  | 0 | 0.5 | 0.5 |  |  | None | Not Given | By User | By User | Andre Filiatrault | B1071.002-DS1-1.JPG | B1071.002-DS2-1.JPG | B1071.002-DS3-1.JPG |  |  | No | None | NO
B1071.002 | B1071.002 | Light framed wood walls with structural panel sheathing, gypsum wallboard and hold-downs | Costing for each 100 ft^2 Wall Panel. Assumed framing: 1 SIDE: 3/8" OSB or 15/32 ply with 8d box nails at 4 to 6 inches along panel edges and 12 inches field nailing. DF #2, 2x4@16 studs. 1 SIDE: 1/2 gypsum board. Panel 8 feet tall, 8 or 16 feet long with or without door and window openings, double top plate, single bottom plate, with hold-downs. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 281 | SF 100 | NO | NO | Slight separation of sheathing or nails which come loose. | Permanent rotation of sheathing, tear out of nails or sheathing. | Fracture of studs, major sill plate cracking. |  |  | 1 | 1 | 1 |  |  | 0.015 | 0.0262 | 0.0369 |  |  | 0.26 | 0.16 | 0.17 |  |  | 0.3 | 0.1 | 0.1 |  |  | 0.4 | 0.19 | 0.2 |  |  | NO | YES | Superior | Superior | Superior | Superior | Remove exterior pliable siding, replace loose nails, reinstall siding. | Remove exterior pliable siding, remove wood sheathing, install new sheathing, reinstall siding. | Remove and replace siding, sheathing, studs and plates. Provide shoring as required. |  |  | NO | NO | NO |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | YES | YES |  |  | 0% | 50% | 25% |  |  | 0 | 0.5 | 0.5 |  |  | None | Not Given | By User | By User | Andre Filiatrault | B1071.001-DS1-1.JPG | B1071.001-DS2-1.JPG | B1071.001-DS3-1.JPG |  |  | No | 2011-08-24 Negative probability below 0.5% drift - overlap deemed acceptable. 2016-09-14 Renamed from B1071.021 | NO
B1071.031 | B1071.031 | Wood walls with diagonal let-in bracing | Costing for each 100 ft^2 Wall Panel. Assumed framing: Stud wall framing consists of 2 x 4’s at 16 inches on center with double top plates and single sill plate. Diagonal bracing includes 2 forms. Block-bracing consists of diagonal blocking between studs that extends from the top of one edge of the panel to the bottom of the opposite edge. Diagonal bracing may also consist of let-in bracing for which a 1x or 2x brace (with same inclination as described for block-bracing) is recessed into studs. Walls may be sheathed with horizontal or vertical lumber siding. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 1 | DS1 |  |  |  |  | Sequential |  |  |  |  | Seq(DS1) | 282 | SF 100 | NO | NO | Failure of diagonal bracing. |  |  |  |  | 1 |  |  |  |  | 0.01 |  |  |  |  | Not Specified |  |  |  |  | 0.4 |  |  |  |  | 0.4 |  |  |  |  | NO | YES | Average | Average | Superior | Superior | Remove and replace sheathing studs, plates and bracing and replace with new stud wall construction of plywood, hold-downs, etc. Provide shoring as required. |  |  |  |  | NO |  |  |  |  | NO |  |  |  |  | Not Applicable |  |  |  |  | 0% | 0 | [8 empty] | 0% | 0 | [8 empty] | YES |  |  |  |  | 25% |  |  |  |  | 0.5 |  |  |  |  | None | Not Given | By User | By User | Andre Filiatrault | B1071.031-DS1-1.JPG |  |  |  |  | No | None | NO
B1071.041 | B1071.041 | Exterior Wall - Type: Gypsum with wood studs, Full Height, Fixed Below, Fixed Above | Costing based upon 13'x100' Panels | Normal | Unknown | Each | Each | Story Drift Ratio | Unit less | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 283 | LF 100 | NO | NO | Screws pop-out, minor cracking of wall board, warping or cracking of tape. | Moderate cracking or crushing of gypsum wall boards (typically in corners and in corners of openings). | Significant cracking and/or crushing of gypsum wall boards- buckling of studs and tearing of tracks. |  |  | 1 | 1 | 1 |  |  | 0.0021 | 0.0071 | 0.012 |  |  | Not Specified | Not Specified | Not Specified |  |  | Not Specified | Not Specified | Not Specified |  |  | 0.6 | 0.45 | 0.45 |  |  | NO | YES | Superior | Superior | Superior | Not Rated | Retape joints, paste and repaint both sides of full 100 foot length of wall board. | Remove full 100 foot length of wall board (both sides), install new wall board (both sides), tape, paste and repaint. | Remove and replace full 100 foot length of metal stud wall, both sides of the gypsum wall board and any embedded utilities, and tape, paste and repaint. |  |  | NO | NO | NO |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | NO | NO |  |  | 0% | 0% | 0% |  |  | 0 | 0 | 0 |  |  | Copy of C1011.011a for use as an exterior wall. | Not Given | By User | By User | Not Given | none | none | none |  |  | No | None | YES
B2011.001a | B2011.001a | Exterior Wall - Cold formed steel walls with wood structural panel sheathing, interior - gypsum board | Costing for each 100 ft^2 Wall Panel. Assumed framing: 38 mil cold formed steel framing with 7/16 OSB and 3/8 plywood panel sheathing with overturning restraint at each end of the wall per AISI design standard. No. 8 screws 2" to 6" OC at perimeter and 12" OC EW in field. | High quality | Overturning restraint at each end of wall. | Each | Each | Story Drift Ratio | Unit less | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 284 | SF 100 | NO | NO | Sheathing faster pull through or tear out. (20% of fasteners.) | Failure of structural panels. | Failure of wall. |  |  | 1 | 1 | 1 |  |  | 0.004 | 0.0226 | 0.0267 |  |  | 0.4 | 0.3 | 0.25 |  |  | 0.1 | 0.1 | 0.1 |  |  | 0.4 | 0.3 | 0.25 |  |  | NO | YES | Superior | Superior | Superior | Superior | Remove damaged wall, ceilings, mechanical, electrical, and office furniture / equipment. Temporarily protect floor and provide dust curtains. Modify mechanical and electrical as required for repair work. Replace 20% of fasteners, replace gypsum wall board, tape and sand, repaint. | Remove damaged wall, ceilings, mechanical, electrical, and office furniture / equipment. Temporarily protect floor and provide dust curtains. Modify mechanical and electrical as required for repair work. Replace sheathing, replace gypsum wall board, tape and sand, repaint. | Remove damaged wall, ceilings, mechanical, electrical, and office furniture / equipment. Temporarily protect floor and provide dust curtains. Provide shoring. Modify mechanical and electrical as required for repair work. Replace metal stud framing, boundary elements, sheathing, replace gypsum wall board, tape and sand, repaint. |  |  | NO | NO | NO |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | YES | YES |  |  | 0% | 25% | 10% |  |  | 0 | 0.5 | 0.5 |  |  | Copy of B1061.001a for use as an exterior wall. | Not Given | By User | By User | Not Given | B1061.001-DS1-1.JPG | B1061.001-DS2-1.JPG | B1061.001-DS3-1.JPG |  |  | No | None | YES
B2011.001b | B2011.001b | Exterior Wall - Cold formed steel walls with wood structural panel sheathing, exterior - stucco one side | Costing for each 100 ft^2 Wall Panel. Assumed framing: 38 mil cold formed steel framing with 7/16 OSB and 3/8 plywood panel sheathing with overturning restraint at each end of the wall per AISI design standard. No. 8 screws 2" to 6" OC at perimeter and 12" OC EW in field. | High quality | Overturning restraint at each end of wall. | Each | Each | Story Drift Ratio | Unit less | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 285 | SF 100 | NO | NO | Sheathing faster pull through or tear out. (20% of fasteners.) | Failure of structural panels. | Failure of wall. |  |  | 1 | 1 | 1 |  |  | 0.004 | 0.0226 | 0.0267 |  |  | 0.4 | 0.3 | 0.25 |  |  | 0.1 | 0.1 | 0.1 |  |  | 0.4 | 0.3 | 0.25 |  |  | NO | YES | Superior | Superior | Superior | Superior | Remove damaged wall, ceilings, mechanical, electrical, and office furniture / equipment. Temporarily protect floor and provide dust curtains. Modify mechanical and electrical as required for repair work. Replace 20% of fasteners, replace gypsum wall board, stucco, tape and sand, repaint. | Remove damaged wall, ceilings, mechanical, electrical, and office furniture / equipment. Temporarily protect floor and provide dust curtains. Modify mechanical and electrical as required for repair work. Replace sheathing, replace gypsum wall board, stucco, tape and sand, repaint. | Remove damaged wall, ceilings, mechanical, electrical, and office furniture / equipment. Temporarily protect floor and provide dust curtains. Provide shoring. Modify mechanical and electrical as required for repair work. Replace metal stud framing, boundary elements, sheathing, replace gypsum wall board, stucco, tape and sand, repaint. |  |  | NO | NO | NO |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | YES | YES |  |  | 0% | 25% | 10% |  |  | 0 | 0.5 | 0.5 |  |  | Copy of B1061.001b for use as an exterior wall. | Not Given | By User | By User | Not Given | B1061.001-DS1-1.JPG | B1061.001-DS2-1.JPG | B1061.001-DS3-1.JPG |  |  | No | None | YES
B2011.011a | B2011.011a | Exterior Wall - Cold formed steel walls with flat strap X-bracing, interior - gypsum board | Costing for each 100 ft^2 Wall Panel. Assumed framing: 33 mil cold formed steel framing with 4.5 inch x 33 mil flat strap X-bracing on one side. Straps attached to gussets with No. 8 screws. | High quality | Overturning restrains required and sheathing screws driven flush with the surface of the strapping. | Each | Each | Story Drift Ratio | Unit less | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 286 | SF 100 | NO | NO | Local buckling of chord studs. | Failure of many framing members and collapse. |  |  |  | 1 | 1 |  |  |  | 0.0139 | 0.0179 |  |  |  | 0.25 | 0.25 |  |  |  | 0.1 | 0.1 |  |  |  | 0.25 | 0.25 |  |  |  | NO | YES | Average | Superior | Average | Superior | Remove damaged wall, ceilings, X bracing as necessary, mechanical, electrical, and office furniture / equipment. Temporarily protect floor and provide dust curtains. Modify mechanical and electrical as required for repair work. Replace gypsum wall board, metal stud framing as needed, reinstall X bracing as required, tape and sand, repaint. | Remove damaged wall, ceilings, X bracing as necessary, mechanical, electrical, and office furniture / equipment. Temporarily protect floor and provide dust curtains. Modify mechanical and electrical as required for repair work. Replace gypsum wall board, boundary elements, metal stud framing, install X bracing, tape and sand, repaint. |  |  |  | NO | NO |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | YES | YES |  |  |  | 20% | 10% |  |  |  | 0.5 | 0.5 |  |  |  | Copy of B1061.011a for use as an exterior wall. | Not Given | By User | By User | Not Given | B1061.011-DS1-1.JPG | B1061.011-DS2-1.JPG |  |  |  | No | None | YES
B2011.011b | B2011.011b | Exterior Wall - Cold formed steel walls with flat strap X-bracing, exterior - stucco one side | Costing for each 100 ft^2 Wall Panel. Assumed framing: 33 mil cold formed steel framing with 4.5 inch x 33 mil flat strap X-bracing on one side. Straps attached to gussets with No. 8 screws. | High quality | Overturning restrains required and sheathing screws driven flush with the surface of the strapping. | Each | Each | Story Drift Ratio | Unit less | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 287 | SF 100 | NO | NO | Local buckling of chord studs. | Failure of many framing members and collapse. |  |  |  | 1 | 1 |  |  |  | 0.0139 | 0.0179 |  |  |  | 0.25 | 0.25 |  |  |  | 0.1 | 0.1 |  |  |  | 0.25 | 0.25 |  |  |  | NO | YES | Average | Superior | Average | Superior | Remove damaged wall, ceilings, X bracing as necessary, mechanical, electrical, and office furniture / equipment. Temporarily protect floor and provide dust curtains. Modify mechanical and electrical as required for repair work. Replace gypsum wall board, stucco, metal stud framing as needed, reinstall X bracing as required, tape and sand, repaint. | Remove damaged wall, ceilings, X bracing as necessary, mechanical, electrical, and office furniture / equipment. Temporarily protect floor and provide dust curtains. Modify mechanical and electrical as required for repair work. Replace gypsum wall board, stucco, boundary elements, metal stud framing, install X bracing, tape and sand, repaint. |  |  |  | NO | NO |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | YES | YES |  |  |  | 20% | 10% |  |  |  | 0.5 | 0.5 |  |  |  | Copy of B1061.011b for use as an exterior wall. | Not Given | By User | By User | Not Given | B1061.011-DS1-1.JPG | B1061.011-DS2-1.JPG |  |  |  | No | None | YES
B2011.021a | B2011.021a | Exterior Wall - Cold formed steel walls with 22 or 31 mil steel sheathing, interior - gypsum board | Costing for each 100 ft^2 Wall Panel. Assumed framing: 33 mil cold formed steel framing with 22 or 31 mil steel sheathing attached with No. 8 screws spaced 2" or 6" OC at perimeter and 12" OC EW in the field. | High quality | Overturning restrains required and sheathing screws driven flush with the surface of the strapping. | Each | Each | Story Drift Ratio | Unit less | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 288 | SF 100 | NO | NO | Pull out of sheathing fasteners from studs. | Buckling of steel sheathing. Buckling of framing members. |  |  |  | 1 | 1 |  |  |  | 0.019 | 0.0253 |  |  |  | 0.25 | 0.25 |  |  |  | 0.1 | 0.1 |  |  |  | 0.25 | 0.25 |  |  |  | NO | YES | Average | Superior | Superior | Superior | Remove damaged wall, ceilings, wall finishes, mechanical, electrical, and office furniture / equipment. Temporarily protect floor and provide dust curtains. Modify mechanical and electrical as required for repair work. Replace 20% of fasteners, replace gypsum wall board, tape, sand, paint. | Remove damaged wall, ceilings, wall finishes, mechanical, electrical, and office furniture / equipment. Temporarily protect floor and provide dust curtains. Modify mechanical and electrical as required for repair work. Install new sheathing, new metal stud framing as needed, replace gypsum wall board, tape, sand, paint. |  |  |  | NO | NO |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | YES | YES |  |  |  | 20% | 10% |  |  |  | 0.5 | 0.5 |  |  |  | Copy of B1061.021a for use as an exterior wall. | Not Given | By User | By User | Not Given | B1061.021-DS1-1.JPG | B1061.021-DS2-1.JPG |  |  |  | No | None | YES
B2011.021b | B2011.021b | Exterior Wall - Cold formed steel walls with 22 or 31 mil steel sheathing, exterior - stucco one side | Costing for each 100 ft^2 Wall Panel. Assumed framing: 33 mil cold formed steel framing with 22 or 31 mil steel sheathing attached with No. 8 screws spaced 2" or 6" OC at perimeter and 12" OC EW in the field. | High quality | Overturning restrains required and sheathing screws driven flush with the surface of the strapping. | Each | Each | Story Drift Ratio | Unit less | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 289 | SF 100 | NO | NO | Pull out of sheathing fasteners from studs. | Buckling of steel sheathing. Buckling of framing members. |  |  |  | 1 | 1 |  |  |  | 0.019 | 0.0253 |  |  |  | 0.25 | 0.25 |  |  |  | 0.1 | 0.1 |  |  |  | 0.25 | 0.25 |  |  |  | NO | YES | Average | Superior | Superior | Superior | Remove damaged wall, ceilings, wall finishes, mechanical, electrical, and office furniture / equipment. Temporarily protect floor and provide dust curtains. Modify mechanical and electrical as required for repair work. Replace 20% of fasteners, replace gypsum wall board, stucco, tape, sand, paint. | Remove damaged wall, ceilings, wall finishes, mechanical, electrical, and office furniture / equipment. Temporarily protect floor and provide dust curtains. Modify mechanical and electrical as required for repair work. Install new sheathing, new metal stud framing as needed, replace gypsum wall board, stucco,, tape, sand, paint. |  |  |  | NO | NO |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | YES | YES |  |  |  | 20% | 10% |  |  |  | 0.5 | 0.5 |  |  |  | Copy of B1061.021b for use as an exterior wall. | Not Given | By User | By User | Not Given | B1061.021-DS1-1.JPG | B1061.021-DS2-1.JPG |  |  |  | No | None | YES
B2011.101 | B2011.101 | Exterior Wall - Light framed wood walls with structural panel sheathing, gypsum wallboard no hold-downs | Costing for each 100 ft^2 Wall Panel. Assumed framing: 1 SIDE: 3/8" OSB or 15/32 ply with 8d box nails at 4 to 6 inches along panel edges and 12 inches field nailing. DF #2, 2x4@16 studs. 1 SIDE: 1/2 gypsum board. Panel 8 feet tall, 8 or 16 feet long with or without door and window openings, double top plate, single bottom plate, no hold-downs. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 290 | SF 100 | NO | NO | Slight separation of sheathing or nails which come loose. | Permanent rotation of sheathing, tear out of nails or sheathing. | Fracture of studs, major sill plate cracking. |  |  | 1 | 1 | 1 |  |  | 0.01 | 0.0175 | 0.025 |  |  | Not Specified | Not Specified | Not Specified |  |  | 0.4 | 0.4 | 0.4 |  |  | 0.4 | 0.4 | 0.4 |  |  | NO | YES | Not Rated | Marginal | Average | Superior | Remove exterior pliable siding, replace loose nails, reinstall siding. | Remove exterior pliable siding, remove wood sheathing, install new sheathing, reinstall siding. | Remove and replace siding, sheathing, studs and plates. Provide shoring as required. |  |  | NO | NO | NO |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | YES | YES |  |  | 0% | 50% | 25% |  |  | 0 | 0.5 | 0.5 |  |  | Copy of B1071.001 for use as an exterior wall. | Not Given | By User | By User | Andre Filiatrault | B1071.001-DS1-1.JPG | B1071.001-DS2-1.JPG | B1071.001-DS3-1.JPG |  |  | No | None | YES
B2011.102 | B2011.102 | Exterior Wall - Light framed wood walls with structural panel sheathing, stucco, hold-downs | Costing for each 100 ft^2 Wall Panel. Assumed framing: 1 SIDE: 3/8" OSB or 15/32 ply with 8d box nails at 4 to 6 inches along panel edges and 12 inches field nailing. DF #2, 2x4@16 studs. 1 SIDE: 1/2 gypsum board. Panel 8 feet tall, 8 or 16 feet long with or without door and window openings, double top plate, single bottom plate, with hold-downs. Three layer 7/8" stucco with 1/2-inch chop strand fibers applied over wire mesh fastened with 1.25 -inch long staples. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 291 | SF 100 | NO | NO | Cracking of stucco. | Spalling of stucco, separation of stucco and sheathing from studs. | Fracture of studs, major sill plate cracking. |  |  | 1 | 1 | 1 |  |  | 0.0025 | 0.0052 | 0.0252 |  |  | 0.43 | 0.28 | 0.12 |  |  | 0.1 | 0.1 | 0.1 |  |  | 0.44 | 0.3 | 0.16 |  |  | NO | YES | Superior | Superior | Superior | Superior | Clean stucco cracks. Fill cracks with cement compound. Repaint wall to hide cracks. | Remove loose stucco and patch spalled areas with stucco. Repaint to hide repairs. | Remove and replace studs, plates, sheathing, and stucco. Shore as required. |  |  | NO | NO | NO |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | YES | YES |  |  | 0% | 35% | 25% |  |  | 0 | 0.5 | 0.5 |  |  | Copy of B1071.002 for use as an exterior wall. | Not Given | By User | By User | Andre Filiatrault | B1071.002-DS1-1.JPG | B1071.002-DS2-1.JPG | B1071.002-DS3-1.JPG |  |  | No | None | YES
B2011.111 | B2011.111 | Exterior Wall - Light framed wood walls with structural panel sheathing, stucco no hold-downs | Costing for each 100 ft^2 Wall Panel. Assumed framing: 1 SIDE: 3/8" OSB or 15/32 ply with 8d box nails at 4 to 6 inches along panel edges and 12 inches field nailing. DF #2, 2x4@16 studs. 1 SIDE: 1/2 gypsum board. Panel 8 feet tall, 8 or 16 feet long with or without door and window openings, double top plate, single bottom plate, with no hold-downs. Three layer 7/8" stucco with 1/2-inch chop strand fibers applied over wire mesh fastened with 1.25 -inch long staples. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 292 | SF 100 | NO | NO | Cracking of stucco. | Spalling of stucco, separation of stucco and sheathing from studs. | Fracture of studs, major sill plate cracking. |  |  | 1 | 1 | 1 |  |  | 0.0017 | 0.0035 | 0.017 |  |  | Not Specified | Not Specified | Not Specified |  |  | 0.5 | 0.4 | 0.4 |  |  | 0.5 | 0.4 | 0.4 |  |  | NO | YES | Not Rated | Marginal | Average | Superior | Clean stucco cracks. Fill cracks with cement compound. Repaint wall to hide cracks. | Remove loose stucco and patch spalled areas with stucco. Repaint to hide repairs. | Remove and replace studs, plates, sheathing, and stucco. Shore as required. |  |  | NO | NO | NO |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | YES | YES |  |  | 0% | 35% | 25% |  |  | 0 | 0.5 | 0.5 |  |  | Copy of B1071.011 for use as an exterior wall. | Not Given | By User | By User | Andre Filiatrault | B1071.002-DS1-1.JPG | B1071.002-DS2-1.JPG | B1071.002-DS3-1.JPG |  |  | No | None | YES
B2011.121 | B2011.121 | Exterior Wall - Light framed wood walls with structural panel sheathing, gypsum wallboard and hold-downs | Costing for each 100 ft^2 Wall Panel. Assumed framing: 1 SIDE: 3/8" OSB or 15/32 ply with 8d box nails at 4 to 6 inches along panel edges and 12 inches field nailing. DF #2, 2x4@16 studs. 1 SIDE: 1/2 gypsum board. Panel 8 feet tall, 8 or 16 feet long with or without door and window openings, double top plate, single bottom plate, with hold-downs. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 293 | SF 100 | NO | NO | Slight separation of sheathing or nails which come loose. | Permanent rotation of sheathing, tear out of nails or sheathing. | Fracture of studs, major sill plate cracking. |  |  | 1 | 1 | 1 |  |  | 0.015 | 0.0262 | 0.0369 |  |  | 0.26 | 0.16 | 0.17 |  |  | 0.3 | 0.1 | 0.1 |  |  | 0.4 | 0.19 | 0.2 |  |  | NO | YES | Superior | Superior | Superior | Superior | Remove exterior pliable siding, replace loose nails, reinstall siding. | Remove exterior pliable siding, remove wood sheathing, install new sheathing, reinstall siding. | Remove and replace siding, sheathing, studs and plates. Provide shoring as required. |  |  | NO | NO | NO |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | YES | YES |  |  | 0% | 50% | 25% |  |  | 0 | 0.5 | 0.5 |  |  | Copy of B1071.021 for use as an exterior wall. | Not Given | By User | By User | Andre Filiatrault | B1071.001-DS1-1.JPG | B1071.001-DS2-1.JPG | B1071.001-DS3-1.JPG |  |  | No | 2011-08-24 Negative probability below 0.5% drift - overlap deemed acceptable. | YES
B2011.131 | B2011.131 | Exterior Wall - Wood walls with diagonal let-in bracing | Costing for each 100 ft^2 Wall Panel. Assumed framing: Stud wall framing consists of 2 x 4’s at 16 inches on center with double top plates and single sill plate. Diagonal bracing includes 2 forms. Block-bracing consists of diagonal blocking between studs that extends from the top of one edge of the panel to the bottom of the opposite edge. Diagonal bracing may also consist of let-in bracing for which a 1x or 2x brace (with same inclination as described for block-bracing) is recessed into studs. Walls may be sheathed with horizontal or vertical lumber siding. | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 1 | DS1 |  |  |  |  | Sequential |  |  |  |  | Seq(DS1) | 294 | SF 100 | NO | NO | Failure of diagonal bracing. |  |  |  |  | 1 |  |  |  |  | 0.01 |  |  |  |  | Not Specified |  |  |  |  | 0.4 |  |  |  |  | 0.4 |  |  |  |  | NO | YES | Average | Average | Superior | Superior | Remove and replace sheathing studs, plates and bracing and replace with new stud wall construction of plywood, hold-downs, etc. Provide shoring as required. |  |  |  |  | NO |  |  |  |  | NO |  |  |  |  | Not Applicable |  |  |  |  | 0% | 0 | [8 empty] | 0% | 0 | [8 empty] | YES |  |  |  |  | 25% |  |  |  |  | 0.5 |  |  |  |  | Copy of B1071.031 for use as an exterior wall. | Not Given | By User | By User | Andre Filiatrault | B1071.031-DS1-1.JPG |  |  |  |  | No | None | YES
B2011.201a | B2011.201a | Precast Concrete Panels 4.5 inches thick - in plane deformation | Costing is based upon 30'x13' panels. | Not Specified | All | Each | Each | Story Drift Ratio | Unit less | 2 | DS1 | DS2 |  |  |  | Mutually Exclusive | Mutually Exclusive |  |  |  | MutEx(DS1,DS2) | 295 | LF 30 | NO | NO | Cladding units damaged by impact at corners at column covers. Damage in field is either attributed to natural edge chipping / damage, or is deemed to not warrant full repair. Repair assumes cosmetic chip patching. | Cladding units damaged by impact at corners at column covers. |  |  |  | 0.5 | 0.5 |  |  |  | By User | By User |  |  |  | Not Specified | Not Specified |  |  |  | Not Specified | Not Specified |  |  |  | By User | By User |  |  |  | NO | YES | By User | By User | By User | By User | By User, Repair cost assumed to equal 20% of DS2. | By User, Cost listed assumed the replacement of the panel |  |  |  | NO | NO |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | NO |  |  |  | 0% | 0% |  |  |  | 0 | 0 |  |  |  | Determine fragility story drift median demand in accordance with Chapter 7 of Volume 2. | By User | By User | By User | By User | none | none |  |  |  | No | 2016-06-27 Revise DS1 to be MutEx reduced cost version of itself. | YES
B2011.201b | B2011.201b | Precast Concrete Panels 4.5 inches thick - out of plane deformation | Costing is based upon 30'x13' panels. | Not Specified | All | Each | Each | Peak Floor Acceleration | g | 1 | DS1 |  |  |  |  | Sequential |  |  |  |  | Seq(DS1) | 296 | LF 30 | NO | NO | Cladding units damaged by out of plane anchorage failure. Unit requires replacement. |  |  |  |  | 1 |  |  |  |  | By User |  |  |  |  | Not Specified |  |  |  |  | Not Specified |  |  |  |  | By User |  |  |  |  | NO | NO | By User | By User | By User | By User | By User - Replace cladding panel. |  |  |  |  | NO |  |  |  |  | NO |  |  |  |  | Not Applicable |  |  |  |  | 0% | 0 | [8 empty] | 0% | 0 | [8 empty] | YES |  |  |  |  | 25% |  |  |  |  | 0.5 |  |  |  |  | Determine fragility peak floor acceleration anchorage capacity in accordance with Chapter 7 of Volume 2. | By User | By User | By User | By User | none |  |  |  |  | No | None | YES
B2022.001 | B2022.001 | Curtain Walls - Generic Midrise Stick-Built Curtain wall, Config: Monolithic, Lamination: Unknown, Glass Type: Unknown, Details: Aspect ratio = 6:5, Other details Unknown | None | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 297 | SF 30 | NO | NO | Glass cracking. | Glass falls from frame. |  |  |  | 1 | 1 |  |  |  | 0.0338 | 0.0383 |  |  |  | 0.0797 | 0.1923 |  |  |  | 0.25 | 0.25 |  |  |  | 0.4 | 0.4 |  |  |  | NO | YES | Superior | Average | Superior | Superior | Replace cracked glass panel. | Replace cracked glass panel; cover exposure in meantime. |  |  |  | NO | NO |  |  |  | NO | YES |  |  |  | Not Applicable | 36 SF |  |  |  | 0% | 0 | 2% | 0.5 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | YES |  |  |  | 0% | 90% |  |  |  | 0 | 0.5 |  |  |  | None | By User | By User | By User | Not Given | B2022.001a-DS1-1.JPG | B2022.001a-DS2-1.JPG |  |  |  | No | 2011-08-24 Negative probability below 0.5% drift - Overlap deemed acceptable. | Yes
B2022.002 | B2022.002 | Curtain Walls - Generic Midrise Stick-Built Curtain wall, Config: Insulating Glass Units (dual pane), Lamination: Unknown, Glass Type: Unknown, Details: Aspect ratio = 6:5, Other details Unknown | None | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 298 | SF 30 | NO | NO | Glass cracking. | Glass falls from frame. |  |  |  | 1 | 1 |  |  |  | 0.021 | 0.024 |  |  |  | 0.1663 | 0.1558 |  |  |  | 0.25 | 0.25 |  |  |  | 0.45 | 0.45 |  |  |  | NO | YES | Superior | Average | Superior | Superior | Replace cracked glass panel. | Replace cracked glass panel; cover exposure in meantime. |  |  |  | NO | NO |  |  |  | NO | YES |  |  |  | Not Applicable | 36 SF |  |  |  | 0% | 0 | 2% | 0.5 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | YES |  |  |  | 0% | 90% |  |  |  | 0 | 0.5 |  |  |  | None | By User | By User | By User | Not Given | B2022.001a-DS1-1.JPG | B2022.001a-DS2-1.JPG |  |  |  | No | None | Yes
B2022.011 | B2022.011 | Midrise stick-built curtain wall, Config: Asymmetric insulating glass units (dual-pane, unequal-thickness IGU), Lamination: Laminated, Glass Type: Annealed, Details: 1/4 in. (6 mm) inner AN / 1/2 in. (13 mm) outer AN LAM (0.030 PVB) IGU; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 6:5 sealant = dry | None | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 299 | SF 30 | NO | NO | Gasket seal failure. | Glass cracking. | Glass falls out. |  |  | 1 | 1 | 1 |  |  | 0.026 | 0.0268 | 0.0339 |  |  | 0.1083 | 0.1443 | 0.0973 |  |  | 0.25 | 0.25 | 0.25 |  |  | 0.25 | 0.25 | 0.25 |  |  | NO | YES | Superior | Average | Superior | Superior | Remove glass panel and replace damaged gaskets. | Replace cracked glass panel. | Replace cracked glass panel; cover exposure in meantime. |  |  | NO | NO | NO |  |  | NO | NO | YES |  |  | Not Applicable | Not Applicable | 36 SF |  |  | 0% | 0 | 0% | 0 | 2% | 0.5 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | NO | YES |  |  | 0% | 0% | 90% |  |  | 0 | 0 | 0.5 |  |  | None | By User | By User | By User | Not Given | B2022.003-DS1-1.JPG | B2022.001a-DS1-1.JPG | B2022.001a-DS2-1.JPG |  |  | No | 2011-08-24 DS2 beta changed from 0.3 to 0.25 to avoid negative probabilities. | Yes
B2022.021 | B2022.021 | Midrise stick-built curtain wall, Config: Monolithic, Lamination: Laminated, Glass Type: Annealed, Details: 1/4 in. (6 mm) AN LAM (0.030 PVB); glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 6:5 sealant = dry | None | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 300 | SF 30 | NO | NO | Glass cracking. | Glass falls from frame. |  |  |  | 1 | 1 |  |  |  | 0.0156 | 0.0561 |  |  |  | 0.2353 | 0.1852 |  |  |  | 0.25 | 0.25 |  |  |  | 0.35 | 0.3 |  |  |  | NO | YES | Superior | Average | Superior | Superior | Replace cracked glass panel. | Replace cracked glass panel; cover exposure in meantime. |  |  |  | NO | NO |  |  |  | NO | YES |  |  |  | Not Applicable | 36 SF |  |  |  | 0% | 0 | 2% | 0.5 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | YES |  |  |  | 0% | 90% |  |  |  | 0 | 0.5 |  |  |  | None | By User | By User | By User | Not Given | B2022.001a-DS1-1.JPG | B2022.001a-DS2-1.JPG |  |  |  | No | None | Yes
B2022.022 | B2022.022 | Midrise stick-built curtain wall, Config: Monolithic, Lamination: Laminated, Glass Type: Annealed, Details: 1/4 in. (6 mm) AN laminated, 2-sided SSG, Center Panel; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 6:5 sealant = wet | None | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 301 | SF 30 | NO | NO | Glass cracking. | Glass falls from frame. |  |  |  | 1 | 1 |  |  |  | 0.0392 | 0.0434 |  |  |  | Not Specified | Not Specified |  |  |  | Not Specified | Not Specified |  |  |  | 0.29 | 0.25 |  |  |  | NO | YES | Not Rated | Not Rated | Not Rated | Not Rated | Replace cracked glass panel. |  |  |  |  | NO | NO |  |  |  | NO | YES |  |  |  | By User | 36 SF |  |  |  | 0% | 0 | 2% | 0.5 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | YES |  |  |  | 0% | 90% |  |  |  | 0 | 0.5 |  |  |  | User to provide median demand and dispersion values. The values listed are default PACT values and do not represent the response of this component. This component requires user specified cost and time consequence data. Values within PACT are defaults (equal to zero) and do not represent actual consequence. | By User | By User | By User | Not Given | none | none |  |  |  | No | None | Yes
B2022.023 | B2022.023 | Midrise stick-built curtain wall, Config: Monolithic, Lamination: Laminated, Glass Type: Annealed, Details: 1/4 in. (6 mm) AN laminated, 2-sided SSG, Outside Panel; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 6:5 sealant = wet | None | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 302 | SF 30 | NO | NO | Glass cracking. | Glass falls from frame. |  |  |  | 1 | 1 |  |  |  | 0.0347 | 0.04 |  |  |  | Not Specified | Not Specified |  |  |  | Not Specified | Not Specified |  |  |  | 0.26 | 0.6 |  |  |  | NO | YES | Not Rated | Not Rated | Not Rated | Not Rated | Replace cracked glass panel. |  |  |  |  | NO | NO |  |  |  | NO | YES |  |  |  | Not Applicable | 36 SF |  |  |  | 0% | 0 | 2% | 0.5 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | YES |  |  |  | 0% | 90% |  |  |  | 0 | 0.5 |  |  |  | User to provide median demand and dispersion values. The values listed are default PACT values and do not represent the response of this component. User to confirm damage state, repair, lead time, and casualty data. This component requires user specified cost and time consequence data. Values within PACT are defaults (equal to zero) and do not represent actual consequence. | By User | By User | By User | By User | none | none |  |  |  | No | None | Yes
B2022.031 | B2022.031 | Midrise stick-built curtain wall, Config: Monolithic, Lamination: Not laminated, Glass Type: Annealed, Details: 1/4 in. (6 mm) AN monolithic; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 6:5 sealant = dry | None | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 303 | SF 30 | NO | NO | Glass cracking. | Glass falls from frame. |  |  |  | 1 | 1 |  |  |  | 0.0138 | 0.0219 |  |  |  | 0.0797 | 0.1923 |  |  |  | 0.25 | 0.25 |  |  |  | 0.25 | 0.3 |  |  |  | NO | YES | Superior | Average | Superior | Superior | Replace cracked glass panel. | Replace cracked glass panel; cover exposure in meantime. |  |  |  | NO | NO |  |  |  | NO | YES |  |  |  | Not Applicable | 36 SF |  |  |  | 0% | 0 | 2% | 0.5 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | YES |  |  |  | 0% | 90% |  |  |  | 0 | 0.5 |  |  |  | None | By User | By User | By User | Not Given | B2022.001a-DS1-1.JPG | B2022.001a-DS2-1.JPG |  |  |  | No | 2011-08-24 Negative probability below 0.5% drift - Overlap deemed acceptable. | Yes
B2022.032 | B2022.032 | Midrise stick-built curtain wall, Config: Monolithic, Lamination: Not laminated, Glass Type: Annealed, Details: 1/4 in. (6 mm) AN monolithic; glass-frame clearance = 0 in. (0 mm); aspect ratio = 6:5 sealant = dry | None | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 304 | SF 30 | NO | NO | Glass cracking. | Glass falls from frame. |  |  |  | 1 | 1 |  |  |  | 0.0088 | 0.0108 |  |  |  | 0.0321 | 0.0262 |  |  |  | 0.25 | 0.25 |  |  |  | 0.25 | 0.25 |  |  |  | NO | YES | Superior | Average | Superior | Superior | Replace cracked glass panel. | Replace cracked glass panel; cover exposure in meantime. |  |  |  | NO | NO |  |  |  | NO | YES |  |  |  | Not Applicable | 36 SF |  |  |  | 0% | 0 | 2% | 0.5 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | YES |  |  |  | 0% | 90% |  |  |  | 0 | 0.5 |  |  |  | None | By User | By User | By User | Not Given | B2022.001a-DS1-1.JPG | B2022.001a-DS2-1.JPG |  |  |  | No | None | Yes
B2022.033 | B2022.033 | Midrise stick-built curtain wall, Config: Monolithic, Lamination: Not laminated, Glass Type: Annealed, Details: 1/4 in. (6 mm) AN monolithic; glass-frame clearance = 0.13 in. (3 mm); aspect ratio = 6:5 sealant = dry | None | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 305 | SF 30 | NO | NO | Glass cracking. | Glass falls from frame. |  |  |  | 1 | 1 |  |  |  | 0.0084 | 0.0107 |  |  |  | 0.0757 | 0.257 |  |  |  | 0.25 | 0.25 |  |  |  | 0.25 | 0.35 |  |  |  | NO | YES | Superior | Average | Superior | Superior | Replace cracked glass panel. | Replace cracked glass panel; cover exposure in meantime. |  |  |  | NO | NO |  |  |  | NO | YES |  |  |  | Not Applicable | 36 SF |  |  |  | 0% | 0 | 2% | 0.5 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | YES |  |  |  | 0% | 90% |  |  |  | 0 | 0.5 |  |  |  | None | By User | By User | By User | Not Given | B2022.001a-DS1-1.JPG | B2022.001a-DS2-1.JPG |  |  |  | No | 2011-08-24 Negative probability below 0.5% drift - Overlap deemed acceptable. | Yes
B2022.034 | B2022.034 | Midrise stick-built curtain wall, Config: Monolithic, Lamination: Not laminated, Glass Type: Annealed, Details: 1/4 in. (6 mm) AN monolithic; glass-frame clearance = 0.25 in. (6 mm); aspect ratio = 6:5 sealant = dry | None | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 306 | SF 30 | NO | NO | Glass cracking. | Glass falls from frame. |  |  |  | 1 | 1 |  |  |  | 0.0147 | 0.0164 |  |  |  | 0.0299 | 0.0799 |  |  |  | 0.25 | 0.25 |  |  |  | 0.25 | 0.25 |  |  |  | NO | YES | Superior | Average | Superior | Superior | Replace cracked glass panel. | Replace cracked glass panel; cover exposure in meantime. |  |  |  | NO | NO |  |  |  | NO | YES |  |  |  | Not Applicable | 36 SF |  |  |  | 0% | 0 | 2% | 0.5 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | YES |  |  |  | 0% | 90% |  |  |  | 0 | 0.5 |  |  |  | None | By User | By User | By User | Not Given | B2022.001a-DS1-1.JPG | B2022.001a-DS2-1.JPG |  |  |  | No | None | Yes
B2022.035 | B2022.035 | Midrise stick-built curtain wall, Config: Monolithic, Lamination: Not laminated, Glass Type: Annealed, Details: 1/4 in. (6 mm) AN monolithic; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 2:1 sealant = dry | None | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 307 | SF 32 | NO | NO | Glass cracking. | Glass falls from frame. |  |  |  | 1 | 1 |  |  |  | 0.0181 | 0.0212 |  |  |  | 0.0782 | User to Calculate |  |  |  | 0.25 | 0.25 |  |  |  | 0.25 | 0.25 |  |  |  | NO | YES | Superior | Average | Superior | Superior | Replace cracked glass panel. | Replace cracked glass panel; cover exposure in meantime. |  |  |  | NO | NO |  |  |  | NO | YES |  |  |  | Not Applicable | 36 SF |  |  |  | 0% | 0 | 2% | 0.5 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | YES |  |  |  | 0% | 90% |  |  |  | 0 | 0.5 |  |  |  | None | By User | By User | By User | Not Given | B2022.001a-DS1-1.JPG | B2022.001a-DS2-1.JPG |  |  |  | No | None | Yes
B2022.036 | B2022.036 | Midrise stick-built curtain wall, Config: Monolithic, Lamination: Not laminated, Glass Type: Annealed, Details: 1/4 in. (6 mm) AN monolithic; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 1:2 sealant = dry | None | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 308 | SF 32 | NO | NO | Glass cracking. | Glass falls from frame. |  |  |  | 1 | 1 |  |  |  | 0.022 | 0.0257 |  |  |  | 0.1189 | 0.1043 |  |  |  | 0.25 | 0.25 |  |  |  | 0.3 | 0.25 |  |  |  | NO | YES | Superior | Average | Superior | Superior | Replace cracked glass panel. | Replace cracked glass panel; cover exposure in meantime. |  |  |  | NO | NO |  |  |  | NO | YES |  |  |  | Not Applicable | 36 SF |  |  |  | 0% | 0 | 2% | 0.5 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | YES |  |  |  | 0% | 90% |  |  |  | 0 | 0.5 |  |  |  | None | By User | By User | By User | Not Given | B2022.001a-DS1-1.JPG | B2022.001a-DS2-1.JPG |  |  |  | No | None | Yes
B2022.037 | B2022.037 | Midrise stick-built curtain wall, Config: Monolithic, Lamination: Not laminated, Glass Type: Annealed, Details: 1/4 in. (6 mm) AN monolithic, 2-sided SSG, Center Panel; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 6:5 sealant = wet | None | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 309 | SF 30 | NO | NO | Glass cracking. | Glass falls from frame. |  |  |  | 1 | 1 |  |  |  | 0.0288 | 0.04 |  |  |  | Not Specified | Not Specified |  |  |  | Not Specified | Not Specified |  |  |  | 0.26 | 0.6 |  |  |  | NO | YES | Not Rated | Not Rated | Not Rated | Not Rated | Replace cracked glass panel. | Replace cracked glass panel; cover exposure in meantime. |  |  |  | NO | NO |  |  |  | NO | YES |  |  |  | Not Applicable | 36 SF |  |  |  | 0% | 0 | 2% | 0.5 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | YES |  |  |  | 0% | 90% |  |  |  | 0 | 0.5 |  |  |  | None | By User | By User | By User | By User | none | none |  |  |  | No | 2018-02-12 Added damage state data | Yes
B2022.038 | B2022.038 | Midrise stick-built curtain wall, Config: Monolithic, Lamination: Not laminated, Glass Type: Annealed, Details: 1/4 in. (6 mm) AN monolithic, 2-sided SSG, Outside Panel; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 6:5 sealant = wet | None | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 310 | SF 30 | NO | NO | Glass cracking. | Glass falls from frame. |  |  |  | 1 | 1 |  |  |  | 0.0273 | 0.0286 |  |  |  | Not Specified | Not Specified |  |  |  | Not Specified | Not Specified |  |  |  | 0.28 | 0.28 |  |  |  | NO | YES | Not Rated | Not Rated | Not Rated | Not Rated | Replace cracked glass panel. | Replace cracked glass panel; cover exposure in meantime. |  |  |  | NO | NO |  |  |  | NO | YES |  |  |  | Not Applicable | 36 SF |  |  |  | 0% | 0 | 2% | 0.5 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | YES |  |  |  | 0% | 90% |  |  |  | 0 | 0.5 |  |  |  | None | By User | By User | By User | By User | none | none |  |  |  | No | 2018-02-12 Added damage state data | Yes
B2022.039 | B2022.039 | Midrise stick-built curtain wall, Config: Monolithic, Lamination: Not laminated, Glass Type: Annealed, Details: 1/4 in. (6 mm) AN monolithic; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 6:5 sealant = dry | None | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 311 | SF 30 | NO | NO | Glass cracking. | Glass falls from frame. |  |  |  | 1 | 1 |  |  |  | 0.027 | 0.029 |  |  |  | Not Specified | Not Specified |  |  |  | Not Specified | Not Specified |  |  |  | 0.26 | 0.26 |  |  |  | NO | YES | Not Rated | Not Rated | Not Rated | Not Rated | Replace cracked glass panel. | Replace cracked glass panel; cover exposure in meantime. |  |  |  | NO | NO |  |  |  | NO | YES |  |  |  | Not Applicable | 36 SF |  |  |  | 0% | 0 | 2% | 0.5 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | YES |  |  |  | 0% | 90% |  |  |  | 0 | 0.5 |  |  |  | None | By User | By User | By User | By User | none | none |  |  |  | No | 2018-02-12 Added damage state data | Yes
B2022.040 | B2022.040 | Midrise stick-built curtain wall, Config: Monolithic, Lamination: Not laminated, Glass Type: Annealed, Details: 1/4 in. (6 mm) AN monolithic; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 2:1 sealant = dry | None | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 312 | SF 30 | NO | NO | Glass cracking. | Glass falls from frame. |  |  |  | 1 | 1 |  |  |  | 0.02 | 0.023 |  |  |  | Not Specified | Not Specified |  |  |  | Not Specified | Not Specified |  |  |  | 0.26 | 0.28 |  |  |  | NO | YES | Not Rated | Not Rated | Not Rated | Not Rated | Replace cracked glass panel. | Replace cracked glass panel; cover exposure in meantime. |  |  |  | NO | NO |  |  |  | NO | YES |  |  |  | Not Applicable | 36 SF |  |  |  | 0% | 0 | 2% | 0.5 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | YES |  |  |  | 0% | 90% |  |  |  | 0 | 0.5 |  |  |  | None | By User | By User | By User | By User | none | none |  |  |  | No | 2018-02-12 Added damage state data | Yes
B2022.041 | B2022.041 | Midrise stick-built curtain wall, Config: Monolithic, Lamination: Not laminated, Glass Type: Annealed, Details: 1/4 in. (6 mm) AN monolithic; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 1:2 sealant = dry | None | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 313 | SF 30 | NO | NO | Glass cracking. | Glass falls from frame. |  |  |  | 1 | 1 |  |  |  | 0.024 | 0.027 |  |  |  | Not Specified | Not Specified |  |  |  | Not Specified | Not Specified |  |  |  | 0.25 | 0.32 |  |  |  | NO | YES | Not Rated | Not Rated | Not Rated | Not Rated | Replace cracked glass panel. | Replace cracked glass panel; cover exposure in meantime. |  |  |  | NO | NO |  |  |  | NO | YES |  |  |  | Not Applicable | 36 SF |  |  |  | 0% | 0 | 2% | 0.5 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | YES |  |  |  | 0% | 90% |  |  |  | 0 | 0.5 |  |  |  | None | By User | By User | By User | By User | none | none |  |  |  | No | 2018-02-12 Added damage state data | Yes
B2022.051 | B2022.051 | Midrise stick-built curtain wall, Config: Monolithic, Lamination: Not laminated, Glass Type: Full tempered, Details: 1/4 in. (6 mm) FT monolithic, 2-sided SSG, Center Panel; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 6:5 sealant = wet | None | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 314 | SF 30 | NO | NO | Glass cracking. | Glass falls from frame. |  |  |  | 1 | 1 |  |  |  | 0.043 | 0.05 |  |  |  | Not Specified | Not Specified |  |  |  | Not Specified | Not Specified |  |  |  | 0.25 | 0.25 |  |  |  | NO | YES | Not Rated | Not Rated | Not Rated | Not Rated | Replace cracked glass panel. | Replace cracked glass panel; cover exposure in meantime. |  |  |  | NO | NO |  |  |  | NO | YES |  |  |  | Not Applicable | 36 SF |  |  |  | 0% | 0 | 2% | 0.5 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | YES |  |  |  | 0% | 90% |  |  |  | 0 | 0.5 |  |  |  | None | By User | By User | By User | By User | none | none |  |  |  | No | 2018-02-12 Added damage state data | Yes
B2022.052 | B2022.052 | Midrise stick-built curtain wall, Config: Monolithic, Lamination: Not laminated, Glass Type: Full tempered, Details: 1/4 in. (6 mm) FT monolithic, 2-sided SSG, Outside Panel; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 6:5 sealant = wet | None | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 315 | SF 30 | NO | NO | Glass cracking. | Glass falls from frame. |  |  |  | 1 | 1 |  |  |  | 0.042 | 0.052 |  |  |  | Not Specified | Not Specified |  |  |  | Not Specified | Not Specified |  |  |  | 0.3 | 0.3 |  |  |  | NO | YES | Not Rated | Not Rated | Not Rated | Not Rated | Replace cracked glass panel. | Replace cracked glass panel; cover exposure in meantime. |  |  |  | NO | NO |  |  |  | NO | YES |  |  |  | Not Applicable | 36 SF |  |  |  | 0% | 0 | 2% | 0.5 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | YES |  |  |  | 0% | 90% |  |  |  | 0 | 0.5 |  |  |  | None | By User | By User | By User | By User | none | none |  |  |  | No | 2018-02-12 Added damage state data | Yes
B2022.053 | B2022.053 | Midrise stick-built curtain wall, Config: Monolithic, Lamination: Not laminated, Glass Type: Full tempered, Details: 1/4 in. (6 mm) FT monolithic, Seamed Edge; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 6:5 sealant = dry | None | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 316 | SF 30 | NO | NO | Glass cracking. | Glass falls from frame. |  |  |  | 1 | 1 |  |  |  | 0.029 | 0.039 |  |  |  | Not Specified | Not Specified |  |  |  | Not Specified | Not Specified |  |  |  | 0.3 | 0.3 |  |  |  | NO | YES | Not Rated | Not Rated | Not Rated | Not Rated | Replace cracked glass panel. | Replace cracked glass panel; cover exposure in meantime. |  |  |  | NO | NO |  |  |  | NO | YES |  |  |  | Not Applicable | 36 SF |  |  |  | 0% | 0 | 2% | 0.5 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | YES |  |  |  | 0% | 90% |  |  |  | 0 | 0.5 |  |  |  | None | By User | By User | By User | By User | none | none |  |  |  | No | 2018-02-12 Added damage state data | Yes
B2022.054 | B2022.054 | Midrise stick-built curtain wall, Config: Monolithic, Lamination: Not laminated, Glass Type: Full tempered, Details: 1/4 in. (6 mm) FT monolithic, Polished Edge; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 6:5 sealant = dry | None | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 317 | SF 30 | NO | NO | Glass cracking. | Glass falls from frame. |  |  |  | 1 | 1 |  |  |  | 0.033 | 0.043 |  |  |  | Not Specified | Not Specified |  |  |  | Not Specified | Not Specified |  |  |  | 0.25 | 0.25 |  |  |  | NO | YES | Not Rated | Not Rated | Not Rated | Not Rated | Replace cracked glass panel. | Replace cracked glass panel; cover exposure in meantime. |  |  |  | NO | NO |  |  |  | NO | YES |  |  |  | Not Applicable | 36 SF |  |  |  | 0% | 0 | 2% | 0.5 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | YES |  |  |  | 0% | 90% |  |  |  | 0 | 0.5 |  |  |  | None | By User | By User | By User | By User | none | none |  |  |  | No | 2018-02-12 Added damage state data | Yes
B2022.061 | B2022.061 | Midrise stick-built curtain wall, Config: Monolithic, Lamination: Not laminated, Glass Type: Heat strengthened, Details: 1/4 in. (6 mm) HS monolithic; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 6:5 sealant = dry | None | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 318 | SF 30 | NO | NO | Glass cracking. | Glass falls from frame. |  |  |  | 1 | 1 |  |  |  | 0.024 | 0.025 |  |  |  | Not Specified | Not Specified |  |  |  | Not Specified | Not Specified |  |  |  | 0.29 | 0.29 |  |  |  | NO | YES | Not Rated | Not Rated | Not Rated | Not Rated | Replace cracked glass panel. | Replace cracked glass panel; cover exposure in meantime. |  |  |  | NO | NO |  |  |  | NO | YES |  |  |  | Not Applicable | 36 SF |  |  |  | 0% | 0 | 2% | 0.5 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | YES |  |  |  | 0% | 90% |  |  |  | 0 | 0.5 |  |  |  | None | By User | By User | By User | By User | none | none |  |  |  | No | 2018-02-12 Added damage state data | Yes
B2022.071 | B2022.071 | Midrise stick-built curtain wall, Config: Symmetric insulating glass units (dual-pane, equal-thickness IGU), Lamination: Laminated, Glass Type: Annealed, Details: 1/4 in. (6 mm) inner AN / 1/4 in. (6 mm) outer AN LAM (0.030 PVB) IGU; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 6:5 sealant = dry | None | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 319 | SF 30 | NO | NO | Gasket seal failure. | Glass cracking. | Glass falls out. |  |  | 1 | 1 | 1 |  |  | 0.027 | 0.0276 | 0.0303 |  |  | 0.2 | 0.1614 | 0.1472 |  |  | 0.25 | 0.25 | 0.25 |  |  | 0.3 | 0.3 | 0.3 |  |  | NO | YES | Superior | Average | Superior | Superior | Remove glass panel and replace damaged gaskets. | Replace cracked glass panel. | Replace cracked glass panel; cover exposure in meantime. |  |  | NO | NO | NO |  |  | NO | NO | YES |  |  | Not Applicable | Not Applicable | 36 SF |  |  | 0% | 0 | 0% | 0 | 2% | 0.5 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | NO | YES |  |  | 0% | 0% | 90% |  |  | 0 | 0 | 0.5 |  |  | None | By User | By User | By User | Not Given | B2022.003-DS1-1.JPG | B2022.001a-DS1-1.JPG | B2022.001a-DS2-1.JPG |  |  | No | None | Yes
B2022.072 | B2022.072 | Midrise stick-built curtain wall, Config: Symmetric insulating glass units (dual-pane, equal-thickness IGU), Lamination: Laminated, Glass Type: Annealed, Details: 1/4 in. (6 mm) inner AN / 1/4 in. (6 mm) outer AN LAM (0.060 PVB) IGU; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 6:5 sealant = dry | None | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 320 | SF 30 | NO | NO | Gasket seal failure. | Glass cracking. | Glass falls out. |  |  | 1 | 1 | 1 |  |  | 0.0262 | 0.0266 | 0.0299 |  |  | 0.1953 | 0.2031 | 0.2396 |  |  | 0.25 | 0.25 | 0.25 |  |  | 0.3 | 0.3 | 0.3 |  |  | NO | YES | Superior | Average | Superior | Superior | Remove glass panel and replace damaged gaskets. | Replace cracked glass panel. | Replace cracked glass panel; cover exposure in meantime. |  |  | NO | NO | NO |  |  | NO | NO | YES |  |  | Not Applicable | Not Applicable | 36 SF |  |  | 0% | 0 | 0% | 0 | 2% | 0.5 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | NO | YES |  |  | 0% | 0% | 90% |  |  | 0 | 0 | 0.5 |  |  | None | By User | By User | By User | Not Given | B2022.003-DS1-1.JPG | B2022.001a-DS1-1.JPG | B2022.001a-DS2-1.JPG |  |  | No | 2011-08-24 DS3 beta changed from 0.35 to 0.3 to avoid negative probabilities. | Yes
B2022.081 | B2022.081 | Midrise stick-built curtain wall, Config: Symmetric insulating glass units (dual-pane, equal-thickness IGU), Lamination: Not laminated, Glass Type: Annealed, Details: 1 in. (25 mm) AN insulating glass unit (IGU) [1/4 in. (6 mm) inner and outer panes]; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 6:5 sealant = dry | None | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 321 | SF 30 | NO | NO | Glass cracking. | Glass falls from frame. |  |  |  | 1 | 1 |  |  |  | 0.0234 | 0.031 |  |  |  | 0.1663 | 0.1558 |  |  |  | 0.25 | 0.25 |  |  |  | 0.3 | 0.3 |  |  |  | NO | YES | Superior | Average | Superior | Superior | Replace cracked glass panel. | Replace cracked glass panel; cover exposure in meantime. |  |  |  | NO | NO |  |  |  | NO | YES |  |  |  | Not Applicable | 36 SF |  |  |  | 0% | 0 | 2% | 0.5 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | YES |  |  |  | 0% | 90% |  |  |  | 0 | 0.5 |  |  |  | None | By User | By User | By User | Not Given | B2022.001a-DS1-1.JPG | B2022.001a-DS2-1.JPG |  |  |  | No | None | Yes
B2022.082 | B2022.082 | Midrise stick-built curtain wall, Config: Symmetric insulating glass units (dual-pane, equal-thickness IGU), Lamination: Not laminated, Glass Type: Annealed, Details: 1 in. (25 mm) AN IGU [1/4 in. (6 mm) inner and outer panes]; glass-frame clearance = 0.25 in. (6 mm); aspect ratio = 6:5 sealant = dry | None | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 322 | SF 30 | NO | NO | Glass cracking. | Glass falls from frame. |  |  |  | 1 | 1 |  |  |  | 0.0142 | 0.0221 |  |  |  | User to Calculate | User to Calculate |  |  |  | 0.25 | 0.25 |  |  |  | 0.25 | 0.25 |  |  |  | NO | YES | Superior | Average | Superior | Superior | Replace cracked glass panel. | Replace cracked glass panel; cover exposure in meantime. |  |  |  | NO | NO |  |  |  | NO | YES |  |  |  | Not Applicable | 36 SF |  |  |  | 0% | 0 | 2% | 0.5 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | YES |  |  |  | 0% | 90% |  |  |  | 0 | 0.5 |  |  |  | None | By User | By User | By User | Not Given | B2022.001a-DS1-1.JPG | B2022.001a-DS2-1.JPG |  |  |  | No | None | Yes
B2022.083 | B2022.083 | Midrise stick-built curtain wall, Config: Symmetric insulating glass units (dual-pane, equal-thickness IGU), Lamination: Not laminated, Glass Type: Annealed, Details: 1 in. (25 mm) AN IGU [1/4 in. (6 mm) inner and outer panes], 2-sided SSG, Center Panel; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 6:5 sealant = wet | None | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 323 | SF 30 | NO | NO | Gasket seal failure. | Glass cracking. | Glass falls out. |  |  | 1 | 1 | 1 |  |  | 0.026 | 0.051 | 0.054 |  |  | Not Specified | Not Specified | Not Specified |  |  | Not Specified | Not Specified | Not Specified |  |  | 0.11 | 0.25 | 0.25 |  |  | NO | YES | Not Rated | Not Rated | Not Rated | Not Rated | Remove glass panel and replace damaged gaskets. | Replace cracked glass panel. | Replace cracked glass panel; cover exposure in meantime. |  |  | NO | NO | NO |  |  | NO | NO | YES |  |  | Not Applicable | Not Applicable | 36 SF |  |  | 0% | 0 | 0% | 0 | 2% | 0.5 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | NO | YES |  |  | 0% | 0% | 90% |  |  | 0 | 0 | 0.5 |  |  | None | By User | By User | By User | By User | none |  |  |  |  | No | None | Yes
B2022.084 | B2022.084 | Midrise stick-built curtain wall, Config: Symmetric insulating glass units (dual-pane, equal-thickness IGU), Lamination: Not laminated, Glass Type: Annealed, Details: 1 in. (25 mm) AN IGU [1/4 in. (6 mm) inner and outer panes], 2-sided SSG, Outside Panel; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 6:5 sealant = wet | None | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 324 | SF 30 | NO | NO | Gasket seal failure. | Glass cracking. | Glass falls out. |  |  | 1 | 1 | 1 |  |  | 0.026 | 0.051 | 0.054 |  |  | Not Specified | Not Specified | Not Specified |  |  | Not Specified | Not Specified | Not Specified |  |  | 0.11 | 0.25 | 0.25 |  |  | NO | YES | Not Rated | Not Rated | Not Rated | Not Rated | Remove glass panel and replace damaged gaskets. | Replace cracked glass panel. | Replace cracked glass panel; cover exposure in meantime. |  |  | NO | NO | NO |  |  | NO | NO | YES |  |  | Not Applicable | Not Applicable | 36 SF |  |  | 0% | 0 | 0% | 0 | 2% | 0.5 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | NO | YES |  |  | 0% | 0% | 90% |  |  | 0 | 0 | 0.5 |  |  | None | By User | By User | By User | By User | none |  |  |  |  | No | 2018-02-12 Added damage state data | Yes
B2022.091 | B2022.091 | Midrise stick-built curtain wall, Config: Symmetric insulating glass units (dual-pane, equal-thickness IGU), Lamination: Not laminated, Glass Type: Full tempered, Details: 1 in. (25 mm) FT IGU [1/4 in. (6 mm) inner and outer panes]; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 6:5 sealant = dry | None | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 325 | SF 30 | NO | NO | Gasket seal failure. | Glass cracking. | Glass falls out. |  |  | 1 | 1 | 1 |  |  | 0.026 | 0.031 | 0.032 |  |  | Not Specified | Not Specified | Not Specified |  |  | Not Specified | Not Specified | Not Specified |  |  | 0.11 | 0.25 | 0.25 |  |  | NO | YES | Not Rated | Not Rated | Not Rated | Not Rated | Remove glass panel and replace damaged gaskets. | Replace cracked glass panel. | Replace cracked glass panel; cover exposure in meantime. |  |  | NO | NO | NO |  |  | NO | NO | YES |  |  | Not Applicable | Not Applicable | 36 SF |  |  | 0% | 0 | 0% | 0 | 2% | 0.5 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | NO | YES |  |  | 0% | 0% | 90% |  |  | 0 | 0 | 0.5 |  |  | None | By User | By User | By User | By User | none |  |  |  |  | No | 2018-02-12 Added damage state data | Yes
B2022.101 | B2022.101 | Midrise stick-built curtain wall, Config: Symmetric insulating glass units (dual-pane, equal-thickness IGU), Lamination: Not laminated, Glass Type: Heat strengthened, Details: 1 in. (25 mm) HS IGU [1/4 in. (6 mm) inner and outer panes]; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 6:5 sealant = dry | None | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 326 | SF 30 | NO | NO | Gasket seal failure. | Glass cracking. | Glass falls out. |  |  | 1 | 1 | 1 |  |  | 0.026 | 0.027 | 0.028 |  |  | Not Specified | Not Specified | Not Specified |  |  | Not Specified | Not Specified | Not Specified |  |  | 0.3 | 0.3 | 0.3 |  |  | NO | YES | Not Rated | Not Rated | Not Rated | Not Rated | Remove glass panel and replace damaged gaskets. | Replace cracked glass panel. | Replace cracked glass panel; cover exposure in meantime. |  |  | NO | NO | NO |  |  | NO | NO | YES |  |  | Not Applicable | Not Applicable | 36 SF |  |  | 0% | 0 | 0% | 0 | 2% | 0.5 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | NO | YES |  |  | 0% | 0% | 90% |  |  | 0 | 0 | 0.5 |  |  | None | By User | By User | By User | By User | none |  |  |  |  | No | 2018-02-12 Added damage state data | Yes
B2022.201 | B2022.201 | Curtain Walls - Unitized curtain wall (also generic unitized curtain wall), Config: Symmetric insulating glass units (dual-pane, equal-thickness IGU), Lamination: Not laminated, Glass Type: Full tempered, Details: 1-1/4 in. (32 mm) FT IGU [1/4 in. (6 mm) inner and outer panes], 4-sided SSG, VHBTM SGTTM; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = Varies sealant = wet | None | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 327 | SF 30 | NO | NO | Gasket seal failure. | Glass cracking. | Glass falls out. |  |  | 1 | 1 | 1 |  |  | 0.026 | 0.05 | 0.1 |  |  | Not Specified | Not Specified | Not Specified |  |  | Not Specified | Not Specified | Not Specified |  |  | 0.45 | 0.25 | 0.25 |  |  | NO | YES | Not Rated | Not Rated | Not Rated | Not Rated | Remove glass panel and replace damaged gaskets. | Replace cracked glass panel. | Replace cracked glass panel; cover exposure in meantime. |  |  | NO | NO | NO |  |  | NO | NO | YES |  |  | Not Applicable | Not Applicable | 36 SF |  |  | 0% | 0 | 0% | 0 | 2% | 0.5 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | NO | YES |  |  | 0% | 0% | 90% |  |  | 0 | 0 | 0.5 |  |  | Damage state DS3 of glass fall out did not occur in physical testing to 10% drift. DS3 0.1 median demand is intentional. | By User | By User | By User | By User | none |  |  |  |  | No | 2018-02-12 Added damage state data | YES
B2023.001 | B2023.001 | Generic Storefront, Config: Monolithic, Lamination: Unknown, Glass Type: Unknown, Details: Aspect ratio = 6:5, Other details Unknown | None | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 328 | SF 30 | NO | No | Gasket seal failure. | Glass cracking. | Glass falls out. |  |  | 1 | 1 | 1 |  |  | 0.029 | 0.0473 | 0.07 |  |  | 0.4492 | 0.1448 | 0.99 |  |  | 0.25 | 0.25 | 0.25 |  |  | 0.5 | 0.25 | 0.25 |  |  | NO | YES | Superior | Average | Superior | Superior | Remove glass panel and replace damaged gaskets. | Replace cracked glass panel. | Replace cracked glass panel; cover exposure in meantime. |  |  | NO | NO | NO |  |  | NO | NO | YES |  |  | Not Applicable | Not Applicable | 36 SF |  |  | 0% | 0 | 0% | 0 | 25% | 0.5 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | NO | YES |  |  | 0% | 0% | 50% |  |  | 0 | 0 | 0.5 |  |  | None This component requires user specified cost and time consequence data. Values within PACT are defaults (equal to zero) and do not represent actual consequence. | By User | By User | By User | Not Given | B2022.003-DS1-1.JPG | B2022.001a-DS1-1.JPG | B2022.001a-DS2-1.JPG |  |  | No | 2011-08-24 DS3 beta changed from 1 to 0.3 to avoid negative probabilities. | Yes
B2023.002 | B2023.002 | Generic Storefront, Config: IGU, Lamination: Unknown, Glass Type: Unknown, Details: Aspect ratio = 6:5, Other details Unknown | None | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 329 | SF 30 | NO | No | Gasket seal failure. | Glass cracking. | Glass falls out. |  |  | 1 | 1 | 1 |  |  | 0.0423 | 0.059 | 0.0665 |  |  | 0.04 | 0.1706 | 0.06 |  |  | 0.25 | 0.25 | 0.25 |  |  | 0.3 | 0.25 | 0.35 |  |  | NO | YES | Superior | Average | Superior | Superior | Remove glass panel and replace damaged gaskets. | Replace cracked glass panel. | Replace cracked glass panel; cover exposure in meantime. |  |  | NO | NO | NO |  |  | NO | NO | YES |  |  | Not Applicable | Not Applicable | 36 SF |  |  | 0% | 0 | 0% | 0 | 25% | 0.5 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | NO | YES |  |  | 0% | 0% | 50% |  |  | 0 | 0 | 0.5 |  |  | None | By User | By User | By User | Not Given | B2022.003-DS1-1.JPG | B2022.001a-DS1-1.JPG | B2022.001a-DS2-1.JPG |  |  | No | None | Yes
B2023.011 | B2023.011 | Storefront, Config: Monolithic, Lamination: Laminated, Glass Type: Annealed, Details: 1/4 in. (6 mm) AN LAM (0.030 PVB); glass-frame clearance = 0.41 in. (10 mm); aspect ratio = 6:5 sealant = dry | None | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 330 | SF 30 | NO | No | Gasket seal failure. | Glass cracking. | Glass falls out. |  |  | 1 | 1 | 1 |  |  | 0.029 | 0.0567 | 0.08 |  |  | 0.4492 | 0.1448 | 0.99 |  |  | 0.25 | 0.25 | 0.25 |  |  | 0.5 | 0.3 | 0.3 |  |  | NO | YES | Superior | Average | Superior | Superior | Remove glass panel and replace damaged gaskets. | Replace cracked glass panel. | Replace cracked glass panel; cover exposure in meantime. |  |  | NO | NO | NO |  |  | NO | NO | YES |  |  | Not Applicable | Not Applicable | 36 SF |  |  | 0% | 0 | 0% | 0 | 25% | 0.5 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | NO | YES |  |  | 0% | 0% | 50% |  |  | 0 | 0 | 0.5 |  |  | None | By User | By User | By User | Not Given | B2022.003-DS1-1.JPG | B2022.001a-DS1-1.JPG | B2022.001a-DS2-1.JPG |  |  | No | 2011-08-24 DS3 beta changed from 1 to 0.3 to avoid negative probabilities. | Yes
B2023.021 | B2023.021 | Storefront, Config: Monolithic, Lamination: Not laminated, Glass Type: Annealed, Details: 1/4 in. (6 mm) AN monolithic; glass-frame clearance = 0.41 in. (10 mm); aspect ratio = 6:5 sealant = dry | None | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 331 | SF 30 | NO | No | Gasket seal failure. | Glass cracking. | Glass falls out. |  |  | 1 | 1 | 1 |  |  | 0.0303 | 0.0413 | 0.051 |  |  | 0.424 | 0.1341 | 0.147 |  |  | 0.25 | 0.25 | 0.25 |  |  | 0.5 | 0.3 | 0.3 |  |  | NO | YES | Superior | Average | Superior | Superior | Remove glass panel and replace damaged gaskets. | Replace cracked glass panel. | Replace cracked glass panel; cover exposure in meantime. |  |  | NO | NO | NO |  |  | NO | NO | YES |  |  | Not Applicable | Not Applicable | 36 SF |  |  | 0% | 0 | 0% | 0 | 25% | 0.5 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | NO | YES |  |  | 0% | 0% | 50% |  |  | 0 | 0 | 0.5 |  |  | None | By User | By User | By User | Not Given | B2022.003-DS1-1.JPG | B2022.001a-DS1-1.JPG | B2022.001a-DS2-1.JPG |  |  | No | 2011-08-24 Negative probability deemed acceptable. | Yes
B2023.031 | B2023.031 | Storefront, Config: Monolithic, Lamination: Not laminated, Glass Type: Full tempered, Details: 3/8 in. (10 mm) FT monolithic, Planar Specimen; glass-frame clearance = 0.5 in. (13 mm); aspect ratio = 1.93:1 sealant = wet | None | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 332 | SF 30 | NO | NO | Glass cracking. | Frame Damage |  |  |  | 1 | 1 |  |  |  | 0.03 | 0.052 |  |  |  | Not Specified | Not Specified |  |  |  | Not Specified | Not Specified |  |  |  | 1 | 0.4 |  |  |  | NO | YES | Not Rated | Not Rated | Not Rated | Not Rated | Remove glass, replace frame, reinstall glass | Remove and replace frame and glass. |  |  |  | NO | NO |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | NO |  |  |  | 0% | 0% |  |  |  | 0 | 0 |  |  |  | None | By User | By User | By User | By User | none | none |  |  |  | No | 2018-02-12 consequence data added. | YES
B2023.032 | B2023.032 | Storefront, Config: Monolithic, Lamination: Not laminated, Glass Type: Full tempered, Details: 3/8 in. (10 mm) FT monolithic, Corner Cond. Specimen, in-plane; glass-frame clearance = 0.5 in. (13 mm); aspect ratio = 1.93:1 sealant = wet | None | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 1 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 333 | SF 30 | NO | NO | Glass cracking. | Frame Damage |  |  |  | 1 | 1 |  |  |  | 0.042 | 0.05 |  |  |  | Not Specified | Not Specified |  |  |  | Not Specified | Not Specified |  |  |  | 0.55 | 1 |  |  |  | NO | YES | Not Rated | Not Rated | Not Rated | Not Rated | Remove glass, replace frame, reinstall glass | Remove and replace frame and glass. |  |  |  | NO | NO |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | NO |  |  |  | 0% | 0% |  |  |  | 0 | 0 |  |  |  | None | By User | By User | By User | By User | none |  |  |  |  | No | 2018-02-12 consequence data added. | YES
B2023.033 | B2023.033 | Storefront, Config: Monolithic, Lamination: Not laminated, Glass Type: Full tempered, Details: 3/8 in. (10 mm) FT monolithic, Corner Cond. Specimen, combined; glass-frame clearance = 0.5 in. (13 mm); aspect ratio = 1.93:1 sealant = wet | None | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 1 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 334 | SF 30 | NO | NO | Glass cracking. | Frame Damage |  |  |  | 1 | 1 |  |  |  | 0.03 | 0.05 |  |  |  | Not Specified | Not Specified |  |  |  | Not Specified | Not Specified |  |  |  | 1 | 0.4 |  |  |  | NO | YES | Not Rated | Not Rated | Not Rated | Not Rated | Remove glass, replace frame, reinstall glass | Remove and replace frame and glass. |  |  |  | NO | NO |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | NO |  |  |  | 0% | 0% |  |  |  | 0 | 0 |  |  |  | None | By User | By User | By User | By User | none |  |  |  |  | No | 2018-02-12 consequence data added. | YES
B2023.034 | B2023.034 | Storefront, Config: Monolithic, Lamination: Not laminated, Glass Type: Full tempered, Details: 3/8 in. (10 mm) FT monolithic, Corner Cond. Specimen, Short side; glass-frame clearance = 0.5 in. (13 mm); aspect ratio = 2.72:1 sealant = wet | None | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 1 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 335 | SF 30 | NO | NO | Glass cracking. | Frame Damage |  |  |  | 1 | 1 |  |  |  | 0.036 | 0.05 |  |  |  | Not Specified | Not Specified |  |  |  | Not Specified | Not Specified |  |  |  | 0.75 | 1 |  |  |  | NO | YES | Not Rated | Not Rated | Not Rated | Not Rated | Remove glass, replace frame, reinstall glass | Remove and replace frame and glass. |  |  |  | NO | NO |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | NO |  |  |  | 0% | 0% |  |  |  | 0 | 0 |  |  |  | None | By User | By User | By User | By User | none |  |  |  |  | No | 2018-02-12 consequence data added. | YES
B2023.041 | B2023.041 | Storefront, Config: Symmetric insulating glass units (dual-pane, equal-thickness IGU), Lamination: Not laminated, Glass Type: Annealed, Details: 1 in. (25 mm) AN IGU; glass-frame clearance = 0.59 in. (15 mm); aspect ratio = 6:5 sealant = dry | None | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 336 | SF 30 | NO | No | Gasket seal failure. | Glass cracking. | Glass falls out. |  |  | 1 | 1 | 1 |  |  | 0.0423 | 0.059 | 0.0665 |  |  | 0.1706 | 0.0639 | 0.039 |  |  | 0.25 | 0.25 | 0.25 |  |  | 0.3 | 0.25 | 0.25 |  |  | NO | YES | Superior | Average | Superior | Superior | Remove glass panel and replace damaged gaskets. | Replace cracked glass panel. | Replace cracked glass panel; cover exposure in meantime. |  |  | NO | NO | NO |  |  | NO | NO | YES |  |  | Not Applicable | Not Applicable | 36 SF |  |  | 0% | 0 | 0% | 0 | 25% | 0.5 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | NO | YES |  |  | 0% | 0% | 50% |  |  | 0 | 0 | 0.5 |  |  | None | By User | By User | By User | Not Given | B2022.003-DS1-1.JPG | B2022.001a-DS1-1.JPG | B2022.001a-DS2-1.JPG |  |  | No | None | Yes
B2023.051 | B2023.051 | Storefront, Config: Symmetric insulating glass units (dual-pane, equal-thickness IGU), Lamination: Not laminated, Glass Type: Full tempered, Details: 1 in. (25 mm) FT IGU [1/4 in. (6 mm) inner and outer panes], Planar Specimen; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 1.89:1 sealant = dry | None | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 337 | SF 30 | NO | NO | Panel damage (no glass damage). | Glass cracks. |  |  |  | 1 | 1 |  |  |  | 0.05 | 0.16 |  |  |  | Not Specified |  |  |  |  | Not Specified |  |  |  |  | 0.29 | 1 |  |  |  | NO | YES | Not Rated | Not Rated | Not Rated | Not Rated | Remove panel, repair frame, replace panel. | Remove panel, replace glass, replace panel. |  |  |  | NO | NO |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | NO |  |  |  | 0% | 0% |  |  |  | 0 | 0 |  |  |  | Median demand of 10% is intentional. Physical testing did not cause frame or glass cracking damage at 10% drift. | By User | By User | By User | By User | none | none |  |  |  | No | None | YES
B2023.052 | B2023.052 | Storefront, Config: Symmetric insulating glass units (dual-pane, equal-thickness IGU), Lamination: Not laminated, Glass Type: Full tempered, Details: 1 in. (25 mm) FT IGU [1/4 in. (6 mm) inner and outer panes], Corner Cond. Specimen, in-plane; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 1.89:1 sealant = dry | None | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 338 | SF 30 | NO | NO | Panel damage (no glass damage). | Glass cracks. |  |  |  | 1 | 1 |  |  |  | 0.054 | 0.16 |  |  |  | Not Specified |  |  |  |  | Not Specified |  |  |  |  | 0.28 | 1 |  |  |  | NO | YES | Not Rated | Not Rated | Not Rated | Not Rated | Remove panel, repair frame, replace panel. | Remove panel, replace glass, replace panel. |  |  |  | NO | NO |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | NO |  |  |  | 0% | 0% |  |  |  | 0 | 0 |  |  |  | Median demand of 10% is intentional. Physical testing did not cause frame or glass cracking damage at 10% drift. | By User | By User | By User | By User | none | none |  |  |  | No | None | YES
B2023.053 | B2023.053 | Storefront, Config: Symmetric insulating glass units (dual-pane, equal-thickness IGU), Lamination: Not laminated, Glass Type: Full tempered, Details: 1 in. (25 mm) FT IGU [1/4 in. (6 mm) inner and outer panes], Corner Cond. Specimen, combined; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 1.89:1 sealant = dry | None | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 339 | SF 30 | NO | NO | Panel damage (no glass damage). | Glass cracks. |  |  |  | 1 | 1 |  |  |  | 0.05 | 0.16 |  |  |  | Not Specified |  |  |  |  | Not Specified |  |  |  |  | 0.28 | 1 |  |  |  | NO | YES | Not Rated | Not Rated | Not Rated | Not Rated | Remove panel, repair frame, replace panel. | Remove panel, replace glass, replace panel. |  |  |  | NO | NO |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | NO |  |  |  | 0% | 0% |  |  |  | 0 | 0 |  |  |  | Median demand of 10% is intentional. Physical testing did not cause frame or glass cracking damage at 10% drift. | By User | By User | By User | By User | none | none |  |  |  | No | None | YES
B2023.054 | B2023.054 | Storefront, Config: Symmetric insulating glass units (dual-pane, equal-thickness IGU), Lamination: Not laminated, Glass Type: Full tempered, Details: 1 in. (25 mm) FT IGU [1/4 in. (6 mm) inner and outer panes], Corner Cond. Specimen, Short side; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 2.83:1 sealant = dry | None | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 340 | SF 30 | NO | NO | Panel damage (no glass damage). | Glass cracks. |  |  |  | 1 | 1 |  |  |  | 0.1 | 0.11 |  |  |  | Not Specified |  |  |  |  | Not Specified |  |  |  |  | 0.32 | 0.32 |  |  |  | NO | YES | Not Rated | Not Rated | Not Rated | Not Rated | Remove panel, repair frame, replace panel. | Remove panel, replace glass, replace panel. |  |  |  | NO | NO |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | NO |  |  |  | 0% | 0% |  |  |  | 0 | 0 |  |  |  | Median demand of 10% is intentional. Physical testing did not cause frame or glass cracking damage at 10% drift. | By User | By User | By User | By User | none | none |  |  |  | No | None | YES
B2023.055 | B2023.055 | Storefront, Config: Symmetric insulating glass units (dual-pane, equal-thickness IGU), Lamination: Not laminated, Glass Type: Full tempered, Details: 1 in. (25 mm) FT IGU [1/4 in. (6 mm) inner and outer panes], Planar Specimen; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 1.88:1 sealant = dry | None | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 341 | SF 30 | NO | NO | Panel damage (no glass damage). | Glass cracks. |  |  |  | 1 | 1 |  |  |  | 0.055 | 0.1 |  |  |  | Not Specified |  |  |  |  | Not Specified |  |  |  |  | 0.29 | 0.32 |  |  |  | NO | YES | Not Rated | Not Rated | Not Rated | Not Rated | Remove panel, repair frame, replace panel. | Remove panel, replace glass, replace panel. |  |  |  | NO | NO |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | NO |  |  |  | 0% | 0% |  |  |  | 0 | 0 |  |  |  | Median demand of 10% is intentional. Physical testing did not cause frame or glass cracking damage at 10% drift. | By User | By User | By User | By User | none | none |  |  |  | No | None | YES
B2023.056 | B2023.056 | Storefront, Config: Symmetric insulating glass units (dual-pane, equal-thickness IGU), Lamination: Not laminated, Glass Type: Full tempered, Details: 1 in. (25 mm) FT IGU [1/4 in. (6 mm) inner and outer panes], Corner Cond. Specimen, in-plane; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 1.88:1 sealant = dry | None | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 342 | SF 30 | NO | NO | Panel damage (no glass damage). | Glass cracks. |  |  |  | 1 | 1 |  |  |  | 0.055 | 0.1 |  |  |  | Not Specified |  |  |  |  | Not Specified |  |  |  |  | 0.32 | 0.32 |  |  |  | NO | YES | Not Rated | Not Rated | Not Rated | Not Rated | Remove panel, repair frame, replace panel. | Remove panel, replace glass, replace panel. |  |  |  | NO | NO |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | NO |  |  |  | 0% | 0% |  |  |  | 0 | 0 |  |  |  | Median demand of 10% is intentional. Physical testing did not cause frame or glass cracking damage at 10% drift. | By User | By User | By User | By User | none | none |  |  |  | No | None | YES
B2023.057 | B2023.057 | Storefront, Config: Symmetric insulating glass units (dual-pane, equal-thickness IGU), Lamination: Not laminated, Glass Type: Full tempered, Details: 1 in. (25 mm) FT IGU [1/4 in. (6 mm) inner and outer panes], Corner Cond. Specimen, combined; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 1.88:1 sealant = dry | None | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 343 | SF 30 | NO | NO | Panel damage (no glass damage). | Glass cracks. |  |  |  | 1 | 1 |  |  |  | 0.055 | 0.1 |  |  |  | Not Specified |  |  |  |  | Not Specified |  |  |  |  | 0.32 | 0.32 |  |  |  | NO | YES | Not Rated | Not Rated | Not Rated | Not Rated | Remove panel, repair frame, replace panel. | Remove panel, replace glass, replace panel. |  |  |  | NO | NO |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | NO |  |  |  | 0% | 0% |  |  |  | 0 | 0 |  |  |  | Median demand of 10% is intentional. Physical testing did not cause frame or glass cracking damage at 10% drift. | By User | By User | By User | By User | none | none |  |  |  | No | None | YES
B2023.058 | B2023.058 | Storefront, Config: Symmetric insulating glass units (dual-pane, equal-thickness IGU), Lamination: Not laminated, Glass Type: Full tempered, Details: 1 in. (25 mm) FT IGU [1/4 in. (6 mm) inner and outer panes], Corner Cond. Specimen, Short side; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 2.82:1 sealant = dry | None | Not Specified | Not Specified | Each | Each | Story Drift Ratio | Unit less | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 344 | SF 30 | NO | NO | Panel damage (no glass damage). | Glass cracks. |  |  |  | 1 | 1 |  |  |  | 0.09 | 0.1 |  |  |  | Not Specified |  |  |  |  | Not Specified |  |  |  |  | 1 | 0.32 |  |  |  | NO | YES | Not Rated | Not Rated | Not Rated | Not Rated | Remove panel, repair frame, replace panel. | Remove panel, replace glass, replace panel. |  |  |  | NO | NO |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | NO |  |  |  | 0% | 0% |  |  |  | 0 | 0 |  |  |  | Median demand of 10% is intentional. Physical testing did not cause frame or glass cracking damage at 10% drift. | By User | By User | By User | By User | none | none |  |  |  | No | None | YES
B3011.011 | B3011.011 | Concrete tile roof, tiles secured and compliant with UBC94 | Costing per roofing square (100 SF) | Any | Compliant with UBC 1994 | Each | Each | Peak Floor Acceleration | g | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 345 | SF 100 | NO | NO | Minor damage; tiles dislodged. | Major portion of tile dislodged. |  |  |  | 1 | 1 |  |  |  | 1.1 | 1.4 |  |  |  | 0.28 | 0.28 |  |  |  | 0.25 | 0.25 |  |  |  | 0.4 | 0.4 |  |  |  | NO | NO | Not Rated | Not Rated | Not Rated | Not Rated | Reinstall dislodged tiles. | Reinstall dislodged tiles. |  |  |  | NO | NO |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | YES |  |  |  | 0% | 50% |  |  |  | 0 | 0.5 |  |  |  | None | Not Given | By User | By User | Not Given | B3011.011-DS1-1.JPG | B3011.011-DS2-1.JPG |  |  |  | No | None | NO
B3011.012 | B3011.012 | Clay tile roof, tiles secured and compliant with UBC94 | Costing per roofing square (100 SF) | Any | Compliant with UBC 1994 | Each | Each | Peak Floor Acceleration | g | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 346 | SF 100 | NO | NO | Minor damage; tiles dislodged. | Major portion of tile dislodged. |  |  |  | 1 | 1 |  |  |  | 1.4 | 1.7 |  |  |  | 0.2 | 0.2 |  |  |  | 0.25 | 0.25 |  |  |  | 0.3 | 0.3 |  |  |  | NO | NO | Not Rated | Not Rated | Not Rated | Not Rated | Replace and install dislodged tiles (assume 5% of area) | Replace and install dislodged tiles. |  |  |  | NO | NO |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | YES |  |  |  | 0% | 50% |  |  |  | 0 | 0.5 |  |  |  | None | Not Given | By User | By User | Not Given | B3011.011-DS1-1.JPG | B3011.011-DS2-1.JPG |  |  |  | No | None | NO
B3011.013 | B3011.013 | Concrete tile roof, unsecured tiles | Costing per roofing square (100 SF) | Any | Compliant with UBC 1994 | Each | Each | Peak Floor Acceleration | g | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 347 | SF 100 | NO | NO | Minor damage; tiles dislodged. | Major portion of tile dislodged. |  |  |  | 1 | 1 |  |  |  | 0.5 | 0.7 |  |  |  | 0.28 | 0.28 |  |  |  | 0.25 | 0.25 |  |  |  | 0.4 | 0.4 |  |  |  | NO | NO | Not Rated | Not Rated | Not Rated | Not Rated | Reinstall dislodged tiles. | Reinstall dislodged tiles. |  |  |  | NO | NO |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | YES |  |  |  | 0% | 50% |  |  |  | 0 | 0.5 |  |  |  | None | Not Given | By User | By User | Not Given | B3011.011-DS1-1.JPG | B3011.011-DS2-1.JPG |  |  |  | No | None | NO
B3011.014 | B3011.014 | Clay tile roof, unsecured tiles | Costing per roofing square (100 SF) | Any | Compliant with UBC 1994 | Each | Each | Peak Floor Acceleration | g | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 348 | SF 100 | NO | NO | Minor damage; tiles dislodged. | Major portion of tile dislodged. |  |  |  | 1 | 1 |  |  |  | 0.4 | 0.5 |  |  |  | 0.2 | 0.2 |  |  |  | 0.25 | 0.25 |  |  |  | 0.3 | 0.3 |  |  |  | NO | NO | Not Rated | Not Rated | Not Rated | Not Rated | Replace and install dislodged tiles (assume 5% of area) | Replace and install dislodged tiles. |  |  |  | NO | NO |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | YES |  |  |  | 0% | 50% |  |  |  | 0 | 0.5 |  |  |  | None | Not Given | By User | By User | Not Given | B3011.011-DS1-1.JPG | B3011.011-DS2-1.JPG |  |  |  | No | None | NO
B3031.001a | B3031.001a | Masonry Chimney - unreinforced, non industrial, above roof 5 ft, replace with masonry | Demand parameter shall be defined as the first floor peak floor acceleration. Unreinforced masonry chimney as a component of wood frame buildings. Includes firebox and chimney, excludes exterior veneer or ornamentation. May include chimneys where the quality of reinforcing is unknown. For multiple story buildings enter the chimney fragility once at the first floor, do not specify this fragility at subsequent elevated floors. | Normal | All | Each | Each | Peak Floor Acceleration | g | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 349 | EA 1 | NO | NO | Cracking with offset > 1/16" | Toppling of all or a portion of the chimney. |  |  |  | 1 | 1 |  |  |  | 0.35 | 0.5 |  |  |  | Not Specified | Not Specified |  |  |  | Not Specified | Not Specified |  |  |  | 0.6 | 0.6 |  |  |  | NO | NO | Not Rated | Not Rated | Not Rated | Not Rated | Rebuild above break or replace entire chimney. Addl comments (edit or delete as necessary): Rebuilding with masonry will restore the chimney to its pre-earthquake condition. Some jurisdictions prohibit unreinforced reconstruction and require either replacement of the damaged portion of the chimney with a metal flue within wood frame chase or a complete removal of the existing fireplace and chimney with replacement with a code compliant reinforced masonry design. Toppled chimney may cause damage to adjacent structure. | Rebuild above break or replace entire chimney. |  |  |  | NO | NO |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | YES | YES |  |  |  | 25% | 50% |  |  |  | 0.5 | 0.5 |  |  |  | Rebuilding with masonry will restore the chimney to its pre-earthquake condition. Some jurisdictions prohibit unreinforced reconstruction and require either replacement of the damaged portion of the chimney with a metal flue within wood frame chase or a complete removal of the existing fireplace and chimney with replacement with a code compliant reinforced masonry design. Toppled chimney may cause damage to adjacent structure. | Not Given | By User | By User | Not Given | B3031.001a-DS1-1.jpg | B3031.001a-DS2-1.jpg |  |  |  | No | None | NO
B3031.001b | B3031.001b | Masonry Chimney - unreinforced, non industrial, above roof 10 ft, replace with masonry | Demand parameter shall be defined as the first floor peak floor acceleration. Unreinforced masonry chimney as a component of wood frame buildings. Includes firebox and chimney, excludes exterior veneer or ornamentation. May include chimneys where the quality of reinforcing is unknown. For multiple story buildings enter the chimney fragility once at the first floor, do not specify this fragility at subsequent elevated floors. | Normal | All | Each | Each | Peak Floor Acceleration | g | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 350 | EA 1 | NO | NO | Cracking with offset > 1/16" | Toppling of all or a portion of the chimney. |  |  |  | 1 | 1 |  |  |  | 0.35 | 0.5 |  |  |  | Not Specified | Not Specified |  |  |  | Not Specified | Not Specified |  |  |  | 0.6 | 0.6 |  |  |  | NO | NO | Not Rated | Not Rated | Not Rated | Not Rated | Rebuild above break or replace entire chimney. Addl comments (edit or delete as necessary): Rebuilding with masonry will restore the chimney to its pre-earthquake condition. Some jurisdictions prohibit unreinforced reconstruction and require either replacement of the damaged portion of the chimney with a metal flue within wood frame chase or a complete removal of the existing fireplace and chimney with replacement with a code compliant reinforced masonry design. Toppled chimney may cause damage to adjacent structure. | Rebuild above break or replace entire chimney. |  |  |  | NO | NO |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | YES | YES |  |  |  | 25% | 50% |  |  |  | 0.5 | 0.5 |  |  |  | Rebuilding with masonry will restore the chimney to its pre-earthquake condition. Some jurisdictions prohibit unreinforced reconstruction and require either replacement of the damaged portion of the chimney with a metal flue within wood frame chase or a complete removal of the existing fireplace and chimney with replacement with a code compliant reinforced masonry design. Toppled chimney may cause damage to adjacent structure. | Not Given | By User | By User | Not Given | B3031.001a-DS1-1.jpg | B3031.001a-DS2-1.jpg |  |  |  | No | None | NO
B3031.001c | B3031.001c | Masonry Chimney - unreinforced, non industrial, above roof 15 ft, replace with masonry | Demand parameter shall be defined as the first floor peak floor acceleration. Unreinforced masonry chimney as a component of wood frame buildings. Includes firebox and chimney, excludes exterior veneer or ornamentation. May include chimneys where the quality of reinforcing is unknown. For multiple story buildings enter the chimney fragility once at the first floor, do not specify this fragility at subsequent elevated floors. | Normal | All | Each | Each | Peak Floor Acceleration | g | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 351 | EA 1 | NO | NO | Cracking with offset > 1/16" | Toppling of all or a portion of the chimney. |  |  |  | 1 | 1 |  |  |  | 0.35 | 0.5 |  |  |  | Not Specified | Not Specified |  |  |  | Not Specified | Not Specified |  |  |  | 0.6 | 0.6 |  |  |  | NO | NO | Not Rated | Not Rated | Not Rated | Not Rated | Rebuild above break or replace entire chimney. Addl comments (edit or delete as necessary): Rebuilding with masonry will restore the chimney to its pre-earthquake condition. Some jurisdictions prohibit unreinforced reconstruction and require either replacement of the damaged portion of the chimney with a metal flue within wood frame chase or a complete removal of the existing fireplace and chimney with replacement with a code compliant reinforced masonry design. Toppled chimney may cause damage to adjacent structure. | Rebuild above break or replace entire chimney. |  |  |  | NO | NO |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | YES | YES |  |  |  | 25% | 50% |  |  |  | 0.5 | 0.5 |  |  |  | Rebuilding with masonry will restore the chimney to its pre-earthquake condition. Some jurisdictions prohibit unreinforced reconstruction and require either replacement of the damaged portion of the chimney with a metal flue within wood frame chase or a complete removal of the existing fireplace and chimney with replacement with a code compliant reinforced masonry design. Toppled chimney may cause damage to adjacent structure. | Not Given | By User | By User | Not Given | B3031.001a-DS1-1.jpg | B3031.001a-DS2-1.jpg |  |  |  | No | None | NO
B3031.002a | B3031.002a | Masonry Chimney - unreinforced, non industrial, above roof 5 ft, replace with framing | Demand parameter shall be defined as the first floor peak floor acceleration. Unreinforced masonry chimney as a component of wood frame buildings. Includes firebox and chimney, excludes exterior veneer or ornamentation. May include chimneys where the quality of reinforcing is unknown. For multiple story buildings enter the chimney fragility once at the first floor, do not specify this fragility at subsequent elevated floors. | Normal | All | Each | Each | Peak Floor Acceleration | g | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 352 | EA 1 | NO | NO | Cracking with offset > 1/16" | Toppling of all or a portion of the chimney. |  |  |  | 1 | 1 |  |  |  | 0.35 | 0.5 |  |  |  | Not Specified | Not Specified |  |  |  | Not Specified | Not Specified |  |  |  | 0.6 | 0.6 |  |  |  | NO | NO | Not Rated | Not Rated | Not Rated | Not Rated | Rebuild above break or replace entire chimney. Addl comments (edit or delete as necessary): Rebuilding with masonry will restore the chimney to its pre-earthquake condition. Some jurisdictions prohibit unreinforced reconstruction and require either replacement of the damaged portion of the chimney with a metal flue within wood frame chase or a complete removal of the existing fireplace and chimney with replacement with a code compliant reinforced masonry design. Toppled chimney may cause damage to adjacent structure. | Rebuild above break or replace entire chimney. |  |  |  | NO | NO |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | YES | YES |  |  |  | 25% | 50% |  |  |  | 0.5 | 0.5 |  |  |  | Rebuilding with masonry will restore the chimney to its pre-earthquake condition. Some jurisdictions prohibit unreinforced reconstruction and require either replacement of the damaged portion of the chimney with a metal flue within wood frame chase or a complete removal of the existing fireplace and chimney with replacement with a code compliant reinforced masonry design. Toppled chimney may cause damage to adjacent structure. | Not Given | By User | By User | Not Given | B3031.001a-DS1-1.jpg | B3031.001a-DS2-1.jpg |  |  |  | No | None | NO
B3031.002b | B3031.002b | Masonry Chimney - unreinforced, non industrial, above roof 10 ft, replace with framing | Demand parameter shall be defined as the first floor peak floor acceleration. Unreinforced masonry chimney as a component of wood frame buildings. Includes firebox and chimney, excludes exterior veneer or ornamentation. May include chimneys where the quality of reinforcing is unknown. For multiple story buildings enter the chimney fragility once at the first floor, do not specify this fragility at subsequent elevated floors. | Normal | All | Each | Each | Peak Floor Acceleration | g | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 353 | EA 1 | NO | NO | Cracking with offset > 1/16" | Toppling of all or a portion of the chimney. |  |  |  | 1 | 1 |  |  |  | 0.35 | 0.5 |  |  |  | Not Specified | Not Specified |  |  |  | Not Specified | Not Specified |  |  |  | 0.6 | 0.6 |  |  |  | NO | NO | Not Rated | Not Rated | Not Rated | Not Rated | Rebuild above break or replace entire chimney. Addl comments (edit or delete as necessary): Rebuilding with masonry will restore the chimney to its pre-earthquake condition. Some jurisdictions prohibit unreinforced reconstruction and require either replacement of the damaged portion of the chimney with a metal flue within wood frame chase or a complete removal of the existing fireplace and chimney with replacement with a code compliant reinforced masonry design. Toppled chimney may cause damage to adjacent structure. | Rebuild above break or replace entire chimney. |  |  |  | NO | NO |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | YES | YES |  |  |  | 25% | 50% |  |  |  | 0.5 | 0.5 |  |  |  | Rebuilding with masonry will restore the chimney to its pre-earthquake condition. Some jurisdictions prohibit unreinforced reconstruction and require either replacement of the damaged portion of the chimney with a metal flue within wood frame chase or a complete removal of the existing fireplace and chimney with replacement with a code compliant reinforced masonry design. Toppled chimney may cause damage to adjacent structure. | Not Given | By User | By User | Not Given | B3031.001a-DS1-1.jpg | B3031.001a-DS2-1.jpg |  |  |  | No | None | NO
B3031.002c | B3031.002c | Masonry Chimney - unreinforced, non industrial, above roof 15 ft, replace with framing | Demand parameter shall be defined as the first floor peak floor acceleration. Unreinforced masonry chimney as a component of wood frame buildings. Includes firebox and chimney, excludes exterior veneer or ornamentation. May include chimneys where the quality of reinforcing is unknown. For multiple story buildings enter the chimney fragility once at the first floor, do not specify this fragility at subsequent elevated floors. | Normal | All | Each | Each | Peak Floor Acceleration | g | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 354 | EA 1 | NO | NO | Cracking with offset > 1/16" | Toppling of all or a portion of the chimney. |  |  |  | 1 | 1 |  |  |  | 0.35 | 0.5 |  |  |  | Not Specified | Not Specified |  |  |  | Not Specified | Not Specified |  |  |  | 0.6 | 0.6 |  |  |  | NO | NO | Not Rated | Not Rated | Not Rated | Not Rated | Rebuild above break or replace entire chimney. Addl comments (edit or delete as necessary): Rebuilding with masonry will restore the chimney to its pre-earthquake condition. Some jurisdictions prohibit unreinforced reconstruction and require either replacement of the damaged portion of the chimney with a metal flue within wood frame chase or a complete removal of the existing fireplace and chimney with replacement with a code compliant reinforced masonry design. Toppled chimney may cause damage to adjacent structure. | Rebuild above break or replace entire chimney. |  |  |  | NO | NO |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | YES | YES |  |  |  | 25% | 50% |  |  |  | 0.5 | 0.5 |  |  |  | Rebuilding with masonry will restore the chimney to its pre-earthquake condition. Some jurisdictions prohibit unreinforced reconstruction and require either replacement of the damaged portion of the chimney with a metal flue within wood frame chase or a complete removal of the existing fireplace and chimney with replacement with a code compliant reinforced masonry design. Toppled chimney may cause damage to adjacent structure. | Not Given | By User | By User | Not Given | B3031.001a-DS1-1.jpg | B3031.001a-DS2-1.jpg |  |  |  | No | None | NO
B3041.001 | B3041.001 | Masonry Parapet - unreinforced, unbraced | Unreinforced and unbraced masonry parapet as a component of a masonry building. Parapet height / width of approximately 3. Costing based upon repair of 3ft tall x 10ft segment. | Normal | All | Each | Each | Peak Floor Acceleration | g | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 355 | LF 10 | NO | NO | Cracking with offset > 1/16" | Toppling of all or portion of parapet. |  |  |  | 1 | 1 |  |  |  | 0.2 | 0.4 |  |  |  | Not Specified | Not Specified |  |  |  | Not Specified | Not Specified |  |  |  | 0.6 | 0.6 |  |  |  | NO | NO | Not Rated | Not Rated | Not Rated | Not Rated | Replace and reinforce | Replace and reinforce |  |  |  | NO | NO |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | YES | YES |  |  |  | 25% | 50% |  |  |  | 0.5 | 0.5 |  |  |  | None | Not Given | By User | By User | Not Given | B2012.001a-DS1-1.jpg | B2012.001a-DS2-1.jpg |  |  |  | No | 2016-09-14 Costing revised to represent a 3ft tall x 10ft segment. | NO
C1011.001a | C1011.001a | Wall Partition, Type: Gypsum with metal studs, Full Height, Fixed Below, Fixed Above | Quantity is based upon 13'x100' Panels. Quantity of wall damaged varies by damage state. | Normal | Unknown | Each | Each | Story Drift Ratio | Unit less | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 356 | LF 100 | NO | NO | Screw pop-out, cracking of wall board, warping or cracking of tape, slight crushing of wall panel at corners. | Moderate cracking or crushing of gypsum wall boards (typically in corners). Moderate corner gap openings, bending of boundary studs. | Buckling of studs and tearing of tracks. Tearing or bending of top track, tearing at corners with transverse walls, large gap openings, walls displaced. |  |  | 1 | 1 | 1 |  |  | 0.005 | 0.01 | 0.021 |  |  | Not Specified | Not Specified | Not Specified |  |  | Not Specified | Not Specified | Not Specified |  |  | 0.4 | 0.3 | 0.2 |  |  | NO | YES | Superior | Superior | Superior | Not Rated | Retape joints, paste and repaint. May require cutting and replacing corner sections of board. Repair 5% wallboard, 10% retape, 25% repaint. | Remove and replace 10% of wall board (both sides), retape and paste 25% of wall, paint 50% of wall. Replace boundary studs of approximately 5 intersections per 100 ft of wall length. | Remove and replace 50% of length of metal stud wall, 50% of both sides of the gypsum, and any embedded utilities. Retape and paste as required. Repaint 100%. |  |  | NO | NO | NO |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | NO | NO |  |  | 0% | 0% | 0% |  |  | 0 | 0 | 0 |  |  | None | Not Given | By User | By User | Not Given | none | none | none |  |  | No | 2015-07-26 Revised DS1,2,3 description, consequence text; 2016-03-08 Revised for new cost and time consequence data | YES
C1011.001b | C1011.001b | Wall Partition, Type: Gypsum with metal studs, Partial Height, Fixed Below, Lateral Braced Above | Quantity is based upon 13'x100' Panels. Quantity of wall damaged varies by damage state. | Normal | Unknown | Each | Each | Story Drift Ratio | Unit less | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 357 | LF 100 | NO | NO | Screw pop-out, cracking of wall board, warping or cracking of tape, slight crushing of wall panel at corners. | Moderate cracking or crushing of gypsum wall boards (typically in corners). Moderate corner gap openings, bending of boundary studs. | Buckling of studs and tearing of tracks. Tearing or bending of top track, tearing at corners with transverse walls, large gap openings, walls displaced. |  |  | 1 | 1 | 1 |  |  | 0.01 | 0.013 | 0.018 |  |  | Not Specified | Not Specified | Not Specified |  |  | Not Specified | Not Specified | Not Specified |  |  | 0.3 | 0.3 | 0.3 |  |  | NO | YES | Superior | Superior | Superior | Not Rated | Retape joints, paste and repaint. May require cutting and replacing corner sections of board. Repair 5% wallboard, 10% retape, 25% repaint. | Remove and replace 10% of wall board (both sides), retape and paste 25% of wall, paint 50% of wall. Replace boundary studs of approximately 5 intersections per 100 ft of wall length. | Remove and replace 50% of length of metal stud wall, 50% of both sides of the gypsum, and any embedded utilities. Retape and paste as required. Repaint 100%. |  |  | NO | NO | NO |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | NO | NO |  |  | 0% | 0% | 0% |  |  | 0 | 0 | 0 |  |  | None | Not Given | By User | By User | Not Given | none | none | none |  |  | No | 2015-07-26 Revised DS1,2,3 description, consequence text; 2016-03-08 Revised for new cost and time consequence data | YES
C1011.001c | C1011.001c | Wall Partition, Type: Gypsum with metal studs, Full Height, Fixed Below, Slip Track Above with returns | Quantity is based upon 13'x100' Panels. Quantity of wall damaged varies by damage state. | Normal | Unknown | Each | Each | Story Drift Ratio | Unit less | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 358 | LF 100 | NO | NO | Screw pop-out, cracking of wall board, warping or cracking of tape, slight crushing of wall panel at corners. | Moderate cracking or crushing of gypsum wall boards (typically in corners). Moderate corner gap openings, bending of boundary studs. | Buckling of studs and tearing of tracks. Tearing or bending of top track, tearing at corners with transverse walls, large gap openings, walls displaced. |  |  | 1 | 1 | 1 |  |  | 0.004 | 0.011 | 0.019 |  |  | Not Specified | Not Specified | Not Specified |  |  | Not Specified | Not Specified | Not Specified |  |  | 0.45 | 0.35 | 0.25 |  |  | NO | YES | Superior | Superior | Superior | Not Rated | Retape joints, paste and repaint. May require cutting and replacing corner sections of board. Repair 5% wallboard, 10% retape, 25% repaint. | Remove and replace 10% of wall board (both sides), retape and paste 25% of wall, paint 50% of wall. Replace boundary studs of approximately 5 intersections per 100 ft of wall length. | Remove and replace 50% of length of metal stud wall, 50% of both sides of the gypsum, and any embedded utilities. Retape and paste as required. Repaint 100%. |  |  | NO | NO | NO |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | NO | NO |  |  | 0% | 0% | 0% |  |  | 0 | 0 | 0 |  |  | None | Not Given | By User | By User | Not Given | none | none | none |  |  | No | 2015-07-26 Revised DS1,2,3 description, consequence text; 2011-08-24 Negative probability below 0.5% drift - overlap deemed acceptable.; 2016-03-08 Revised for new cost and time consequence data | YES
C1011.001d | C1011.001d | Wall Partition, Type: Gypsum with metal studs, Full Height, Fixed Below, Slip Track Above w/o returns (friction connections) | Quantity is based upon 13'x100' Panels. Quantity of wall damaged varies by damage state. | Normal | Unknown | Each | Each | Story Drift Ratio | Unit less | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 359 | LF 100 | NO | NO | Screw pop-out, cracking of wall board, warping or cracking of tape, slight crushing of wall panel at corners. | Moderate cracking or crushing of gypsum wall boards (typically in corners). Moderate corner gap openings, bending of boundary studs. |  |  |  | 1 | 1 |  |  |  | 0.0035 | 0.0095 |  |  |  | Not Specified | Not Specified |  |  |  | Not Specified | Not Specified |  |  |  | 0.6 | 0.45 |  |  |  | NO | YES | Superior | Superior | Superior | Not Rated | Retape joints, paste and repaint. May require cutting and replacing corner sections of board. Repair 5% wallboard, 10% retape, 25% repaint. | Remove and replace 10% of wall board (both sides), retape and paste 25% of wall, paint 50% of wall. Replace boundary studs of approximately 5 intersections per 100 ft of wall length. |  |  |  | NO | NO |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | NO |  |  |  | 0% | 0% |  |  |  | 0 | 0 |  |  |  | None | Not Given | By User | By User | Not Given | none | none |  |  |  | No | 2015-07-26 Revised DS1,2,3 description, consequence text; 2015-08-13 Removed DS3 data - no such damage state or consequence; 2016-03-08 Revised for new cost and time consequence data | YES
C1011.011a | C1011.011a | Wall Partition, Type: Gypsum with wood studs, Full Height, Fixed Below, Fixed Above | Quantity is based upon 13'x100' Panels. Quantity of wall damaged varies by damage state. | Normal | Unknown | Each | Each | Story Drift Ratio | Unit less | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,MutEx(DS2,DS3)) | 360 | LF 100 | NO | NO | Cracking of paint over fasteners or joints. | Local and global buckling out-of-plane and crushing of gypsum wallboards. Studs are typically not damaged by failure of the gypsum wallboard. | Local and global buckling out-of-plane and crushing of gypsum wallboards. Studs are typically not damaged by failure of the gypsum wallboard. |  |  | 1 | 0.8 | 0.2 |  |  | 0.0021 | 0.0071 | 0.0071 |  |  | Not Specified | Not Specified | Not Specified |  |  | Not Specified | Not Specified | Not Specified |  |  | 0.6 | 0.45 | 0.45 |  |  | NO | YES | Superior | Superior | Superior | Not Rated | Gypsum wallboard repaired by replacing the tape along the seam of two adjacent panels, applying new joint compound, sanding, and repainting. | Replace 25 feet of the affected panel along with the application of new tape, joint compound, followed by sanding and repainting. Studs are not damaged. | Replace 100 feet of the affected panel along with the application of new tape, joint compound, followed by sanding and repainting. Studs are not damaged. |  |  | NO | NO | NO |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | NO | NO |  |  | 0% | 0% | 0% |  |  | 0 | 0 | 0 |  |  | None | Not Given | By User | By User | Not Given | none | none | none |  |  | No | 2016-03-08 Revised for new cost and time consequence data | YES
C2011.001a | C2011.001a | Prefabricated steel stair with steel treads and landings with seismic joints that accommodate drift. | Flexible stair with seismic interstory slip joint. Steel prefab stringers, steel or concrete filled pan treads. | Normal | All | Each | Each | Story Drift Ratio | Unit less | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 361 | EA 1 | YES | FLR | Non structural damage, local steel yielding. | Structural damage but live load capacity remains intact. Buckling of steel, weld cracking. | Loss of live load capacity. Connection and or weld fracture. |  |  | 1 | 1 | 1 |  |  | By User | By User | By User |  |  | Not Specified | Not Specified | Not Specified |  |  | Not Specified | Not Specified | Not Specified |  |  | By User | By User | By User |  |  | NO | YES | Marginal | Marginal | Average | Not Rated | Patch, paint. | Removal and replacement of damaged components. Field repair of damage (such as welding). Repair finsihes. | Replace stair and handrail. Repair and replace affected soffits and floor finishes. |  |  | NO | NO | NO |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | NO | YES |  |  | 0% | 0% | 75% |  |  | 0 | 0 | 0.5 |  |  | User to provide median demand and dispersion values. The values listed are default PACT values and do not represent the response of this component. | Not Given | By User | By User | Not Given | C2011.001a-DS1-1.jpg | C2011.001a-DS2-1.jpg | C2011.001a-DS2-1.jpg |  |  | No | 2011-08-24 DS2 beta changed from 0.08 to 0.15 to avoid negative probability above 0.5% drift. | YES
C2011.001b | C2011.001b | Prefabricated steel stair with steel treads and landings with no seismic joint. | Flexible stair without seismic interstory slip joint. Steel prefab stringers, steel or concrete filled pan treads. | Normal | All | Each | Each | Story Drift Ratio | Unit less | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 362 | EA 1 | YES | FLR | Non structural damage, local steel yielding. | Buckling of steel, weld cracking. | Loss of live load capacity. Connection and or weld fracture. |  |  | 1 | 1 | 1 |  |  | 0.005 | 0.017 | 0.028 |  |  | Not Specified | Not Specified | Not Specified |  |  | Not Specified | Not Specified | Not Specified |  |  | 0.6 | 0.6 | 0.45 |  |  | NO | YES | Marginal | Marginal | Average | Not Rated | Patch, paint. | Removal and replacement of damaged components. Field repair of damage (such as welding). Repair finsihes. | Replace stair and handrail. Repair and replace affected soffits and floor finishes. |  |  | NO | NO | NO |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | NO | YES |  |  | 0% | 0% | 75% |  |  | 0 | 0 | 0.5 |  |  | Confirm median demand and dispersion values | Not Given | By User | By User | Not Given | C2011.001a-DS1-1.jpg | C2011.001a-DS2-1.jpg | C2011.001a-DS2-1.jpg |  |  | No | 2011-08-24 DS2 beta changed from 0.08 to 0.15 to avoid negative probability above 0.5% drift. | YES
C2011.011a | C2011.011a | Non-monolithic precast concrete stair assembly with concrete stringers and treads with seismic joints that accommodate drift. | Rigid stair with seismic interstory drift joint. Precast concrete stair. | Normal | All | Each | Each | Story Drift Ratio | Unit less | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 363 | EA 1 | YES | FLR | Non structural damage, local concrete cracking, localized concrete spalling, localized rebar yielding. | Structural damage but live load capacity remains intact. Extensive concrete cracking, concrete crushing, buckling of rebar. | Loss of live load capacity. Extensive concrete crushing, connection failure. |  |  | 1 | 1 | 1 |  |  | By User | By User | By User |  |  | Not Specified | Not Specified | Not Specified |  |  | Not Specified | Not Specified | Not Specified |  |  | By User | By User | By User |  |  | NO | YES | Marginal | Marginal | Average | Not Rated | Patch, paint, epoxy injection. Repair finishes. | Remove damaged components, install replacement components. | Replace stair and handrail. Repair and replace affected soffits and floor finishes. |  |  | NO | NO | NO |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | NO | YES |  |  | 0% | 0% | 75% |  |  | 0 | 0 | 0.5 |  |  | User to provide median demand and dispersion values. The values listed are default PACT values and do not represent the response of this component. | Not Given | By User | By User | Not Given | C2011.011a-DS1-1.jpg | C2011.011a-DS2-1.jpg | C2011.011a-DS2-1.jpg |  |  | No | None | YES
C2011.011b | C2011.011b | Non-monolithic precast concrete stair assembly with concrete stringers and treads with no seismic joint. | Rigid stair without seismic interstory drift joint. Precast concrete stair. | Normal | All | Each | Each | Story Drift Ratio | Unit less | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 364 | EA 1 | YES | FLR | Non structural damage, local concrete cracking, localized concrete spalling, localized rebar yielding. | Structural damage but live load capacity remains intact. Extensive concrete cracking, concrete crushing, buckling of rebar. | Loss of live load capacity. Extensive concrete crushing, connection failure. |  |  | 1 | 1 | 1 |  |  | 0.005 | 0.017 | 0.028 |  |  | Not Specified | Not Specified | Not Specified |  |  | Not Specified | Not Specified | Not Specified |  |  | 0.6 | 0.6 | 0.45 |  |  | NO | YES | Marginal | Marginal | Average | Not Rated | Patch, paint, epoxy injection. Repair finishes. | Remove damaged components, install replacement components. | Replace stair and handrail. Repair and replace affected soffits and floor finishes. |  |  | NO | NO | NO |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | NO | YES |  |  | 0% | 0% | 75% |  |  | 0 | 0 | 0.5 |  |  | Confirm median demand and dispersion values. Base document noted that there was insufficient data to establish median demand or dispersion values. The median demand and dispersion values listed are from a best fit approximation of the data performed by MKA. | Not Given | By User | By User | Not Given | C2011.011a-DS1-1.jpg | C2011.011a-DS2-1.jpg | C2011.011a-DS2-1.jpg |  |  | No | None | YES
C2011.021a | C2011.021a | Monolithic cast-in-place and precast concrete stairs with seismic joints that accommodate drift - replace in kind if replacement is required. | Cast in place concrete stair, with seismic interstory drift joint | Normal | All | Each | Each | Story Drift Ratio | Unit less | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 365 | EA 1 | YES | FLR | Local concrete cracking, localized concrete spalling | Extensive concrete cracking, concrete crushing | Loss of live load capacity. |  |  | 1 | 1 | 1 |  |  | By User | By User | By User |  |  | Not Specified | Not Specified | Not Specified |  |  | Not Specified | Not Specified | Not Specified |  |  | By User | By User | By User |  |  | NO | YES | Marginal | Marginal | Average | Not Rated | Protect surrounding space, epoxy inject cracks, repair finishes. Modify or relocate mechanical and electrical as required for repair work. Repair finishes. | Protect floor, cut out damaged areas, repair buckled rebar, patch / cast concrete, repair finishes. Modify or relocate mechanical and electrical as required for repair work. Repair finishes. | Protect area, remove damaged stair including landings and handrails. Remove and reinstall damaged soffit and mechanical systems. Replace stair, landings, and handrail. Modify or relocate mechanical and electrical as required for repair work. Repair finishes. |  |  | NO | NO | NO |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | NO | YES |  |  | 0% | 0% | 75% |  |  | 0 | 0 | 0.5 |  |  | User to provide median demand and dispersion values. The values listed are default PACT values and do not represent the response of this component. | Not Given | By User | By User | Not Given | C2011.011a-DS1-1.jpg | C2011.011a-DS2-1.jpg | C2011.011a-DS2-1.jpg |  |  | No | None | YES
C2011.021b | C2011.021b | Monolithic cast-in-place and precast concrete stairs with no seismic joints - replace in kind if replacement is required. | Cast in place concrete stair, no seismic interstory drift joint | Normal | All | Each | Each | Story Drift Ratio | Unit less | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 366 | EA 1 | YES | FLR | Local concrete cracking, localized concrete spalling | Extensive concrete cracking, concrete crushing | Loss of live load capacity. |  |  | 1 | 1 | 1 |  |  | By User | By User | By User |  |  | Not Specified | Not Specified | Not Specified |  |  | Not Specified | Not Specified | Not Specified |  |  | By User | By User | By User |  |  | NO | YES | Marginal | Marginal | Average | Not Rated | Protect surrounding space, epoxy inject cracks, repair finishes. Modify or relocate mechanical and electrical as required for repair work. Repair finishes. | Protect floor, cut out damaged areas, repair buckled rebar, patch / cast concrete, repair finishes. Modify or relocate mechanical and electrical as required for repair work. Repair finishes. | Protect area, remove damaged stair including landings and handrails. Remove and reinstall damaged soffit and mechanical systems. Replace stair, landings, and handrail. Modify or relocate mechanical and electrical as required for repair work. Repair finishes. |  |  | NO | NO | NO |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | NO | YES |  |  | 0% | 0% | 75% |  |  | 0 | 0 | 0.5 |  |  | User to provide median demand and dispersion values. The values listed are default PACT values and do not represent the response of this component. | Not Given | By User | By User | Not Given | C2011.011a-DS1-1.jpg | C2011.011a-DS2-1.jpg | C2011.011a-DS2-1.jpg |  |  | No | None | NO
C2011.021c | C2011.021c | Monolithic cast-in-place and precast concrete stairs with seismic joints that accommodate drift - replace with prefabricated steel stair if replacement is required. | Cast in place concrete stair, with seismic interstory drift joint | Normal | All | Each | Each | Story Drift Ratio | Unit less | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 367 | EA 1 | YES | FLR | Local concrete cracking, localized concrete spalling | Extensive concrete cracking, concrete crushing | Loss of live load capacity. |  |  | 1 | 1 | 1 |  |  | By User | By User | By User |  |  | Not Specified | Not Specified | Not Specified |  |  | Not Specified | Not Specified | Not Specified |  |  | By User | By User | By User |  |  | NO | YES | Marginal | Marginal | Average | Not Rated | Protect surrounding space, epoxy inject cracks, repair finishes. Modify or relocate mechanical and electrical as required for repair work. Repair finishes. | Protect floor, cut out damaged areas, repair buckled rebar, patch / cast concrete, repair finishes. Modify or relocate mechanical and electrical as required for repair work. Repair finishes. | Protect area, remove damaged stair including landings and handrails. Remove and reinstall damaged soffit and mechanical systems. Replace stair, landings, and handrail. Modify or relocate mechanical and electrical as required for repair work. Repair finishes. |  |  | NO | NO | NO |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | NO | YES |  |  | 0% | 0% | 75% |  |  | 0 | 0 | 0.5 |  |  | User to provide median demand and dispersion values. The values listed are default PACT values and do not represent the response of this component. | Not Given | By User | By User | Not Given | C2011.011a-DS1-1.jpg | C2011.011a-DS2-1.jpg | C2011.011a-DS2-1.jpg |  |  | No | None | NO
C2011.021d | C2011.021d | Monolithic cast-in-place and precast concrete stairs with no seismic joints - replace with prefabricated steel stair if replacement is required. | Cast in place concrete stair, no seismic interstory drift joint | Normal | All | Each | Each | Story Drift Ratio | Unit less | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 368 | EA 1 | YES | FLR | Local concrete cracking, localized concrete spalling | Extensive concrete cracking, concrete crushing | Loss of live load capacity. |  |  | 1 | 1 | 1 |  |  | By User | By User | By User |  |  | Not Specified | Not Specified | Not Specified |  |  | Not Specified | Not Specified | Not Specified |  |  | By User | By User | By User |  |  | NO | YES | Marginal | Marginal | Average | Not Rated | Protect surrounding space, epoxy inject cracks, repair finishes. Modify or relocate mechanical and electrical as required for repair work. Repair finishes. | Protect floor, cut out damaged areas, repair buckled rebar, patch / cast concrete, repair finishes. Modify or relocate mechanical and electrical as required for repair work. Repair finishes. |  |  |  | NO | NO | NO |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | NO | YES |  |  | 0% | 0% | 75% |  |  | 0 | 0 | 0.5 |  |  | User to provide median demand and dispersion values. The values listed are default PACT values and do not represent the response of this component. | Not Given | By User | By User | Not Given | C2011.011a-DS1-1.jpg | C2011.011a-DS2-1.jpg | C2011.011a-DS2-1.jpg |  |  | No | None | NO
C2011.031a | C2011.031a | Hybrid stair assembly with steel stringers and concrete treads and landings with seismic joints that accommodate drift. | Stair consists of steel stringers with precast treads rigidly linked to stringer | Normal | All | Each | Each | Story Drift Ratio | Unit less | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 369 | EA 1 | YES | FLR | Localized steel yielding. | Buckling of steel, weld cracking. | Loss of live load capacity. |  |  | 1 | 1 | 1 |  |  | By User | By User | By User |  |  | Not Specified | Not Specified | Not Specified |  |  | Not Specified | Not Specified | Not Specified |  |  | By User | By User | By User |  |  | NO | YES | Marginal | Marginal | Average | Not Rated | Protect surrounding space. Minor repair of finishes. Modify or relocate mechanical and electrical as required for repair work. Repair finishes. | Protect floor, cut out damaged areas, reweld. Repair finishes. Modify or relocate mechanical and electrical as required for repair work. Repair finishes. | Protect area, remove damaged stair including landings and handrails. Remove and reinstall damaged soffit and mechanical systems. Replace stair, landings, and handrail. Modify or relocate mechanical and electrical as required for repair work. Repair finishes. |  |  | NO | NO | NO |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | NO | YES |  |  | 0% | 0% | 75% |  |  | 0 | 0 | 0.5 |  |  | User to provide median demand and dispersion values. The values listed are default PACT values and do not represent the response of this component. | Not Given | By User | By User | Not Given | none | none | none |  |  | No | None | YES
C2011.031b | C2011.031b | Hybrid stair assembly with steel stringers and concrete treads and landings with no seismic joints. | Stair consists of steel stringers with precast treads rigidly linked to stringer | Normal | All | Each | Each | Story Drift Ratio | Unit less | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 370 | EA 1 | YES | FLR | Localized steel yielding. | Buckling of steel, weld cracking. | Loss of live load capacity. |  |  | 1 | 1 | 1 |  |  | 0.005 | 0.017 | 0.028 |  |  | Not Specified | Not Specified | Not Specified |  |  | Not Specified | Not Specified | Not Specified |  |  | 0.6 | 0.6 | 0.45 |  |  | NO | YES | Marginal | Marginal | Average | Not Rated | Protect surrounding space. Minor repair of finishes. Modify or relocate mechanical and electrical as required for repair work. Repair finishes. | Protect floor, cut out damaged areas, reweld. Repair finishes. Modify or relocate mechanical and electrical as required for repair work. Repair finishes. | Protect area, remove damaged stair including landings and handrails. Remove and reinstall damaged soffit and mechanical systems. Replace stair, landings, and handrail. Modify or relocate mechanical and electrical as required for repair work. Repair finishes. |  |  | NO | NO | NO |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | NO | YES |  |  | 0% | 0% | 75% |  |  | 0 | 0 | 0.5 |  |  | None | Not Given | By User | By User | Not Given | none | none | none |  |  | No | None | NO
C3011.001a | C3011.001a | Wall Partition, Type: Gypsum + Wallpaper, Full Height, Fixed Below, Fixed Above | Costing based upon 9'x100' Panels | Normal | Not Specified | Each | Each | Story Drift Ratio | Unit less | 1 | DS1 |  |  |  |  | Sequential |  |  |  |  | Seq(DS1) | 371 | LF 100 | NO | NO | Wall paper warped and torn. |  |  |  |  | 1 |  |  |  |  | 0.0021 |  |  |  |  | Not Specified |  |  |  |  | Not Specified |  |  |  |  | 0.6 |  |  |  |  | NO | YES | Superior | Superior | Superior | Not Rated | Remove existing wall paper (or wall) and install new wall paper for full 100 foot length of wall. Existing wall damage per wall type NISTIR file. |  |  |  |  | NO |  |  |  |  | NO |  |  |  |  | Not Applicable |  |  |  |  | 0% | 0 | [8 empty] | 0% | 0 | [8 empty] | NO |  |  |  |  | 0% |  |  |  |  | 0 |  |  |  |  | None | Not Given | By User | By User | Not Given | none |  |  |  |  | No | None | YES
C3011.001b | C3011.001b | Wall Partition, Type: Gypsum + Wallpaper, Partial Height, Fixed Below, Lateral Braced Above | Costing based upon 9'x100' Panels | Normal | Not Specified | Each | Each | Story Drift Ratio | Unit less | 1 | DS1 |  |  |  |  | Sequential |  |  |  |  | Seq(DS1) | 372 | LF 100 | NO | NO | Wall paper warped and torn. |  |  |  |  | 1 |  |  |  |  | 0.0064 |  |  |  |  | Not Specified |  |  |  |  | Not Specified |  |  |  |  | 0.3 |  |  |  |  | NO | YES | Superior | Superior | Superior | Not Rated | Remove existing wall paper (or wall) and install new wall paper for full 100 foot length of wall. Existing wall damage per wall type NISTIR file. |  |  |  |  | NO |  |  |  |  | NO |  |  |  |  | Not Applicable |  |  |  |  | 0% | 0 | [8 empty] | 0% | 0 | [8 empty] | NO |  |  |  |  | 0% |  |  |  |  | 0 |  |  |  |  | None | Not Given | By User | By User | Not Given | none |  |  |  |  | No | None | YES
C3011.001c | C3011.001c | Wall Partition, Type: Gypsum + Wallpaper, Full Height, Fixed Below, Slip Track Above w/ returns (friction connection) | Costing based upon 9'x100' Panels | Normal | Not Specified | Each | Each | Story Drift Ratio | Unit less | 1 | DS1 |  |  |  |  | Sequential |  |  |  |  | Seq(DS1) | 373 | LF 100 | NO | NO | Wall paper warped and torn. |  |  |  |  | 1 |  |  |  |  | 0.002 |  |  |  |  | Not Specified |  |  |  |  | Not Specified |  |  |  |  | 0.7 |  |  |  |  | NO | YES | Superior | Superior | Superior | Not Rated | Remove existing wall paper (or wall) and install new wall paper for full 100 foot length of wall. Existing wall damage per wall type NISTIR file. |  |  |  |  | NO |  |  |  |  | NO |  |  |  |  | Not Applicable |  |  |  |  | 0% | 0 | [8 empty] | 0% | 0 | [8 empty] | NO |  |  |  |  | 0% |  |  |  |  | 0 |  |  |  |  | None | Not Given | By User | By User | Not Given | none |  |  |  |  | No | None | YES
C3011.001d | C3011.001d | Wall Partition, Type: Gypsum + Wallpaper, Full Height, Fixed Below, Slip Track Above w/o returns (friction connection) | Costing based upon 9'x100' Panels | Normal | Not Specified | Each | Each | Story Drift Ratio | Unit less | 1 | DS1 |  |  |  |  | Sequential |  |  |  |  | Seq(DS1) | 374 | LF 100 | NO | NO | Wall paper warped and torn. |  |  |  |  | 1 |  |  |  |  | 0.0035 |  |  |  |  | Not Specified |  |  |  |  | Not Specified |  |  |  |  | 0.7 |  |  |  |  | NO | YES | Superior | Superior | Superior | Not Rated | Remove existing wall paper (or wall) and install new wall paper for full 100 foot length of wall. Existing wall damage per wall type NISTIR file. |  |  |  |  | NO |  |  |  |  | NO |  |  |  |  | Not Applicable |  |  |  |  | 0% | 0 | [8 empty] | 0% | 0 | [8 empty] | NO |  |  |  |  | 0% |  |  |  |  | 0 |  |  |  |  | None | Not Given | By User | By User | Not Given | none |  |  |  |  | No | None | YES
C3011.002a | C3011.002a | Wall Partition, Type: Gypsum + Ceramic Tile, Full Height, Fixed Below, Fixed Above | Costing based upon 9'x100' Panels | Normal | Not Specified | Each | Each | Story Drift Ratio | Unit less | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 375 | LF 100 | NO | NO | Minor cracked joints and tile. | Cracked joints and tile. |  |  |  | 1 | 1 |  |  |  | 0.0021 | 0.0071 |  |  |  | Not Specified | Not Specified |  |  |  | Not Specified | Not Specified |  |  |  | 0.6 | 0.45 |  |  |  | NO | YES | Superior | Superior | Superior | Not Rated | Carefully remove cracked tile and grout at cracked joints, install new ceramic tile and re-grout joints for 10% of full 100 foot length of wall. Existing wall board will remain in place. | Install ceramic tile and grout all joints for full 100 foot length of wall. Note: gypsum wall board will also be removed and replaced which means the removal of ceramic tile will be part of the gypsum wall board removal. |  |  |  | NO | NO |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | NO |  |  |  | 0% | 0% |  |  |  | 0 | 0 |  |  |  | None | Not Given | By User | By User | Not Given | none | none |  |  |  | No | None | YES
C3011.002b | C3011.002b | Wall Partition, Type: Gypsum + Ceramic Tile, Partial Height, Fixed Below, Lateral Braced Above | Costing based upon 9'x100' Panels | Normal | Not Specified | Each | Each | Story Drift Ratio | Unit less | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 376 | LF 100 | NO | NO | Minor cracked joints and tile. | Cracked joints and tile. |  |  |  | 1 | 1 |  |  |  | 0.0064 | 0.011 |  |  |  | Not Specified | Not Specified |  |  |  | Not Specified | Not Specified |  |  |  | 0.3 | 0.3 |  |  |  | NO | YES | Superior | Superior | Superior | Not Rated | Carefully remove cracked tile and grout at cracked joints, install new ceramic tile and re-grout joints for 10% of full 100 foot length of wall. Existing wall board will remain in place. | Install ceramic tile and grout all joints for full 100 foot length of wall. Note: gypsum wall board will also be removed and replaced which means the removal of ceramic tile will be part of the gypsum wall board removal. |  |  |  | NO | NO |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | NO |  |  |  | 0% | 0% |  |  |  | 0 | 0 |  |  |  | None | Not Given | By User | By User | Not Given | none | none |  |  |  | No | None | YES
C3011.002c | C3011.002c | Wall Partition, Type: Gypsum + Ceramic Tile, Full Height, Fixed Below, Slip Track Above w/ returns (friction connection) | Costing based upon 9'x100' Panels | Normal | Not Specified | Each | Each | Story Drift Ratio | Unit less | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 377 | LF 100 | NO | NO | Minor cracked joints and tile. | Cracked joints and tile. |  |  |  | 1 | 1 |  |  |  | 0.002 | 0.005 |  |  |  | Not Specified | Not Specified |  |  |  | Not Specified | Not Specified |  |  |  | 0.7 | 0.4 |  |  |  | NO | YES | Superior | Superior | Superior | Not Rated | Carefully remove cracked tile and grout at cracked joints, install new ceramic tile and re-grout joints for 10% of full 100 foot length of wall. Existing wall board will remain in place. | Install ceramic tile and grout all joints for full 100 foot length of wall. Note: gypsum wall board will also be removed and replaced which means the removal of ceramic tile will be part of the gypsum wall board removal. |  |  |  | NO | NO |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | NO |  |  |  | 0% | 0% |  |  |  | 0 | 0 |  |  |  | None | Not Given | By User | By User | Not Given | none | none |  |  |  | No | None | YES
C3011.002d | C3011.002d | Wall Partition, Type: Gypsum + Ceramic Tile, Full Height, Fixed Below, Slip Track Above w/o returns (friction connection) | Costing based upon 9'x100' Panels | Normal | Not Specified | Each | Each | Story Drift Ratio | Unit less | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 378 | LF 100 | NO | NO | Minor cracked joints and tile. | Cracked joints and tile. |  |  |  | 1 | 1 |  |  |  | 0.0035 | 0.0093 |  |  |  | Not Specified | Not Specified |  |  |  | Not Specified | Not Specified |  |  |  | 0.7 | 0.45 |  |  |  | NO | YES | Superior | Superior | Superior | Not Rated | Carefully remove cracked tile and grout at cracked joints, install new ceramic tile and re-grout joints for 10% of full 100 foot length of wall. Existing wall board will remain in place. | Install ceramic tile and grout all joints for full 100 foot length of wall. Note: gypsum wall board will also be removed and replaced which means the removal of ceramic tile will be part of the gypsum wall board removal. |  |  |  | NO | NO |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | NO |  |  |  | 0% | 0% |  |  |  | 0 | 0 |  |  |  | None | Not Given | By User | By User | Not Given | none | none |  |  |  | No | None | YES
C3011.003a | C3011.003a | Wall Partition, Type: High End Marble or Wood Panel, Full Height, Fixed Below, Fixed Above | Costing based upon 9'x100' Panels | Normal | Not Specified | Each | Each | Story Drift Ratio | Unit less | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 379 | LF 100 | NO | NO | minor cracked joints and minor cracks in marble / wood paneling. | significant cracks in marble / wood paneling. |  |  |  | 1 | 1 |  |  |  | 0.0021 | 0.0071 |  |  |  | Not Specified | Not Specified |  |  |  | Not Specified | Not Specified |  |  |  | 0.6 | 0.45 |  |  |  | NO | YES | Superior | Superior | Superior | Not Rated | Carefully remove cracked marble/paneling and grout at cracked joints, and install new marble/paneling and re-grout joints for 10% of full 100 foot length of wall. Existing wall board will remain place. | Install new marble/paneling for full 100 foot length of wall. Note: the gypsum wall board will also be removed and replaced which means the removal of the marble/paneling will be part of the gypsum wall board removal. |  |  |  | NO | NO |  |  |  | NO | YES |  |  |  | Not Applicable | 100 SF |  |  |  | 0% | 0 | 10% | 0.5 | [6 empty] | 0% | 0 | 5% | 0.5 | [6 empty] | NO | YES |  |  |  | 0% | 50% |  |  |  | 0 | 0.5 |  |  |  | None | Not Given | By User | By User | Not Given | none | none |  |  |  | No | None | YES
C3011.003b | C3011.003b | Wall Partition, Type: High End Marble or Wood Panel, Partial Height, Fixed Below, Lateral Braced Above | Costing based upon 9'x100' Panels | Normal | Not Specified | Each | Each | Story Drift Ratio | Unit less | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 380 | LF 100 | NO | NO | minor cracked joints and minor cracks in marble / wood paneling. | significant cracks in marble / wood paneling. |  |  |  | 1 | 1 |  |  |  | 0.0064 | 0.011 |  |  |  | Not Specified | Not Specified |  |  |  | Not Specified | Not Specified |  |  |  | 0.3 | 0.3 |  |  |  | NO | YES | Superior | Superior | Superior | Not Rated | Carefully remove cracked marble/paneling and grout at cracked joints, and install new marble/paneling and re-grout joints for 10% of full 100 foot length of wall. Existing wall board will remain place. | Install new marble/paneling for full 100 foot length of wall. Note: the gypsum wall board will also be removed and replaced which means the removal of the marble/paneling will be part of the gypsum wall board removal. |  |  |  | NO | NO |  |  |  | NO | YES |  |  |  | Not Applicable | 100 SF |  |  |  | 0% | 0 | 10% | 0.5 | [6 empty] | 0% | 0 | 5% | 0.5 | [6 empty] | NO | YES |  |  |  | 0% | 50% |  |  |  | 0 | 0.5 |  |  |  | None | Not Given | By User | By User | Not Given | none | none |  |  |  | No | None | YES
C3011.003c | C3011.003c | Wall Partition, Type: High End Marble or Wood Panel, Full Height, Fixed Below, Slip Track Above w/ returns (friction connection) | Costing based upon 9'x100' Panels | Normal | Not Specified | Each | Each | Story Drift Ratio | Unit less | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 381 | LF 100 | NO | NO | minor cracked joints and minor cracks in marble / wood paneling. | significant cracks in marble / wood paneling. |  |  |  | 1 | 1 |  |  |  | 0.002 | 0.005 |  |  |  | Not Specified | Not Specified |  |  |  | Not Specified | Not Specified |  |  |  | 0.7 | 0.4 |  |  |  | NO | YES | Superior | Superior | Superior | Not Rated | Carefully remove cracked marble/paneling and grout at cracked joints, and install new marble/paneling and re-grout joints for 10% of full 100 foot length of wall. Existing wall board will remain place. | Install new marble/paneling for full 100 foot length of wall. Note: the gypsum wall board will also be removed and replaced which means the removal of the marble/paneling will be part of the gypsum wall board removal. |  |  |  | NO | NO |  |  |  | NO | YES |  |  |  | Not Applicable | 100 SF |  |  |  | 0% | 0 | 10% | 0.5 | [6 empty] | 0% | 0 | 5% | 0.5 | [6 empty] | NO | YES |  |  |  | 0% | 50% |  |  |  | 0 | 0.5 |  |  |  | None | Not Given | By User | By User | Not Given | none | none |  |  |  | No | None | YES
C3011.003d | C3011.003d | Wall Partition, Type: High End Marble or Wood Panel, Full Height, Fixed Below, Slip Track Above w/o returns (friction connection) | Costing based upon 9'x100' Panels | Normal | Not Specified | Each | Each | Story Drift Ratio | Unit less | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 382 | LF 100 | NO | NO | minor cracked joints and minor cracks in marble / wood paneling. | significant cracks in marble / wood paneling. |  |  |  | 1 | 1 |  |  |  | 0.0035 | 0.0093 |  |  |  | Not Specified | Not Specified |  |  |  | Not Specified | Not Specified |  |  |  | 0.7 | 0.45 |  |  |  | NO | YES | Superior | Superior | Superior | Not Rated | Carefully remove cracked marble/paneling and grout at cracked joints, and install new marble/paneling and re-grout joints for 10% of full 100 foot length of wall. Existing wall board will remain place. | Install new marble/paneling for full 100 foot length of wall. Note: the gypsum wall board will also be removed and replaced which means the removal of the marble/paneling will be part of the gypsum wall board removal. |  |  |  | NO | NO |  |  |  | NO | YES |  |  |  | Not Applicable | 100 SF |  |  |  | 0% | 0 | 10% | 0.5 | [6 empty] | 0% | 0 | 5% | 0.5 | [6 empty] | NO | YES |  |  |  | 0% | 50% |  |  |  | 0 | 0.5 |  |  |  | None | Not Given | By User | By User | Not Given | none | none |  |  |  | No | None | YES
C3021.001a | C3021.001a | Generic Floor Covering - Flooding of floor caused by failure of pipe - Office - Dry | The user needs to review the fragilities of all piping modeled in the ceiling of the floor and input the peak floor acceleration value for the pipe with the lowest median peak floor acceleration value, along with the associated total dispersion (beta). Flooring type assumed to be carpet or vinyl. Available costs are per one square foot of floor area. | Normal | Not Specified | Each | Each | Peak Floor Acceleration | g | 1 | DS1 |  |  |  |  | Sequential |  |  |  |  | Seq(DS1) | 383 | By User | NO | NO | Flooding of all or a portion of the total floor associated with a major leakage of a pipe. |  |  |  |  | 1 |  |  |  |  | By User |  |  |  |  | Not Specified |  |  |  |  | Not Specified |  |  |  |  | By User |  |  |  |  | NO | NO | Not Rated | Not Rated | Not Rated | Not Rated | Replace or dry out of the affected flooring materials, equipment and contents. Remove areas that could be affected by mold. Potentially considerable downtime. Cleanup and replacement of all water damaged items on floor. User must establish area of floor with flooding. Default recommendation is flooding of total floor area. Damage to unit floor area shall be entered to consequence which is multiplied by PACT "Fragility Unit of Measure". |  |  |  |  | NO |  |  |  |  | NO |  |  |  |  | Not Applicable |  |  |  |  | 0% | 0 | [8 empty] | 0% | 0 | [8 empty] | NO |  |  |  |  | 0% |  |  |  |  | 0 |  |  |  |  | None | Not Given | By User | By User | Not Given | none |  |  |  |  | Yes | 2015-07-28 User must replace median and total dispersion (beta) associated with fragility of major piping. Made consequence generic for user specification according to particulars of structure. | NO
C3021.001b | C3021.001b | Generic Floor Covering - Flooding of floor caused by failure of pipe - Office - Humid | The user needs to review the fragilities of all piping modeled in the ceiling of the floor and input the peak floor acceleration value for the pipe with the lowest median peak floor acceleration value, along with the associated total dispersion (beta). Flooring type assumed to be carpet or vinyl. Available costs are per one square foot of floor area. | Normal | Not Specified | Each | Each | Peak Floor Acceleration | g | 1 | DS1 |  |  |  |  | Sequential |  |  |  |  | Seq(DS1) | 384 | By User | NO | NO | Flooding of all or a portion of the total floor associated with a major leakage of a pipe. |  |  |  |  | 1 |  |  |  |  | By User |  |  |  |  | Not Specified |  |  |  |  | Not Specified |  |  |  |  | By User |  |  |  |  | NO | NO | Not Rated | Not Rated | Not Rated | Not Rated | Replace or dry out of the affected flooring materials, equipment and contents. Remove areas that could be affected by mold. Potentially considerable downtime. Cleanup and replacement of all water damaged items on floor. User must establish area of floor with flooding. Default recommendation is flooding of total floor area. Damage to unit floor area shall be entered to consequence which is multiplied by PACT "Fragility Unit of Measure". |  |  |  |  | NO |  |  |  |  | NO |  |  |  |  | Not Applicable |  |  |  |  | 0% | 0 | [8 empty] | 0% | 0 | [8 empty] | NO |  |  |  |  | 0% |  |  |  |  | 0 |  |  |  |  | None | Not Given | By User | By User | Not Given | none |  |  |  |  | Yes | 2015-07-28 Made consequence generic for user specification according to particulars of structure. | NO
C3021.001c | C3021.001c | Generic Floor Covering - Flooding of floor caused by failure of pipe - Laboratory - Dry | The user needs to review the fragilities of all piping modeled in the ceiling of the floor and input the peak floor acceleration value for the pipe with the lowest median peak floor acceleration value, along with the associated total dispersion (beta). Flooring type assumed to be sheet vinyl. Available costs are per one square foot of floor area. | Normal | Not Specified | Each | Each | Peak Floor Acceleration | g | 1 | DS1 |  |  |  |  | Sequential |  |  |  |  | Seq(DS1) | 385 | By User | NO | NO | Flooding of all or a portion of the total floor associated with a major leakage of a pipe. |  |  |  |  | 1 |  |  |  |  | By User |  |  |  |  | Not Specified |  |  |  |  | Not Specified |  |  |  |  | By User |  |  |  |  | NO | NO | Not Rated | Not Rated | Not Rated | Not Rated | Replace or dry out of the affected flooring materials, equipment and contents. Remove areas that could be affected by mold. Potentially considerable downtime. Cleanup and replacement of all water damaged items on floor. User must establish area of floor with flooding. Default recommendation is flooding of total floor area. Damage to unit floor area shall be entered to consequence which is multiplied by PACT "Fragility Unit of Measure". |  |  |  |  | NO |  |  |  |  | NO |  |  |  |  | Not Applicable |  |  |  |  | 0% | 0 | [8 empty] | 0% | 0 | [8 empty] | NO |  |  |  |  | 0% |  |  |  |  | 0 |  |  |  |  | None | Not Given | By User | By User | Not Given | none |  |  |  |  | Yes | 2015-07-28 Made consequence generic for user specification according to particulars of structure. | NO
C3021.001d | C3021.001d | Generic Floor Covering - Flooding of floor caused by failure of pipe - Laboratory - Humid | The user needs to review the fragilities of all piping modeled in the ceiling of the floor and input the peak floor acceleration value for the pipe with the lowest median peak floor acceleration value, along with the associated total dispersion (beta). Flooring type assumed to be sheet vinyl. Available costs are per one square foot of floor area. | Normal | Not Specified | Each | Each | Peak Floor Acceleration | g | 1 | DS1 |  |  |  |  | Sequential |  |  |  |  | Seq(DS1) | 386 | By User | NO | NO | Flooding of all or a portion of the total floor associated with a major leakage of a pipe. |  |  |  |  | 1 |  |  |  |  | By User |  |  |  |  | Not Specified |  |  |  |  | Not Specified |  |  |  |  | By User |  |  |  |  | NO | NO | Not Rated | Not Rated | Not Rated | Not Rated | Replace or dry out of the affected flooring materials, equipment and contents. Remove areas that could be affected by mold. Potentially considerable downtime. Cleanup and replacement of all water damaged items on floor. User must establish area of floor with flooding. Default recommendation is flooding of total floor area. Damage to unit floor area shall be entered to consequence which is multiplied by PACT "Fragility Unit of Measure". |  |  |  |  | NO |  |  |  |  | NO |  |  |  |  | Not Applicable |  |  |  |  | 0% | 0 | [8 empty] | 0% | 0 | [8 empty] | NO |  |  |  |  | 0% |  |  |  |  | 0 |  |  |  |  | None | Not Given | By User | By User | Not Given | none |  |  |  |  | Yes | 2015-07-28 Made consequence generic for user specification according to particulars of structure. | NO
C3021.001e | C3021.001e | Generic Floor Covering - Flooding of floor caused by failure of pipe - Hospital - Dry | The user needs to review the fragilities of all piping modeled in the ceiling of the floor and input the peak floor acceleration value for the pipe with the lowest median peak floor acceleration value, along with the associated total dispersion (beta). Flooring type assumed to be sheet vinyl. Available costs are per one square foot of floor area. | Normal | Not Specified | Each | Each | Peak Floor Acceleration | g | 1 | DS1 |  |  |  |  | Sequential |  |  |  |  | Seq(DS1) | 387 | By User | NO | NO | Flooding of all or a portion of the total floor associated with a major leakage of a pipe. |  |  |  |  | 1 |  |  |  |  | By User |  |  |  |  | Not Specified |  |  |  |  | Not Specified |  |  |  |  | By User |  |  |  |  | NO | NO | Not Rated | Not Rated | Not Rated | Not Rated | Replace or dry out of the affected flooring materials, equipment and contents. Remove areas that could be affected by mold. Potentially considerable downtime. Cleanup and replacement of all water damaged items on floor. User must establish area of floor with flooding. Default recommendation is flooding of total floor area. Damage to unit floor area shall be entered to consequence which is multiplied by PACT "Fragility Unit of Measure". |  |  |  |  | NO |  |  |  |  | NO |  |  |  |  | Not Applicable |  |  |  |  | 0% | 0 | [8 empty] | 0% | 0 | [8 empty] | NO |  |  |  |  | 0% |  |  |  |  | 0 |  |  |  |  | None | Not Given | By User | By User | Not Given | none |  |  |  |  | Yes | 2015-07-28 Made consequence generic for user specification according to particulars of structure. | NO
C3021.001f | C3021.001f | Generic Floor Covering - Flooding of floor caused by failure of pipe - Hospital - Humid | The user needs to review the fragilities of all piping modeled in the ceiling of the floor and input the peak floor acceleration value for the pipe with the lowest median peak floor acceleration value, along with the associated total dispersion (beta). Flooring type assumed to be sheet vinyl. Available costs are per one square foot of floor area. | Normal | Not Specified | Each | Each | Peak Floor Acceleration | g | 1 | DS1 |  |  |  |  | Sequential |  |  |  |  | Seq(DS1) | 388 | By User | NO | NO | Flooding of all or a portion of the total floor associated with a major leakage of a pipe. |  |  |  |  | 1 |  |  |  |  | By User |  |  |  |  | Not Specified |  |  |  |  | Not Specified |  |  |  |  | By User |  |  |  |  | NO | NO | Not Rated | Not Rated | Not Rated | Not Rated | Replace or dry out of the affected flooring materials, equipment and contents. Remove areas that could be affected by mold. Potentially considerable downtime. Cleanup and replacement of all water damaged items on floor. User must establish area of floor with flooding. Default recommendation is flooding of total floor area. Damage to unit floor area shall be entered to consequence which is multiplied by PACT "Fragility Unit of Measure". |  |  |  |  | NO |  |  |  |  | NO |  |  |  |  | Not Applicable |  |  |  |  | 0% | 0 | [8 empty] | 0% | 0 | [8 empty] | NO |  |  |  |  | 0% |  |  |  |  | 0 |  |  |  |  | None | Not Given | By User | By User | Not Given | none |  |  |  |  | Yes | 2015-07-28 Made consequence generic for user specification according to particulars of structure. | NO
C3021.001g | C3021.001g | Generic Floor Covering - Flooding of floor caused by failure of pipe - School - Dry | The user needs to review the fragilities of all piping modeled in the ceiling of the floor and input the peak floor acceleration value for the pipe with the lowest median peak floor acceleration value, along with the associated total dispersion (beta). Flooring type assumed to be vinyl composition tile. Available costs are per one square foot of floor area. | Normal | Not Specified | Each | Each | Peak Floor Acceleration | g | 1 | DS1 |  |  |  |  | Sequential |  |  |  |  | Seq(DS1) | 389 | By User | NO | NO | Flooding of all or a portion of the total floor associated with a major leakage of a pipe. |  |  |  |  | 1 |  |  |  |  | By User |  |  |  |  | Not Specified |  |  |  |  | Not Specified |  |  |  |  | By User |  |  |  |  | NO | NO | Not Rated | Not Rated | Not Rated | Not Rated | Replace or dry out of the affected flooring materials, equipment and contents. Remove areas that could be affected by mold. Potentially considerable downtime. Cleanup and replacement of all water damaged items on floor. User must establish area of floor with flooding. Default recommendation is flooding of total floor area. Damage to unit floor area shall be entered to consequence which is multiplied by PACT "Fragility Unit of Measure". |  |  |  |  | NO |  |  |  |  | NO |  |  |  |  | Not Applicable |  |  |  |  | 0% | 0 | [8 empty] | 0% | 0 | [8 empty] | NO |  |  |  |  | 0% |  |  |  |  | 0 |  |  |  |  | None | Not Given | By User | By User | Not Given | none |  |  |  |  | Yes | 2015-07-28 Made consequence generic for user specification according to particulars of structure. | NO
C3021.001h | C3021.001h | Generic Floor Covering - Flooding of floor caused by failure of pipe - School - Humid | The user needs to review the fragilities of all piping modeled in the ceiling of the floor and input the peak floor acceleration value for the pipe with the lowest median peak floor acceleration value, along with the associated total dispersion (beta). Flooring type assumed to be vinyl composition tile. Available costs are per one square foot of floor area. | Normal | Not Specified | Each | Each | Peak Floor Acceleration | g | 1 | DS1 |  |  |  |  | Sequential |  |  |  |  | Seq(DS1) | 390 | By User | NO | NO | Flooding of all or a portion of the total floor associated with a major leakage of a pipe. |  |  |  |  | 1 |  |  |  |  | By User |  |  |  |  | Not Specified |  |  |  |  | Not Specified |  |  |  |  | By User |  |  |  |  | NO | NO | Not Rated | Not Rated | Not Rated | Not Rated | Replace or dry out of the affected flooring materials, equipment and contents. Remove areas that could be affected by mold. Potentially considerable downtime. Cleanup and replacement of all water damaged items on floor. User must establish area of floor with flooding. Default recommendation is flooding of total floor area. Damage to unit floor area shall be entered to consequence which is multiplied by PACT "Fragility Unit of Measure". |  |  |  |  | NO |  |  |  |  | NO |  |  |  |  | Not Applicable |  |  |  |  | 0% | 0 | [8 empty] | 0% | 0 | [8 empty] | NO |  |  |  |  | 0% |  |  |  |  | 0 |  |  |  |  | None | Not Given | By User | By User | Not Given | none |  |  |  |  | Yes | 2015-07-28 Made consequence generic for user specification according to particulars of structure. | NO
C3021.001i | C3021.001i | Generic Floor Covering - Flooding of floor caused by failure of pipe - Apartments - Dry | The user needs to review the fragilities of all piping modeled in the ceiling of the floor and input the peak floor acceleration value for the pipe with the lowest median peak floor acceleration value, along with the associated total dispersion (beta). Flooring type assumed to be carpet. Available costs are per one square foot of floor area. | Normal | Not Specified | Each | Each | Peak Floor Acceleration | g | 1 | DS1 |  |  |  |  | Sequential |  |  |  |  | Seq(DS1) | 391 | By User | NO | NO | Flooding of all or a portion of the total floor associated with a major leakage of a pipe. |  |  |  |  | 1 |  |  |  |  | By User |  |  |  |  | Not Specified |  |  |  |  | Not Specified |  |  |  |  | By User |  |  |  |  | NO | NO | Not Rated | Not Rated | Not Rated | Not Rated | Replace or dry out of the affected flooring materials, equipment and contents. Remove areas that could be affected by mold. Potentially considerable downtime. Cleanup and replacement of all water damaged items on floor. User must establish area of floor with flooding. Default recommendation is flooding of total floor area. Damage to unit floor area shall be entered to consequence which is multiplied by PACT "Fragility Unit of Measure". |  |  |  |  | NO |  |  |  |  | NO |  |  |  |  | Not Applicable |  |  |  |  | 0% | 0 | [8 empty] | 0% | 0 | [8 empty] | NO |  |  |  |  | 0% |  |  |  |  | 0 |  |  |  |  | None | Not Given | By User | By User | Not Given | none |  |  |  |  | Yes | 2015-07-28 Made consequence generic for user specification according to particulars of structure. | NO
C3021.001j | C3021.001j | Generic Floor Covering - Flooding of floor caused by failure of pipe - Apartments - Humid | The user needs to review the fragilities of all piping modeled in the ceiling of the floor and input the peak floor acceleration value for the pipe with the lowest median peak floor acceleration value, along with the associated total dispersion (beta). Flooring type assumed to be carpet. Available costs are per one square foot of floor area. | Normal | Not Specified | Each | Each | Peak Floor Acceleration | g | 1 | DS1 |  |  |  |  | Sequential |  |  |  |  | Seq(DS1) | 392 | By User | NO | NO | Flooding of all or a portion of the total floor associated with a major leakage of a pipe. |  |  |  |  | 1 |  |  |  |  | By User |  |  |  |  | Not Specified |  |  |  |  | Not Specified |  |  |  |  | By User |  |  |  |  | NO | NO | Not Rated | Not Rated | Not Rated | Not Rated | Replace or dry out of the affected flooring materials, equipment and contents. Remove areas that could be affected by mold. Potentially considerable downtime. Cleanup and replacement of all water damaged items on floor. User must establish area of floor with flooding. Default recommendation is flooding of total floor area. Damage to unit floor area shall be entered to consequence which is multiplied by PACT "Fragility Unit of Measure". |  |  |  |  | NO |  |  |  |  | NO |  |  |  |  | Not Applicable |  |  |  |  | 0% | 0 | [8 empty] | 0% | 0 | [8 empty] | NO |  |  |  |  | 0% |  |  |  |  | 0 |  |  |  |  | None | Not Given | By User | By User | Not Given | none |  |  |  |  | Yes | 2015-07-28 Made consequence generic for user specification according to particulars of structure. | NO
C3021.001k | C3021.001k | Generic Floor Covering - Flooding of floor caused by failure of pipe - Retail - Dry | The user needs to review the fragilities of all piping modeled in the ceiling of the floor and input the peak floor acceleration value for the pipe with the lowest median peak floor acceleration value, along with the associated total dispersion (beta). Flooring type assumed to be vinyl composition tile. Available costs are per one square foot of floor area. | Normal | Not Specified | Each | Each | Peak Floor Acceleration | g | 1 | DS1 |  |  |  |  | Sequential |  |  |  |  | Seq(DS1) | 393 | By User | NO | NO | Flooding of all or a portion of the total floor associated with a major leakage of a pipe. |  |  |  |  | 1 |  |  |  |  | By User |  |  |  |  | Not Specified |  |  |  |  | Not Specified |  |  |  |  | By User |  |  |  |  | NO | NO | Not Rated | Not Rated | Not Rated | Not Rated | Replace or dry out of the affected flooring materials, equipment and contents. Remove areas that could be affected by mold. Potentially considerable downtime. Cleanup and replacement of all water damaged items on floor. User must establish area of floor with flooding. Default recommendation is flooding of total floor area. Damage to unit floor area shall be entered to consequence which is multiplied by PACT "Fragility Unit of Measure". |  |  |  |  | NO |  |  |  |  | NO |  |  |  |  | Not Applicable |  |  |  |  | 0% | 0 | [8 empty] | 0% | 0 | [8 empty] | NO |  |  |  |  | 0% |  |  |  |  | 0 |  |  |  |  | None | Not Given | By User | By User | Not Given | none |  |  |  |  | Yes | 2015-07-28 Made consequence generic for user specification according to particulars of structure. | NO
C3021.001l | C3021.001l | Generic Floor Covering - Flooding of floor caused by failure of pipe - Retail - Humid | The user needs to review the fragilities of all piping modeled in the ceiling of the floor and input the peak floor acceleration value for the pipe with the lowest median peak floor acceleration value, along with the associated total dispersion (beta). Flooring type assumed to be vinyl composition tile. Available costs are per one square foot of floor area. | Normal | Not Specified | Each | Each | Peak Floor Acceleration | g | 1 | DS1 |  |  |  |  | Sequential |  |  |  |  | Seq(DS1) | 394 | By User | NO | NO | Flooding of all or a portion of the total floor associated with a major leakage of a pipe. |  |  |  |  | 1 |  |  |  |  | By User |  |  |  |  | Not Specified |  |  |  |  | Not Specified |  |  |  |  | By User |  |  |  |  | NO | NO | Not Rated | Not Rated | Not Rated | Not Rated | Replace or dry out of the affected flooring materials, equipment and contents. Remove areas that could be affected by mold. Potentially considerable downtime. Cleanup and replacement of all water damaged items on floor. User must establish area of floor with flooding. Default recommendation is flooding of total floor area. Damage to unit floor area shall be entered to consequence which is multiplied by PACT "Fragility Unit of Measure". |  |  |  |  | NO |  |  |  |  | NO |  |  |  |  | Not Applicable |  |  |  |  | 0% | 0 | [8 empty] | 0% | 0 | [8 empty] | NO |  |  |  |  | 0% |  |  |  |  | 0 |  |  |  |  | None | Not Given | By User | By User | Not Given | none |  |  |  |  | Yes | 2015-07-28 Made consequence generic for user specification according to particulars of structure. | NO
C3021.001m | C3021.001m | Generic Floor Covering - Flooding of floor caused by failure of pipe - Warehouse - Dry | The user needs to review the fragilities of all piping modeled in the ceiling of the floor and input the peak floor acceleration value for the pipe with the lowest median peak floor acceleration value, along with the associated total dispersion (beta). Flooring type assumed to be sealed concrete. Available costs are per one square foot of floor area. | Normal | Not Specified | Each | Each | Peak Floor Acceleration | g | 1 | DS1 |  |  |  |  | Sequential |  |  |  |  | Seq(DS1) | 395 | By User | NO | NO | Flooding of all or a portion of the total floor associated with a major leakage of a pipe. |  |  |  |  | 1 |  |  |  |  | By User |  |  |  |  | Not Specified |  |  |  |  | Not Specified |  |  |  |  | By User |  |  |  |  | NO | NO | Not Rated | Not Rated | Not Rated | Not Rated | Replace or dry out of the affected flooring materials, equipment and contents. Remove areas that could be affected by mold. Potentially considerable downtime. Cleanup and replacement of all water damaged items on floor. User must establish area of floor with flooding. Default recommendation is flooding of total floor area. Damage to unit floor area shall be entered to consequence which is multiplied by PACT "Fragility Unit of Measure". |  |  |  |  | NO |  |  |  |  | NO |  |  |  |  | Not Applicable |  |  |  |  | 0% | 0 | [8 empty] | 0% | 0 | [8 empty] | NO |  |  |  |  | 0% |  |  |  |  | 0 |  |  |  |  | None | Not Given | By User | By User | Not Given | none |  |  |  |  | Yes | 2015-07-28 Made consequence generic for user specification according to particulars of structure. | NO
C3021.001n | C3021.001n | Generic Floor Covering - Flooding of floor caused by failure of pipe - Warehouse - Humid | The user needs to review the fragilities of all piping modeled in the ceiling of the floor and input the peak floor acceleration value for the pipe with the lowest median peak floor acceleration value, along with the associated total dispersion (beta). Flooring type assumed to be sealed concrete. Available costs are per one square foot of floor area. | Normal | Not Specified | Each | Each | Peak Floor Acceleration | g | 1 | DS1 |  |  |  |  | Sequential |  |  |  |  | Seq(DS1) | 396 | By User | NO | NO | Flooding of all or a portion of the total floor associated with a major leakage of a pipe. |  |  |  |  | 1 |  |  |  |  | By User |  |  |  |  | Not Specified |  |  |  |  | Not Specified |  |  |  |  | By User |  |  |  |  | NO | NO | Not Rated | Not Rated | Not Rated | Not Rated | Replace or dry out of the affected flooring materials, equipment and contents. Remove areas that could be affected by mold. Potentially considerable downtime. Cleanup and replacement of all water damaged items on floor. User must establish area of floor with flooding. Default recommendation is flooding of total floor area. Damage to unit floor area shall be entered to consequence which is multiplied by PACT "Fragility Unit of Measure". |  |  |  |  | NO |  |  |  |  | NO |  |  |  |  | Not Applicable |  |  |  |  | 0% | 0 | [8 empty] | 0% | 0 | [8 empty] | NO |  |  |  |  | 0% |  |  |  |  | 0 |  |  |  |  | None | Not Given | By User | By User | Not Given | none |  |  |  |  | Yes | 2015-07-28 Made consequence generic for user specification according to particulars of structure. | NO
C3021.001o | C3021.001o | Generic Floor Covering - Flooding of floor caused by failure of pipe - Hospitality - Dry | The user needs to review the fragilities of all piping modeled in the ceiling of the floor and input the peak floor acceleration value for the pipe with the lowest median peak floor acceleration value, along with the associated total dispersion (beta). Flooring type assumed to be carpet. Available costs are per one square foot of floor area. | Normal | Not Specified | Each | Each | Peak Floor Acceleration | g | 1 | DS1 |  |  |  |  | Sequential |  |  |  |  | Seq(DS1) | 397 | By User | NO | NO | Flooding of all or a portion of the total floor associated with a major leakage of a pipe. |  |  |  |  | 1 |  |  |  |  | By User |  |  |  |  | Not Specified |  |  |  |  | Not Specified |  |  |  |  | By User |  |  |  |  | NO | NO | Not Rated | Not Rated | Not Rated | Not Rated | Replace or dry out of the affected flooring materials, equipment and contents. Remove areas that could be affected by mold. Potentially considerable downtime. Cleanup and replacement of all water damaged items on floor. User must establish area of floor with flooding. Default recommendation is flooding of total floor area. Damage to unit floor area shall be entered to consequence which is multiplied by PACT "Fragility Unit of Measure". |  |  |  |  | NO |  |  |  |  | NO |  |  |  |  | Not Applicable |  |  |  |  | 0% | 0 | [8 empty] | 0% | 0 | [8 empty] | NO |  |  |  |  | 0% |  |  |  |  | 0 |  |  |  |  | None | Not Given | By User | By User | Not Given | none |  |  |  |  | Yes | 2015-07-28 Made consequence generic for user specification according to particulars of structure. | NO
C3021.001p | C3021.001p | Generic Floor Covering - Flooding of floor caused by failure of pipe - Hospitality - Humid | The user needs to review the fragilities of all piping modeled in the ceiling of the floor and input the peak floor acceleration value for the pipe with the lowest median peak floor acceleration value, along with the associated total dispersion (beta). Flooring type assumed to be carpet. Available costs are per one square foot of floor area. | Normal | Not Specified | Each | Each | Peak Floor Acceleration | g | 1 | DS1 |  |  |  |  | Sequential |  |  |  |  | Seq(DS1) | 398 | By User | NO | NO | Flooding of all or a portion of the total floor associated with a major leakage of a pipe. |  |  |  |  | 1 |  |  |  |  | By User |  |  |  |  | Not Specified |  |  |  |  | Not Specified |  |  |  |  | By User |  |  |  |  | NO | NO | Not Rated | Not Rated | Not Rated | Not Rated | Replace or dry out of the affected flooring materials, equipment and contents. Remove areas that could be affected by mold. Potentially considerable downtime. Cleanup and replacement of all water damaged items on floor. User must establish area of floor with flooding. Default recommendation is flooding of total floor area. Damage to unit floor area shall be entered to consequence which is multiplied by PACT "Fragility Unit of Measure". |  |  |  |  | NO |  |  |  |  | NO |  |  |  |  | Not Applicable |  |  |  |  | 0% | 0 | [8 empty] | 0% | 0 | [8 empty] | NO |  |  |  |  | 0% |  |  |  |  | 0 |  |  |  |  | None | Not Given | By User | By User | Not Given | none |  |  |  |  | Yes | 2015-07-28 Made consequence generic for user specification according to particulars of structure. | NO
C3027.001 | C3027.001 | Raised Access Floor, non seismically rated. | Access floor unanchored or anchored with adhesive. Costing is based upon a xxx SF floor area. | Normal | All | Each | Each | Peak Floor Acceleration | g | 1 | DS1 |  |  |  |  | Sequential |  |  |  |  | Seq(DS1) | 399 | SF 100 | NO | NO | Minor damage to the flooring system. Damage to the equipment of the flooring system. |  |  |  |  | 1 |  |  |  |  | 0.5 |  |  |  |  | Not Specified |  |  |  |  | Not Specified |  |  |  |  | 0.5 |  |  |  |  | NO | NO | Not Rated | Not Rated | Not Rated | Not Rated | Repair the flooring system, assume cost equal to 5% of the replacement cost. Repair the flooring equipment, assume a cost equal to 10% of the replacement cost. |  |  |  |  | NO |  |  |  |  | NO |  |  |  |  | Not Applicable |  |  |  |  | 0% | 0 | [8 empty] | 0% | 0 | [8 empty] | NO |  |  |  |  | 0% |  |  |  |  | 0 |  |  |  |  | Consequence Note: Some downtime for repair of floor and equipment. | Not Given | By User | By User | Not Given | none |  |  |  |  | No | None | YES
C3027.002 | C3027.002 | Raised Access Floor, seismically rated. | Access floor is designed to meet code requirements and mechanically anchored and braced as necessary to resist anchor loads. Equipment is anchored to floor systems and heavier equipment is anchored directly to the structural floor. Costing is based upon a xxx SF floor area. | Normal | All | Each | Each | Peak Floor Acceleration | g | 1 | DS1 |  |  |  |  | Sequential |  |  |  |  | Seq(DS1) | 400 | SF 100 | NO | NO | Minor damage to the flooring system. Damage to the equipment of the flooring system. |  |  |  |  | 1 |  |  |  |  | 1.5 |  |  |  |  | Not Specified |  |  |  |  | Not Specified |  |  |  |  | 0.4 |  |  |  |  | NO | NO | Not Rated | Not Rated | Not Rated | Not Rated | Repair the flooring system, assume cost equal to 5% of the replacement cost. Repair the flooring equipment, assume a cost equal to 10% of the replacement cost. |  |  |  |  | NO |  |  |  |  | NO |  |  |  |  | Not Applicable |  |  |  |  | 0% | 0 | [8 empty] | 0% | 0 | [8 empty] | NO |  |  |  |  | 0% |  |  |  |  | 0 |  |  |  |  | Consequence Note: Some downtime for repair of floor and equipment. | Not Given | By User | By User | Not Given | none |  |  |  |  | No | None | YES
C3032.001a | C3032.001a | Suspended Ceiling, SDC A,B,C, Area (A): A < 250, Vert support only | Costing for each 250 SF Unit, Suspended Lay-in Acoustic Tile Ceiling, Support: Vertical hanging wires only. Includes lighting fixtures in suspended ceiling. | Normal | SDC A, B, or C | Each | Each | Peak Floor Acceleration | g | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 401 | SF 250 | NO | NO | 5 % of ceiling grid and tile damage. | 30% of ceiling grid and tile damage. | 50% of ceiling grid and tile damage. |  |  | 1 | 1 | 1 |  |  | 1.17 | 1.58 | 1.82 |  |  | Not Specified | Not Specified | Not Specified |  |  | Not Specified | Not Specified | Not Specified |  |  | 0.25 | 0.25 | 0.25 |  |  | NO | NO | Marginal | Superior | Marginal | Average | Reinstall, repair, or replace 5% of the ceiling area. | Replace 30% of the ceiling area. | Replace the entire ceiling |  |  | NO | NO | NO |  |  | NO | NO | YES |  |  | Not Applicable | Not Applicable | 250 SF |  |  | 0% | 0 | 0% | 0 | 10% | 0.5 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | NO | NO |  |  | 0% | 0% | 0% |  |  | 0 | 0 | 0 |  |  | None | Not Given | By User | By User | Not Given | none | none | none |  |  | Yes | 2015-07-28 Update median demand and dispersion beta. 2015-08-21 Added SDC C | YES
C3032.001b | C3032.001b | Suspended Ceiling, SDC A,B,C, Area (A): 250 < A < 1000, Vert support only | Costing for each 600 SF Unit, Suspended Lay-in Acoustic Tile Ceiling, Support: Vertical hanging wires only. Includes lighting fixtures in suspended ceiling. | Normal | SDC A, B, or C | Each | Each | Peak Floor Acceleration | g | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 402 | SF 600 | NO | NO | 5 % of ceiling grid and tile damage. | 30% of ceiling grid and tile damage. | 50% of ceiling grid and tile damage. |  |  | 1 | 1 | 1 |  |  | 1.01 | 1.45 | 1.69 |  |  | Not Specified | Not Specified | Not Specified |  |  | Not Specified | Not Specified | Not Specified |  |  | 0.25 | 0.25 | 0.25 |  |  | NO | NO | Marginal | Superior | Marginal | Average | Reinstall, repair, or replace 5% of the ceiling area. | Replace 30% of the ceiling area. | Replace the entire ceiling |  |  | NO | NO | NO |  |  | NO | NO | YES |  |  | Not Applicable | Not Applicable | 650 SF |  |  | 0% | 0 | 0% | 0 | 10% | 0.5 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | NO | NO |  |  | 0% | 0% | 0% |  |  | 0 | 0 | 0 |  |  | None | Not Given | By User | By User | Not Given | none | none | none |  |  | Yes | 2015-07-28 Update median demand and dispersion beta. 2015-08-21 Added SDC C | YES
C3032.001c | C3032.001c | Suspended Ceiling, SDC A,B,C, Area (A): 1000 < A < 2500, Vert support only | Costing for each 1800 SF Unit, Suspended Lay-in Acoustic Tile Ceiling, Support: Vertical hanging wires only. Includes lighting fixtures in suspended ceiling. | Normal | SDC A, B, or C | Each | Each | Peak Floor Acceleration | g | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 403 | SF 1800 | NO | NO | 5 % of ceiling grid and tile damage. | 30% of ceiling grid and tile damage. | 50% of ceiling grid and tile damage. |  |  | 1 | 1 | 1 |  |  | 0.7 | 1.2 | 1.43 |  |  | Not Specified | Not Specified | Not Specified |  |  | Not Specified | Not Specified | Not Specified |  |  | 0.25 | 0.25 | 0.25 |  |  | NO | NO | Marginal | Superior | Marginal | Average | Reinstall, repair, or replace 5% of the ceiling area. | Replace 30% of the ceiling area. | Replace the entire ceiling |  |  | NO | NO | NO |  |  | NO | NO | YES |  |  | Not Applicable | Not Applicable | 1700 SF |  |  | 0% | 0 | 0% | 0 | 10% | 0.5 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | NO | NO |  |  | 0% | 0% | 0% |  |  | 0 | 0 | 0 |  |  | None | Not Given | By User | By User | Not Given | none | none | none |  |  | Yes | 2015-07-28 Update median demand and dispersion beta. 2015-08-21 Added SDC C | YES
C3032.001d | C3032.001d | Suspended Ceiling, SDC A,B,C, Area (A): A > 2500, Vert support only | Costing for each 2500 SF Unit, Suspended Lay-in Acoustic Tile Ceiling, Support: Vertical hanging wires only. Includes lighting fixtures in suspended ceiling. | Normal | SDC A, B, or C | Each | Each | Peak Floor Acceleration | g | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 404 | SF 2500 | NO | NO | 5 % of ceiling grid and tile damage. | 30% of ceiling grid and tile damage. | 50% of ceiling grid and tile damage. |  |  | 1 | 1 | 1 |  |  | 0.56 | 1.08 | 1.31 |  |  | Not Specified | Not Specified | Not Specified |  |  | Not Specified | Not Specified | Not Specified |  |  | 0.25 | 0.25 | 0.25 |  |  | NO | NO | Marginal | Superior | Marginal | Average | Reinstall, repair, or replace 5% of the ceiling area. | Replace 30% of the ceiling area. | Replace the entire ceiling |  |  | NO | NO | NO |  |  | NO | NO | YES |  |  | Not Applicable | Not Applicable | 2500 SF |  |  | 0% | 0 | 0% | 0 | 10% | 0.5 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | YES | YES |  |  | 0% | 75% | 50% |  |  | 0 | 0.5 | 0.5 |  |  | None | Not Given | By User | By User | Not Given | none | none | none |  |  | Yes | 2015-07-28 Update median demand and dispersion beta. 2015-08-21 Added SDC C | YES
C3032.003a | C3032.003a | Suspended Ceiling, SDC D,E (Ip=1.0), Area (A): A < 250, Vert & Lat support | Costing for each 250 SF Unit, Suspended Lay-in Acoustic Tile Ceiling, Support: Vertical hanging wire, diagonal wires, and compression posts, 2 inch wide ledger support angles at wall and oversize holes around tile openings. Includes lighting fixtures in suspended ceiling. | Normal | SDC D or E (Ip = 1.0) | Each | Each | Peak Floor Acceleration | g | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 405 | SF 250 | NO | NO | 5 % of ceiling grid and tile damage. | 30% of ceiling grid and tile damage. | 50% of ceiling grid and tile damage. |  |  | 1 | 1 | 1 |  |  | 1.6 | 1.95 | 2.07 |  |  | Not Specified | Not Specified | Not Specified |  |  | Not Specified | Not Specified | Not Specified |  |  | 0.3 | 0.3 | 0.3 |  |  | NO | NO | Marginal | Superior | Marginal | Average | Reinstall, repair, or replace 5% of the ceiling area. | Replace 30% of the ceiling area. | Replace the entire ceiling |  |  | NO | NO | NO |  |  | NO | NO | YES |  |  | Not Applicable | Not Applicable | 250 SF |  |  | 0% | 0 | 0% | 0 | 10% | 0.5 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | NO | NO |  |  | 0% | 0% | 0% |  |  | 0 | 0 | 0 |  |  | None | Not Given | By User | By User | Not Given | none | none | none |  |  | Yes | 2015-07-28 Update median demand and dispersion beta. | YES
C3032.003b | C3032.003b | Suspended Ceiling, SDC D,E (Ip=1.0), Area (A): 250 < A < 1000, Vert & Lat support | Costing for each 600 SF Unit, Suspended Lay-in Acoustic Tile Ceiling, Support: Vertical hanging wire, diagonal wires, and compression posts, 2 inch wide ledger support angles at wall and oversize holes around tile openings. Includes lighting fixtures in suspended ceiling. | Normal | SDC D or E (Ip = 1.0) | Each | Each | Peak Floor Acceleration | g | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 406 | SF 600 | NO | NO | 5 % of ceiling grid and tile damage. | 30% of ceiling grid and tile damage. | 50% of ceiling grid and tile damage. |  |  | 1 | 1 | 1 |  |  | 1.47 | 1.88 | 2.03 |  |  | Not Specified | Not Specified | Not Specified |  |  | Not Specified | Not Specified | Not Specified |  |  | 0.3 | 0.3 | 0.3 |  |  | NO | NO | Marginal | Superior | Marginal | Average | Reinstall, repair, or replace 5% of the ceiling area. | Replace 30% of the ceiling area. | Replace the entire ceiling |  |  | NO | NO | NO |  |  | NO | NO | YES |  |  | Not Applicable | Not Applicable | 650 SF |  |  | 0% | 0 | 0% | 0 | 10% | 0.5 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | NO | NO |  |  | 0% | 0% | 0% |  |  | 0 | 0 | 0 |  |  | None | Not Given | By User | By User | Not Given | none | none | none |  |  | Yes | 2015-07-28 Update median demand and dispersion beta. | YES
C3032.003c | C3032.003c | Suspended Ceiling, SDC D,E (Ip=1.0), Area (A): 1000 < A < 2500, Vert & Lat support | Costing for each 1800 SF Unit, Suspended Lay-in Acoustic Tile Ceiling, Support: Vertical hanging wire, diagonal wires, and compression posts, 2 inch wide ledger support angles at wall and oversize holes around tile openings. Includes lighting fixtures in suspended ceiling. | Normal | SDC D or E (Ip = 1.0) | Each | Each | Peak Floor Acceleration | g | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 407 | SF 1800 | NO | NO | 5 % of ceiling grid and tile damage. | 30% of ceiling grid and tile damage. | 50% of ceiling grid and tile damage. |  |  | 1 | 1 | 1 |  |  | 1.21 | 1.75 | 1.95 |  |  | Not Specified | Not Specified | Not Specified |  |  | Not Specified | Not Specified | Not Specified |  |  | 0.3 | 0.3 | 0.3 |  |  | NO | NO | Marginal | Superior | Marginal | Average | Reinstall, repair, or replace 5% of the ceiling area. | Replace 30% of the ceiling area. | Replace the entire ceiling |  |  | NO | NO | NO |  |  | NO | NO | YES |  |  | Not Applicable | Not Applicable | 1700 SF |  |  | 0% | 0 | 0% | 0 | 10% | 0.5 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | NO | NO |  |  | 0% | 0% | 0% |  |  | 0 | 0 | 0 |  |  | None | Not Given | By User | By User | Not Given | none | none | none |  |  | Yes | 2015-07-28 Update median demand and dispersion beta. | YES
C3032.003d | C3032.003d | Suspended Ceiling, SDC D,E (Ip=1.0), Area (A): A > 2500, Vert & Lat support | Costing for each 2500 SF Unit, Suspended Lay-in Acoustic Tile Ceiling, Support: Vertical hanging wire, diagonal wires, and compression posts, 2 inch wide ledger support angles at wall and oversize holes around tile openings. Includes lighting fixtures in suspended ceiling. | Normal | SDC D or E (Ip = 1.0) | Each | Each | Peak Floor Acceleration | g | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 408 | SF 2500 | NO | NO | 5 % of ceiling grid and tile damage. | 30% of ceiling grid and tile damage. | 50% of ceiling grid and tile damage. |  |  | 1 | 1 | 1 |  |  | 1.09 | 1.69 | 1.91 |  |  | Not Specified | Not Specified | Not Specified |  |  | Not Specified | Not Specified | Not Specified |  |  | 0.3 | 0.3 | 0.3 |  |  | NO | NO | Marginal | Superior | Marginal | Average | Reinstall, repair, or replace 5% of the ceiling area. | Replace 30% of the ceiling area. | Replace the entire ceiling |  |  | NO | NO | NO |  |  | NO | NO | YES |  |  | Not Applicable | Not Applicable | 2500 SF |  |  | 0% | 0 | 0% | 0 | 10% | 0.5 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | YES | YES |  |  | 0% | 75% | 50% |  |  | 0 | 0.5 | 0.5 |  |  | None | Not Given | By User | By User | Not Given | none | none | none |  |  | Yes | 2015-07-28 Update median demand and dispersion beta. | YES
C3032.004a | C3032.004a | Suspended Ceiling, SDC D,E,F (Ip=1.5), Area (A): A < 250, Vert & Lat support | Costing for each 250 SF Unit, Suspended Lay-in Acoustic Tile Ceiling, Support: Vertical hanging wire, diagonal wires, and compression posts, 2 inch wide ledger support angles at wall and oversize holes around tile openings. Includes lighting fixtures in suspended ceiling. | Special Inspection (e.g. OSHPD) | SDC D, E or F (Ip = 1.5) | Each | Each | Peak Floor Acceleration | g | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 409 | SF 250 | NO | NO | 5 % of ceiling grid and tile damage. | 30% of ceiling grid and tile damage. | 50% of ceiling grid and tile damage. |  |  | 1 | 1 | 1 |  |  | 1.92 | 2.34 | 2.48 |  |  | Not Specified | Not Specified | Not Specified |  |  | Not Specified | Not Specified | Not Specified |  |  | 0.3 | 0.3 | 0.3 |  |  | NO | NO | Marginal | Superior | Marginal | Average | Reinstall, repair, or replace 5% of the ceiling area. | Replace 30% of the ceiling area. | Replace the entire ceiling |  |  | NO | NO | NO |  |  | NO | NO | YES |  |  | Not Applicable | Not Applicable | 250 SF |  |  | 0% | 0 | 0% | 0 | 10% | 0.5 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | NO | NO |  |  | 0% | 0% | 0% |  |  | 0 | 0 | 0 |  |  | None | Not Given | By User | By User | Not Given | none | none | none |  |  | Yes | 2015-07-28 Update median demand and dispersion beta. | YES
C3032.004b | C3032.004b | Suspended Ceiling, SDC D,E,F (Ip=1.5), Area (A): 250 < A < 1000, Vert & Lat support | Costing for each 600 SF Unit, Suspended Lay-in Acoustic Tile Ceiling, Support: Vertical hanging wire, diagonal wires, and compression posts, 2 inch wide ledger support angles at wall and oversize holes around tile openings. Includes lighting fixtures in suspended ceiling. | Special Inspection (e.g. OSHPD) | SDC D, E or F (Ip = 1.5) | Each | Each | Peak Floor Acceleration | g | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 410 | SF 600 | NO | NO | 5 % of ceiling grid and tile damage. | 30% of ceiling grid and tile damage. | 50% of ceiling grid and tile damage. |  |  | 1 | 1 | 1 |  |  | 1.76 | 2.26 | 2.44 |  |  | Not Specified | Not Specified | Not Specified |  |  | Not Specified | Not Specified | Not Specified |  |  | 0.3 | 0.3 | 0.3 |  |  | NO | NO | Marginal | Superior | Marginal | Average | Reinstall, repair, or replace 5% of the ceiling area. | Replace 30% of the ceiling area. | Replace the entire ceiling |  |  | NO | NO | NO |  |  | NO | NO | YES |  |  | Not Applicable | Not Applicable | 650 SF |  |  | 0% | 0 | 0% | 0 | 10% | 0.5 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | NO | NO |  |  | 0% | 0% | 0% |  |  | 0 | 0 | 0 |  |  | None | Not Given | By User | By User | Not Given | none | none | none |  |  | Yes | 2015-07-28 Update median demand and dispersion beta. | YES
C3032.004c | C3032.004c | Suspended Ceiling, SDC D,E,F (Ip=1.5), Area (A): 1000 < A < 2500, Vert & Lat support | Costing for each 1800 SF Unit, Suspended Lay-in Acoustic Tile Ceiling, Support: Vertical hanging wire, diagonal wires, and compression posts, 2 inch wide ledger support angles at wall and oversize holes around tile openings. Includes lighting fixtures in suspended ceiling. | Special Inspection (e.g. OSHPD) | SDC D, E or F (Ip = 1.5) | Each | Each | Peak Floor Acceleration | g | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 411 | SF 1800 | NO | NO | 5 % of ceiling grid and tile damage. | 30% of ceiling grid and tile damage. | 50% of ceiling grid and tile damage. |  |  | 1 | 1 | 1 |  |  | 1.45 | 2.1 | 2.34 |  |  | Not Specified | Not Specified | Not Specified |  |  | Not Specified | Not Specified | Not Specified |  |  | 0.3 | 0.3 | 0.3 |  |  | NO | NO | Marginal | Superior | Marginal | Average | Reinstall, repair, or replace 5% of the ceiling area. | Replace 30% of the ceiling area. | Replace the entire ceiling |  |  | NO | NO | NO |  |  | NO | NO | YES |  |  | Not Applicable | Not Applicable | 1700 SF |  |  | 0% | 0 | 0% | 0 | 10% | 0.5 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | NO | NO |  |  | 0% | 0% | 0% |  |  | 0 | 0 | 0 |  |  | None | Not Given | By User | By User | Not Given | none | none | none |  |  | Yes | 2015-07-28 Update median demand and dispersion beta. | YES
C3032.004d | C3032.004d | Suspended Ceiling, SDC D,E,F (Ip=1.5), Area (A): A > 2500, Vert & Lat support | Costing for each 2500 SF Unit, Suspended Lay-in Acoustic Tile Ceiling, Support: Vertical hanging wire, diagonal wires, and compression posts, 2 inch wide ledger support angles at wall and oversize holes around tile openings. Includes lighting fixtures in suspended ceiling. | Special Inspection (e.g. OSHPD) | SDC D, E or F (Ip = 1.5) | Each | Each | Peak Floor Acceleration | g | 3 | DS1 | DS2 | DS3 |  |  | Sequential | Sequential | Sequential |  |  | Seq(DS1,DS2,DS3) | 412 | SF 2500 | NO | NO | 5 % of ceiling grid and tile damage. | 30% of ceiling grid and tile damage. | 50% of ceiling grid and tile damage. |  |  | 1 | 1 | 1 |  |  | 1.31 | 2.03 | 2.29 |  |  | Not Specified | Not Specified | Not Specified |  |  | Not Specified | Not Specified | Not Specified |  |  | 0.3 | 0.3 | 0.3 |  |  | NO | NO | Marginal | Superior | Marginal | Average | Reinstall, repair, or replace 5% of the ceiling area. | Replace 30% of the ceiling area. | Replace the entire ceiling |  |  | NO | NO | NO |  |  | NO | NO | YES |  |  | Not Applicable | Not Applicable | 2500 SF |  |  | 0% | 0 | 0% | 0 | 10% | 0.5 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | YES | YES |  |  | 0% | 75% | 50% |  |  | 0 | 0.5 | 0.5 |  |  | None | Not Given | By User | By User | Not Given | none | none | none |  |  | Yes | 2015-07-28 Update median demand and dispersion beta. | YES
C3034.001 | C3034.001 | Independent Pendant Lighting - non seismic | Horizontal light fixtures 4 to 16 ft long suspended 12 to 24 inches from ceiling. No seismic design or bracing. Hung from ceiling above by two or more rods or cables. | Normal | All | Each | Each | Peak Floor Acceleration | g | 1 | DS1 |  |  |  |  | Sequential |  |  |  |  | Seq(DS1) | 413 | EA 1 | NO | NO | Disassembly of rod system at connections with horizontal light fixture, low cycle fatigue failure of the threaded rod, pullout of rods from ceiling assembly. |  |  |  |  | 1 |  |  |  |  | 0.6 |  |  |  |  | Not Specified |  |  |  |  | Not Specified |  |  |  |  | 0.4 |  |  |  |  | NO | NO | Not Rated | Not Rated | Not Rated | Not Rated | Replace damaged lighting components. |  |  |  |  | NO |  |  |  |  | YES |  |  |  |  | 100 SF |  |  |  |  | 75% | 0.5 | [8 empty] | 25% | 0.5 | [8 empty] | NO |  |  |  |  | 0% |  |  |  |  | 0 |  |  |  |  | Low cost industrial hung lighting in warehouse or gymnasium that is not part of suspended ceiling or hanging from a suspended ceiling space. | Not Given | By User | By User | Not Given | none |  |  |  |  | Yes | None | YES
C3034.002 | C3034.002 | Independent Pendant Lighting - seismically rated | Horizontal light fixtures 4 to 16 ft long suspended 12 to 24 inches from ceiling. Hung from ceiling above by two or more rods or cables. Fixture and rods or cables are either designed for seismic movements or are laterally braced to prevent sway. | Normal | All | Each | Each | Peak Floor Acceleration | g | 1 | DS1 |  |  |  |  | Sequential |  |  |  |  | Seq(DS1) | 414 | EA 1 | NO | NO | Disassembly of rod system at connections with horizontal light fixture, low cycle fatigue failure of the threaded rod, pullout of rods from ceiling assembly. |  |  |  |  | 1 |  |  |  |  | 1.5 |  |  |  |  | Not Specified |  |  |  |  | Not Specified |  |  |  |  | 0.4 |  |  |  |  | NO | NO | Not Rated | Not Rated | Not Rated | Not Rated | Replace damaged lighting components. |  |  |  |  | NO |  |  |  |  | NO |  |  |  |  | Not Applicable |  |  |  |  | 0% | 0 | [8 empty] | 0% | 0 | [8 empty] | NO |  |  |  |  | 0% |  |  |  |  | 0 |  |  |  |  | Low cost industrial hung lighting in warehouse or gymnasium that is not part of suspended ceiling or hanging from a suspended ceiling space. | Not Given | By User | By User | Not Given | none |  |  |  |  | Yes | None | YES
D1014.011 | D1014.011 | Traction Elevator – Applies to most California Installations 1976 or later, most western states installations 1982 or later and most other U.S installations 1998 or later. | Costing per elevator. Elevator demand parameter shall be defined as the peak floor acceleration at the first floor. The elevator fragility for a multiple story building should only be entered once on the first floor. | Any | Any | Each | Each | Peak Floor Acceleration | g | 4 | DS1 | DS2 | DS3 | DS4 |  | Simultaneous | Simultaneous | Simultaneous | Simultaneous |  | Simul(DS1,DS2,DS3,DS4) | 415 | EA 1 | YES | BLDG | Controller anchorage failed, and or machine anchorage failed, and or motor generator anchorage failed, and or governor anchorage failed, and or rope guard failures. | Rail distortion, and or intermediate bracket separate and spread, and or counterweight bracket break or bend, and or car bracket break or bend, and or car guide shoes damaged, and or counterweight guide shoes damaged, and or counterweight frame distortion, and or tail sheave dislodged and/or twisted | Cab stabilizers bent, or cab walls damaged, or cab doors damaged. | Cab ceiling damaged. |  | 0.26 | 0.79 | 0.68 | 0.17 |  | 0.39 | 0.39 | 0.39 | 0.39 |  | 0.4 | Not Specified | Not Specified | Not Specified |  | 0.1 | Not Specified | Not Specified | Not Specified |  | 0.45 | 0.45 | 0.45 | 0.45 |  | NO | NO | Not Rated | Not Rated | Not Rated | Not Rated | Multiple repairs possible (% change of each): Reinstall or replace controller (4%), and or reinstall or replace motor generator (63%), and or Install new generator with appropriate anchors (23%), and or Install new governor (7%), and or Reinstall or replace rope guards (15%). | Multiple repairs possible (% change of each): Replace rail (62%), and or replace bracket or tie rod (28%), and or replace counterweight bracket 14%), and or replace intermediate bracket (28%), and or replace car guide shoes (35%), and or replace counterweight guide shoe (28%), and or repair or replace counterweight frame (28%), and or repair or replace tail sheave (1%) | Multiple repairs possible (% change of each): Repair or replace cab walls (3%), and or repair or replace cab doors (17%), and or repair or replace cab stabilizers (92%) | Multiple repairs possible (% change of each): Repair or replace cab ceiling (100%) |  | YES | YES | YES | YES |  | NO | NO | NO | YES |  | Not Applicable | Not Applicable | Not Applicable | 40 SF |  | 0% | 0 | 0% | 0 | 0% | 0 | 10% | 0.5 |  |  | 0% | 0 | 0% | 0 | 0% | 0 | 5% | 0.5 |  |  | NO | NO | NO | NO |  | 0% | 0% | 0% | 0% |  | 0 | 0 | 0 | 0 |  | None | Not Given | By User | By User | Not Given | D1014.010-DS1-1.JPG | D1014.010-DS2-6.JPG | none | D1014.010-DS4-1.JPG |  | No | None | YES
D1014.012 | D1014.012 | Traction Elevator – Applies to most California Installations prior to 1976, most western states installations prior to 1982 and most other U.S installations prior to 1998. | Costing per elevator. Elevator demand parameter shall be defined as the peak floor acceleration at the first floor. The elevator fragility for a multiple story building should only be entered once on the first floor. | Any | Any | Each | Each | Peak Floor Acceleration | g | 4 | DS1 | DS2 | DS3 | DS4 |  | Simultaneous | Simultaneous | Simultaneous | Simultaneous |  | Simul(DS1,DS2,DS3,DS4) | 416 | EA 1 | YES | BLDG | Controller anchorage failed, and or machine anchorage failed, and or motor generator anchorage failed, and or governor anchorage failed, and or rope guard failures. | Rail distortion, and or intermediate bracket separate and spread, and or counterweight bracket break or bend, and or car bracket break or bend, and or car guide shoes damaged, and or counterweight guide shoes damaged, and or counterweight frame distortion, and or tail sheave dislodged and/or twisted | Cab stabilizers bent, or cab walls damaged, or cab doors damaged. | Cab ceiling damaged. |  | 0.26 | 0.79 | 0.68 | 0.17 |  | 0.31 | 0.31 | 0.31 | 0.31 |  | Not Specified | Not Specified | Not Specified | Not Specified |  | Not Specified | Not Specified | Not Specified | Not Specified |  | 0.45 | 0.45 | 0.45 | 0.45 |  | NO | NO | Not Rated | Not Rated | Not Rated | Not Rated | Multiple repairs possible (% change of each): Reinstall or replace controller (4%), and or reinstall or replace motor generator (63%), and or Install new generator with appropriate anchors (23%), and or Install new governor (7%), and or Reinstall or replace rope guards (15%). | Multiple repairs possible (% change of each): Replace rail (62%), and or replace bracket or tie rod (28%), and or replace counterweight bracket 14%), and or replace intermediate bracket (28%), and or replace car guide shoes (35%), and or replace counterweight guide shoe (28%), and or repair or replace counterweight frame (28%), and or repair or replace tail sheave (1%) | Multiple repairs possible (% change of each): Repair or replace cab walls (3%), and or repair or replace cab doors (17%), and or repair or replace cab stabilizers (92%) | Multiple repairs possible (% change of each): Repair or replace cab ceiling (100%) |  | YES | YES | YES | YES |  | NO | NO | NO | YES |  | Not Applicable | Not Applicable | Not Applicable | 40 SF |  | 0% | 0 | 0% | 0 | 0% | 0 | 10% | 0.5 |  |  | 0% | 0 | 0% | 0 | 0% | 0 | 5% | 0.5 |  |  | NO | NO | NO | NO |  | 0% | 0% | 0% | 0% |  | 0 | 0 | 0 | 0 |  | None | Not Given | By User | By User | Not Given | D1014.010-DS1-1.JPG | D1014.010-DS2-6.JPG | none | D1014.010-DS4-1.JPG |  | No | None | YES
D1014.021 | D1014.021 | Hydraulic Elevator – Applies to most California Installations 1976 or later, most western states installations postdating 1982 and most U.S installations postdating 1998. | Costing per elevator. Elevator demand parameter shall be defined as the peak floor acceleration at the first floor. The elevator fragility for a multiple story building should only be entered once on the first floor. | Any | Any | Each | Each | Peak Floor Acceleration | g | 4 | DS1 | DS2 | DS3 | DS4 |  | Simultaneous | Simultaneous | Simultaneous | Simultaneous |  | Simul(DS1,DS2,DS3,DS4) | 417 | EA 1 | YES | BLDG | Damaged controls. | Damaged vane and hoist-way switches, and or bent cab stabilizers, and or damaged car guide shoes. | Damaged entrance and car door, and or flooring damage. | Oil leak in hydraulic line, and or hydraulic tank failure. |  | 0.3 | 0.49 | 0.44 | 0.37 |  | 0.5 | 0.5 | 0.5 | 0.5 |  | 0.28 | Not Specified | Not Specified | Not Specified |  | 0.1 | Not Specified | Not Specified | Not Specified |  | 0.3 | 0.3 | 0.3 | 0.3 |  | NO | NO | Not Rated | Not Rated | Not Rated | Not Rated | Multiple repairs possible (% change of each): Repair damaged controls (100%) | Multiple repairs possible (% change of each): Repair damaged vane and hoist-way switches (41%), and or repair bent cab stabilizers (41%), and or repair damaged car guide shoes (41%). | Multiple repairs possible (% change of each): Repair damage to doors (68%), and or repair flooring (46%) | Multiple repairs possible (% change of each): Repair oil leak in hydraulic line (27%), and or hydraulic tank failure (81%) |  | NO | NO | YES | NO |  | NO | NO | NO | NO |  | Not Applicable | Not Applicable | Not Applicable | Not Applicable |  | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 |  |  | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 |  |  | NO | NO | NO | NO |  | 0% | 0% | 0% | 0% |  | 0 | 0 | 0 | 0 |  | None | Not Given | By User | By User | Not Given | none | none | none | none |  | No | None | YES
D1014.022 | D1014.022 | Hydraulic Elevator – Applies to most California Installations prior to 1976, most western states installations prior to 1982 and most U.S installations prior to 1998. | Costing per elevator. Elevator demand parameter shall be defined as the peak floor acceleration at the first floor. The elevator fragility for a multiple story building should only be entered once on the first floor. | Any | Any | Each | Each | Peak Floor Acceleration | g | 4 | DS1 | DS2 | DS3 | DS4 |  | Simultaneous | Simultaneous | Simultaneous | Simultaneous |  | Simul(DS1,DS2,DS3,DS4) | 418 | EA 1 | YES | BLDG | Damaged controls. | Damaged vane and hoist-way switches, and or bent cab stabilizers, and or damaged car guide shoes. | Damaged entrance and car door, and or flooring damage. | Oil leak in hydraulic line, and or hydraulic tank failure. |  | 0.3 | 0.49 | 0.44 | 0.37 |  | 0.3 | 0.3 | 0.3 | 0.3 |  | 0.28 | Not Specified | Not Specified | Not Specified |  | 0.1 | Not Specified | Not Specified | Not Specified |  | 0.3 | 0.3 | 0.3 | 0.3 |  | NO | NO | Not Rated | Not Rated | Not Rated | Not Rated | Multiple repairs possible (% change of each): Repair damaged controls (100%) | Multiple repairs possible (% change of each): Repair damaged vane and hoist-way switches (41%), and or repair bent cab stabilizers (41%), and or repair damaged car guide shoes (41%). | Multiple repairs possible (% change of each): Repair damage to cab door (68%), and or repair cab flooring (46%) | Multiple repairs possible (% change of each): Repair oil leak in hydraulic line (27%), and or hydraulic tank failure (81%) |  | NO | NO | YES | NO |  | NO | NO | NO | NO |  | Not Applicable | Not Applicable | Not Applicable | Not Applicable |  | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 |  |  | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 |  |  | NO | NO | NO | NO |  | 0% | 0% | 0% | 0% |  | 0 | 0 | 0 | 0 |  | None | Not Given | By User | By User | Not Given | none | none | none | none |  | No | None | YES
D2061.023a | D2061.023a | Steam Piping - Large Diameter Welded Steel - (greater than 2.5 inches in diameter), SDC D, E, or F, PIPING FRAGILITY | Costing based upon 1000 ft segments of pipe, pipe greater than 2.5 inches in diameter | Normal | SDC D, E, F (high seismic design) | Each | Each | Peak Floor Acceleration | g | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 419 | LF 1000 | NO | NO | Minor leakage at flange connections - 1 leak per 1000 feet of pipe. | Pipe Break - 1 break per 1000 feet of pipe |  |  |  | 1 | 1 |  |  |  | 2.25 | 4.1 |  |  |  | Not Specified | Not Specified |  |  |  | Not Specified | Not Specified |  |  |  | 0.4 | 0.4 |  |  |  | NO | NO | Marginal | Superior | Marginal | Marginal | Retighten flange bolts at leaking joints, 1 joint per 1000 LF. | Replace 20 foot sections of pipe where breaks occur, one per 1000 LF. |  |  |  | NO | NO |  |  |  | NO | YES |  |  |  | Not Applicable | 10 SF |  |  |  | 0% | 0 | 5% | 0.5 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | NO |  |  |  | 0% | 0% |  |  |  | 0 | 0 |  |  |  | Consequence is for piping only. Enter floor wetting consequence seperately. Cost includes allowance for MEP relocation to perform work. | Not Given | By User | By User | Not Given | none | none |  |  |  | Yes | 2016-10-26 - Corrected consequence descriptions. | YES
D2061.023b | D2061.023b | Steam Piping - Large Diameter Welded Steel - (greater than 2.5 inches in diameter), SDC D, E, or F, BRACING FRAGILITY | Costing based upon 1000 ft segments of pipe, pipe greater than 2.5 inches in diameter | Normal | SDC D, E, F (high seismic design) | Each | Each | Peak Floor Acceleration | g | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 420 | LF 1000 | NO | NO | Lateral Brace Failure - 1 failure per 1000 feet of pipe . | Vertical Brace Failure - 1 failure per 1000 feet of pipe |  |  |  | 1 | 1 |  |  |  | 1.5 | 2.25 |  |  |  | Not Specified | Not Specified |  |  |  | Not Specified | Not Specified |  |  |  | 0.4 | 0.4 |  |  |  | NO | NO | Marginal | Superior | Marginal | Marginal | Replace failed supports, one per 1000 LF. | Replace failed supports, one per 1000 LF. |  |  |  | NO | NO |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | NO |  |  |  | 0% | 0% |  |  |  | 0 | 0 |  |  |  | Consequence is for piping only. Enter floor wetting consequence seperately. Cost includes allowance for MEP relocation to perform work. | Not Given | By User | By User | Not Given | none | none |  |  |  | Yes | 2016-10-26 - Corrected consequence descriptions. | YES
D2061.024a | D2061.024a | Steam Piping - Large Diameter Welded Steel - (greater than 2.5 inches in diameter), SDC D, E, or F (OSHPD or sim), PIPING FRAGILITY | Costing based upon 1000 ft segments of pipe, pipe greater than 2.5 inches in diameter | Special Regulation (e.g. OSHPD) for Piping Installations | SDC D, E, F (high seismic design) | Each | Each | Peak Floor Acceleration | g | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 421 | LF 1000 | NO | NO | Minor leakage at flange connections - 1 leak per 1000 feet of pipe. | Pipe Break - 1 break per 1000 feet of pipe |  |  |  | 1 | 1 |  |  |  | 2.25 | 4.1 |  |  |  | Not Specified | Not Specified |  |  |  | Not Specified | Not Specified |  |  |  | 0.4 | 0.4 |  |  |  | NO | NO | Marginal | Superior | Marginal | Marginal | Retighten flange bolts at leaking joints, 1 joint per 1000 LF. | Replace 20 foot sections of pipe where breaks occur, one per 1000 LF. |  |  |  | NO | NO |  |  |  | NO | YES |  |  |  | Not Applicable | 10 SF |  |  |  | 0% | 0 | 5% | 0.5 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | NO |  |  |  | 0% | 0% |  |  |  | 0 | 0 |  |  |  | Consequence is for piping only. Enter floor wetting consequence seperately. Cost includes allowance for MEP relocation to perform work. | Not Given | By User | By User | Not Given | none | none |  |  |  | Yes | 2016-10-26 - Corrected consequence descriptions. | YES
D2061.024b | D2061.024b | Steam Piping - Large Diameter Welded Steel - (greater than 2.5 inches in diameter), SDC D, E, or F (OSHPD or sim), BRACING FRAGILITY | Costing based upon 1000 ft segments of pipe, pipe greater than 2.5 inches in diameter | Special Regulation (e.g. OSHPD) for Piping Installations | SDC D, E, F (high seismic design) | Each | Each | Peak Floor Acceleration | g | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 422 | LF 1000 | NO | NO | Lateral Brace Failure - 1 failure per 1000 feet of pipe. | Vertical Brace Failure - 1 failure per 1000 feet of pipe |  |  |  | 1 | 1 |  |  |  | 1.5 | 2.25 |  |  |  | Not Specified | Not Specified |  |  |  | Not Specified | Not Specified |  |  |  | 0.4 | 0.4 |  |  |  | NO | NO | Marginal | Superior | Marginal | Marginal | Replace failed supports, one per 1000 LF. | Replace failed supports, one per 1000 LF. |  |  |  | NO | NO |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | NO |  |  |  | 0% | 0% |  |  |  | 0 | 0 |  |  |  | Consequence is for piping only. Enter floor wetting consequence seperately. Cost includes allowance for MEP relocation to perform work. | Not Given | By User | By User | Not Given | none | none |  |  |  | Yes | 2016-10-26 - Corrected consequence descriptions. | YES
D3031.011a | D3031.011a | Chiller - Capacity: < 100 Ton - Unanchored equipment that is not vibration isolated - Equipment fragility only | Costing is per unit and is based upon 75 Ton. | Normal - Not designed for seismic loads | Unanchored equipment that is not vibration isolated | Each | Each | Peak Floor Acceleration | g | 1 | DS1 |  |  |  |  | Sequential |  |  |  |  | Seq(DS1) | 423 | TN 75 | YES | BLDG | Damaged, inoperative. |  |  |  |  | 1 |  |  |  |  | 0.2 |  |  |  |  | 0.4 |  |  |  |  | 0.1 |  |  |  |  | 0.4 |  |  |  |  | NO | NO | Average | Average | Superior | Superior | Repair chiller and attached piping. Chiller removed, repaired offsite, and reinstalled. |  |  |  |  | NO |  |  |  |  | NO |  |  |  |  | Not Applicable |  |  |  |  | 0% | 0 | [8 empty] | 0% | 0 | [8 empty] | NO |  |  |  |  | 0% |  |  |  |  | 0 |  |  |  |  | None | Not Given | By User | By User | Not Given | none |  |  |  |  | No | 2016-10-25 - Repair method clarified. | YES
D3031.011b | D3031.011b | Chiller - Capacity: 100 to <350 Ton - Unanchored equipment that is not vibration isolated - Equipment fragility only | Costing is per unit and is based upon 250 Ton. | Normal - Not designed for seismic loads | Unanchored equipment that is not vibration isolated | Each | Each | Peak Floor Acceleration | g | 1 | DS1 |  |  |  |  | Sequential |  |  |  |  | Seq(DS1) | 424 | TN 250 | YES | BLDG | Damaged, inoperative. |  |  |  |  | 1 |  |  |  |  | 0.2 |  |  |  |  | 0.4 |  |  |  |  | 0.1 |  |  |  |  | 0.4 |  |  |  |  | NO | NO | Average | Average | Superior | Superior | Repair chiller and attached piping. Chiller removed, repaired offsite, and reinstalled. |  |  |  |  | YES |  |  |  |  | NO |  |  |  |  | Not Applicable |  |  |  |  | 0% | 0 | [8 empty] | 0% | 0 | [8 empty] | NO |  |  |  |  | 0% |  |  |  |  | 0 |  |  |  |  | None | Not Given | By User | By User | Not Given | none |  |  |  |  | No | 2016-10-25 - Repair method clarified. | YES
D3031.011c | D3031.011c | Chiller - Capacity: 350 to <750 Ton - Unanchored equipment that is not vibration isolated - Equipment fragility only | Costing is per unit and is based upon 500 Ton. | Normal - Not designed for seismic loads | Unanchored equipment that is not vibration isolated | Each | Each | Peak Floor Acceleration | g | 1 | DS1 |  |  |  |  | Sequential |  |  |  |  | Seq(DS1) | 425 | TN 500 | YES | BLDG | Damaged, inoperative. |  |  |  |  | 1 |  |  |  |  | 0.2 |  |  |  |  | 0.4 |  |  |  |  | 0.1 |  |  |  |  | 0.4 |  |  |  |  | NO | NO | Average | Average | Superior | Superior | Repair chiller and attached piping. Chiller removed, repaired offsite, and reinstalled. |  |  |  |  | YES |  |  |  |  | NO |  |  |  |  | Not Applicable |  |  |  |  | 0% | 0 | [8 empty] | 0% | 0 | [8 empty] | NO |  |  |  |  | 0% |  |  |  |  | 0 |  |  |  |  | None | Not Given | By User | By User | Not Given | none |  |  |  |  | No | 2016-10-25 - Repair method clarified. | YES
D3031.011d | D3031.011d | Chiller - Capacity: 750 to <1000 Ton - Unanchored equipment that is not vibration isolated - Equipment fragility only | Costing is per unit and is based upon 850 Ton. | Normal - Not designed for seismic loads | Unanchored equipment that is not vibration isolated | Each | Each | Peak Floor Acceleration | g | 1 | DS1 |  |  |  |  | Sequential |  |  |  |  | Seq(DS1) | 426 | TN 850 | YES | BLDG | Damaged, inoperative. |  |  |  |  | 1 |  |  |  |  | 0.2 |  |  |  |  | 0.4 |  |  |  |  | 0.1 |  |  |  |  | 0.4 |  |  |  |  | NO | NO | Average | Average | Superior | Superior | Repair chiller and attached piping. Chiller removed, repaired offsite, and reinstalled. |  |  |  |  | YES |  |  |  |  | NO |  |  |  |  | Not Applicable |  |  |  |  | 0% | 0 | [8 empty] | 0% | 0 | [8 empty] | NO |  |  |  |  | 0% |  |  |  |  | 0 |  |  |  |  | None | Not Given | By User | By User | Not Given | none |  |  |  |  | No | 2016-10-25 - Repair method clarified. | YES
D3031.012a | D3031.012a | Chiller - Capacity: < 100 Ton - Vibration isolated equipment that is not snubbed or restrained - Anchorage fragility only | Costing is per unit and is based upon 75 Ton. | Normal - Not designed for seismic loads | Vibration isolated equipment that is not snubbed or restrained | Each | Each | Peak Floor Acceleration | g | 2 | DS1 | DS2 |  |  |  | Mutually Exclusive | Mutually Exclusive |  |  |  | MutEx(DS1,DS2) | 427 | TN 75 | YES | BLDG | Anchorage failure. | Anchorage failure & Equipment damaged beyond repair. |  |  |  | 0.7 | 0.3 |  |  |  | By User | By User |  |  |  | User to Calculate | User to Calculate |  |  |  | User to Calculate | User to Calculate |  |  |  | By User | By User |  |  |  | NO | NO | Average | Average | Superior | Superior | Repair anchorage and concrete pad and remount equipment. | Replace equipment including attached utilities in addition to repairing anchorage and concrete pad. Chiller removed, repaired offsite, and reinstalled. |  |  |  | NO | YES |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | NO |  |  |  | 0% | 0% |  |  |  | 0 | 0 |  |  |  | User to provide median demand and dispersion values. The values listed are default PACT values and do not represent the response of this component. | Not Given | By User | By User | Not Given | none | none |  |  |  | No | 2016-10-25 - Repair method clarified. | YES
D3031.012b | D3031.012b | Chiller - Capacity: < 100 Ton - Vibration isolated equipment that is not snubbed or restrained - Equipment fragility only | Costing is per unit and is based upon 75 Ton. | Normal - Not designed for seismic loads | Vibration isolated equipment that is not snubbed or restrained | Each | Each | Peak Floor Acceleration | g | 1 | DS1 |  |  |  |  | Sequential |  |  |  |  | Seq(DS1) | 428 | TN 75 | YES | BLDG | Damaged, inoperative but anchorage is OK. |  |  |  |  | 1 |  |  |  |  | 0.43 |  |  |  |  | 0.6 |  |  |  |  | 0.1 |  |  |  |  | 0.6 |  |  |  |  | NO | NO | Average | Average | Superior | Superior | Repair chiller and attached piping. Chiller removed, repaired offsite, and reinstalled. |  |  |  |  | NO |  |  |  |  | NO |  |  |  |  | Not Applicable |  |  |  |  | 0% | 0 | [8 empty] | 0% | 0 | [8 empty] | NO |  |  |  |  | 0% |  |  |  |  | 0 |  |  |  |  | None | Not Given | By User | By User | Not Given | none |  |  |  |  | No | 2016-10-25 - Repair method clarified. | YES
D3031.012c | D3031.012c | Chiller - Capacity: < 100 Ton - Vibration isolated equipment that is not snubbed or restrained - Combined anchorage/isolator & equipment fragility | Costing is per unit and is based upon 75 Ton. | Normal - Not designed for seismic loads | Vibration isolated equipment that is not snubbed or restrained | Each | Each | Peak Floor Acceleration | g | 3 | DS1 | DS2 | DS3 |  |  | Mutually Exclusive | Mutually Exclusive | Mutually Exclusive |  |  | MutEx(DS1,DS2,DS3) | 429 | TN 75 | YES | BLDG | Anchorage failure. | Anchorage failure & Equipment damaged beyond repair. | Damaged, Inoperative but anchorage is OK. |  |  | 0.35 | 0.15 | 0.5 |  |  | By User | By User | By User |  |  | User to Calculate | User to Calculate | User to Calculate |  |  | User to Calculate | User to Calculate | User to Calculate |  |  | By User | By User | By User |  |  | NO | NO | Average | Average | Superior | Superior | Repair anchorage and concrete pad and remount equipment. | Replace equipment including attached utilities in addition to repairing anchorage and concrete pad. Chiller removed, repaired offsite, and reinstalled. | Repair chiller and attached piping. Chiller removed, repaired offsite, and reinstalled. |  |  | NO | YES | NO |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | NO | NO |  |  | 0% | 0% | 0% |  |  | 0 | 0 | 0 |  |  | User to provide median demand and dispersion values. The values listed are default PACT values and do not represent the response of this component. | Not Given | By User | By User | Not Given | none | none | none |  |  | No | 2016-10-25 - Repair method clarified. | YES
D3031.012d | D3031.012d | Chiller - Capacity: 100 to <350 Ton - Vibration isolated equipment that is not snubbed or restrained - Anchorage fragility only | Costing is per unit and is based upon 250 Ton. | Normal - Not designed for seismic loads | Vibration isolated equipment that is not snubbed or restrained | Each | Each | Peak Floor Acceleration | g | 2 | DS1 | DS2 |  |  |  | Mutually Exclusive | Mutually Exclusive |  |  |  | MutEx(DS1,DS2) | 430 | TN 250 | YES | BLDG | Anchorage failure. | Anchorage failure & Equipment damaged beyond repair. |  |  |  | 0.7 | 0.3 |  |  |  | By User | By User |  |  |  | User to Calculate | User to Calculate |  |  |  | User to Calculate | User to Calculate |  |  |  | By User | By User |  |  |  | NO | NO | Average | Average | Superior | Superior | Repair anchorage and concrete pad and remount equipment. | Replace equipment including attached utilities in addition to repairing anchorage and concrete pad. Chiller removed, repaired offsite, and reinstalled. |  |  |  | YES | YES |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | NO |  |  |  | 0% | 0% |  |  |  | 0 | 0 |  |  |  | User to provide median demand and dispersion values. The values listed are default PACT values and do not represent the response of this component. | Not Given | By User | By User | Not Given | none | none |  |  |  | No | 2016-10-25 - Repair method clarified. | YES
D3031.012e | D3031.012e | Chiller - Capacity: 100 to <350 Ton - Vibration isolated equipment that is not snubbed or restrained - Equipment fragility only | Costing is per unit and is based upon 250 Ton. | Normal - Not designed for seismic loads | Vibration isolated equipment that is not snubbed or restrained | Each | Each | Peak Floor Acceleration | g | 1 | DS1 |  |  |  |  | Sequential |  |  |  |  | Seq(DS1) | 431 | TN 250 | YES | BLDG | Damaged, inoperative but anchorage is OK. |  |  |  |  | 1 |  |  |  |  | 0.43 |  |  |  |  | 0.6 |  |  |  |  | 0.1 |  |  |  |  | 0.6 |  |  |  |  | NO | NO | Average | Average | Superior | Superior | Repair chiller and attached piping. Chiller removed, repaired offsite, and reinstalled. |  |  |  |  | YES |  |  |  |  | NO |  |  |  |  | Not Applicable |  |  |  |  | 0% | 0 | [8 empty] | 0% | 0 | [8 empty] | NO |  |  |  |  | 0% |  |  |  |  | 0 |  |  |  |  | None | Not Given | By User | By User | Not Given | none |  |  |  |  | No | 2016-10-25 - Repair method clarified. | YES
D3031.012f | D3031.012f | Chiller - Capacity: 100 to <350 Ton - Vibration isolated equipment that is not snubbed or restrained - Combined anchorage/isolator & equipment fragility | Costing is per unit and is based upon 250 Ton. | Normal - Not designed for seismic loads | Vibration isolated equipment that is not snubbed or restrained | Each | Each | Peak Floor Acceleration | g | 3 | DS1 | DS2 | DS3 |  |  | Mutually Exclusive | Mutually Exclusive | Mutually Exclusive |  |  | MutEx(DS1,DS2,DS3) | 432 | TN 250 | YES | BLDG | Anchorage failure. | Anchorage failure & Equipment damaged beyond repair. | Damaged, Inoperative but anchorage is OK. |  |  | 0.35 | 0.15 | 0.5 |  |  | By User | By User | By User |  |  | User to Calculate | User to Calculate | User to Calculate |  |  | User to Calculate | User to Calculate | User to Calculate |  |  | By User | By User | By User |  |  | NO | NO | Average | Average | Superior | Superior | Repair anchorage and concrete pad and remount equipment. | Replace equipment including attached utilities in addition to repairing anchorage and concrete pad. Chiller removed, repaired offsite, and reinstalled. | Repair chiller and attached piping. Chiller removed, repaired offsite, and reinstalled. |  |  | YES | YES | YES |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | NO | NO |  |  | 0% | 0% | 0% |  |  | 0 | 0 | 0 |  |  | User to provide median demand and dispersion values. The values listed are default PACT values and do not represent the response of this component. | Not Given | By User | By User | Not Given | none | none | none |  |  | No | 2016-10-25 - Repair method clarified. | YES
D3031.012g | D3031.012g | Chiller - Capacity: 350 to <750 Ton - Vibration isolated equipment that is not snubbed or restrained - Anchorage fragility only | Costing is per unit and is based upon 500 Ton. | Normal - Not designed for seismic loads | Vibration isolated equipment that is not snubbed or restrained | Each | Each | Peak Floor Acceleration | g | 2 | DS1 | DS2 |  |  |  | Mutually Exclusive | Mutually Exclusive |  |  |  | MutEx(DS1,DS2) | 433 | TN 500 | YES | BLDG | Anchorage failure. | Anchorage failure & Equipment damaged beyond repair. |  |  |  | 0.7 | 0.3 |  |  |  | By User | By User |  |  |  | User to Calculate | User to Calculate |  |  |  | User to Calculate | User to Calculate |  |  |  | By User | By User |  |  |  | NO | NO | Average | Average | Superior | Superior | Repair anchorage and concrete pad and remount equipment. | Replace equipment including attached utilities in addition to repairing anchorage and concrete pad. Chiller removed, repaired offsite, and reinstalled. |  |  |  | YES | YES |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | NO |  |  |  | 0% | 0% |  |  |  | 0 | 0 |  |  |  | User to provide median demand and dispersion values. The values listed are default PACT values and do not represent the response of this component. | Not Given | By User | By User | Not Given | none | none |  |  |  | No | 2016-10-25 - Repair method clarified. | YES
D3031.012h | D3031.012h | Chiller - Capacity: 350 to <750 Ton - Vibration isolated equipment that is not snubbed or restrained - Equipment fragility only | Costing is per unit and is based upon 500 Ton. | Normal - Not designed for seismic loads | Vibration isolated equipment that is not snubbed or restrained | Each | Each | Peak Floor Acceleration | g | 1 | DS1 |  |  |  |  | Sequential |  |  |  |  | Seq(DS1) | 434 | TN 500 | YES | BLDG | Damaged, inoperative but anchorage is OK. |  |  |  |  | 1 |  |  |  |  | 0.43 |  |  |  |  | 0.6 |  |  |  |  | 0.1 |  |  |  |  | 0.6 |  |  |  |  | NO | NO | Average | Average | Superior | Superior | Repair chiller and attached piping. Chiller removed, repaired offsite, and reinstalled. |  |  |  |  | YES |  |  |  |  | NO |  |  |  |  | Not Applicable |  |  |  |  | 0% | 0 | [8 empty] | 0% | 0 | [8 empty] | NO |  |  |  |  | 0% |  |  |  |  | 0 |  |  |  |  | None | Not Given | By User | By User | Not Given | none |  |  |  |  | No | 2016-10-25 - Repair method clarified. | YES
D3031.012i | D3031.012i | Chiller - Capacity: 350 to <750 Ton - Vibration isolated equipment that is not snubbed or restrained - Combined anchorage/isolator & equipment fragility | Costing is per unit and is based upon 500 Ton. | Normal - Not designed for seismic loads | Vibration isolated equipment that is not snubbed or restrained | Each | Each | Peak Floor Acceleration | g | 3 | DS1 | DS2 | DS3 |  |  | Mutually Exclusive | Mutually Exclusive | Mutually Exclusive |  |  | MutEx(DS1,DS2,DS3) | 435 | TN 500 | YES | BLDG | Anchorage failure. | Anchorage failure & Equipment damaged beyond repair. | Damaged, Inoperative but anchorage is OK. |  |  | 0.35 | 0.15 | 0.5 |  |  | By User | By User | By User |  |  | User to Calculate | User to Calculate | User to Calculate |  |  | User to Calculate | User to Calculate | User to Calculate |  |  | By User | By User | By User |  |  | NO | NO | Average | Average | Superior | Superior | Repair anchorage and concrete pad and remount equipment. | Replace equipment including attached utilities in addition to repairing anchorage and concrete pad. Chiller removed, repaired offsite, and reinstalled. | Repair chiller and attached piping. Chiller removed, repaired offsite, and reinstalled. |  |  | YES | YES | YES |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | NO | NO |  |  | 0% | 0% | 0% |  |  | 0 | 0 | 0 |  |  | User to provide median demand and dispersion values. The values listed are default PACT values and do not represent the response of this component. | Not Given | By User | By User | Not Given | none | none | none |  |  | No | 2016-10-25 - Repair method clarified. | YES
D3031.012j | D3031.012j | Chiller - Capacity: 750 to <1000 Ton - Vibration isolated equipment that is not snubbed or restrained - Anchorage fragility only | Costing is per unit and is based upon 850 Ton. | Normal - Not designed for seismic loads | Vibration isolated equipment that is not snubbed or restrained | Each | Each | Peak Floor Acceleration | g | 2 | DS1 | DS2 |  |  |  | Mutually Exclusive | Mutually Exclusive |  |  |  | MutEx(DS1,DS2) | 436 | TN 850 | YES | BLDG | Anchorage failure. | Anchorage failure & Equipment damaged beyond repair. |  |  |  | 0.7 | 0.3 |  |  |  | By User | By User |  |  |  | User to Calculate | User to Calculate |  |  |  | User to Calculate | User to Calculate |  |  |  | By User | By User |  |  |  | NO | NO | Average | Average | Superior | Superior | Repair anchorage and concrete pad and remount equipment. | Replace equipment including attached utilities in addition to repairing anchorage and concrete pad. Chiller removed, repaired offsite, and reinstalled. |  |  |  | YES | YES |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | NO |  |  |  | 0% | 0% |  |  |  | 0 | 0 |  |  |  | User to provide median demand and dispersion values. The values listed are default PACT values and do not represent the response of this component. | Not Given | By User | By User | Not Given | none | none |  |  |  | No | 2016-10-25 - Repair method clarified. | YES
D3031.012k | D3031.012k | Chiller - Capacity: 750 to <1000 Ton - Vibration isolated equipment that is not snubbed or restrained - Equipment fragility only | Costing is per unit and is based upon 850 Ton. | Normal - Not designed for seismic loads | Vibration isolated equipment that is not snubbed or restrained | Each | Each | Peak Floor Acceleration | g | 1 | DS1 |  |  |  |  | Sequential |  |  |  |  | Seq(DS1) | 437 | TN 850 | YES | BLDG | Damaged, inoperative but anchorage is OK. |  |  |  |  | 1 |  |  |  |  | 0.43 |  |  |  |  | 0.6 |  |  |  |  | 0.1 |  |  |  |  | 0.6 |  |  |  |  | NO | NO | Average | Average | Superior | Superior | Repair chiller and attached piping. Chiller removed, repaired offsite, and reinstalled. |  |  |  |  | YES |  |  |  |  | NO |  |  |  |  | Not Applicable |  |  |  |  | 0% | 0 | [8 empty] | 0% | 0 | [8 empty] | NO |  |  |  |  | 0% |  |  |  |  | 0 |  |  |  |  | None | Not Given | By User | By User | Not Given | none |  |  |  |  | No | 2016-10-25 - Repair method clarified. | YES
D3031.012l | D3031.012l | Chiller - Capacity: 750 to <1000 Ton - Vibration isolated equipment that is not snubbed or restrained - Combined anchorage/isolator & equipment fragility | Costing is per unit and is based upon 850 Ton. | Normal - Not designed for seismic loads | Vibration isolated equipment that is not snubbed or restrained | Each | Each | Peak Floor Acceleration | g | 3 | DS1 | DS2 | DS3 |  |  | Mutually Exclusive | Mutually Exclusive | Mutually Exclusive |  |  | MutEx(DS1,DS2,DS3) | 438 | TN 850 | YES | BLDG | Anchorage failure. | Anchorage failure & Equipment damaged beyond repair. | Damaged, Inoperative but anchorage is OK. |  |  | 0.35 | 0.15 | 0.5 |  |  | By User | By User | By User |  |  | User to Calculate | User to Calculate | User to Calculate |  |  | User to Calculate | User to Calculate | User to Calculate |  |  | By User | By User | By User |  |  | NO | NO | Average | Average | Superior | Superior | Repair anchorage and concrete pad and remount equipment. | Replace equipment including attached utilities in addition to repairing anchorage and concrete pad. Chiller removed, repaired offsite, and reinstalled. | Repair chiller and attached piping. Chiller removed, repaired offsite, and reinstalled. |  |  | YES | YES | YES |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | NO | NO |  |  | 0% | 0% | 0% |  |  | 0 | 0 | 0 |  |  | User to provide median demand and dispersion values. The values listed are default PACT values and do not represent the response of this component. | Not Given | By User | By User | Not Given | none | none | none |  |  | No | 2016-10-25 - Repair method clarified. | YES
D3031.013a | D3031.013a | Chiller - Capacity: < 100 Ton - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only | Costing is per unit and is based upon 75 Ton. | Normal - Designed for seismic loads but no special seismic certification | Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints | Each | Each | Peak Floor Acceleration | g | 2 | DS1 | DS2 |  |  |  | Mutually Exclusive | Mutually Exclusive |  |  |  | MutEx(DS1,DS2) | 439 | TN 75 | YES | BLDG | Anchorage failure. | Anchorage failure & Equipment damaged beyond repair. |  |  |  | 0.7 | 0.3 |  |  |  | By User | By User |  |  |  | User to Calculate | User to Calculate |  |  |  | User to Calculate | User to Calculate |  |  |  | By User | By User |  |  |  | NO | NO | Average | Average | Superior | Superior | Repair anchorage and concrete pad and remount equipment. | Replace equipment including attached utilities in addition to repairing anchorage and concrete pad. Chiller removed, repaired offsite, and reinstalled. |  |  |  | NO | YES |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | NO |  |  |  | 0% | 0% |  |  |  | 0 | 0 |  |  |  | User to provide median demand and dispersion values. The values listed are default PACT values and do not represent the response of this component. | Not Given | By User | By User | Not Given | D3031.013a-DS1-1.JPG | none |  |  |  | No | 2016-10-25 - Repair method clarified. | YES
D3031.013b | D3031.013b | Chiller - Capacity: < 100 Ton - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only | Costing is per unit and is based upon 75 Ton. | Normal - Designed for seismic loads but no special seismic certification | Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints | Each | Each | Peak Floor Acceleration | g | 1 | DS1 |  |  |  |  | Sequential |  |  |  |  | Seq(DS1) | 440 | TN 75 | YES | BLDG | Damaged, inoperative but anchorage is OK. |  |  |  |  | 1 |  |  |  |  | 0.72 |  |  |  |  | 0.2 |  |  |  |  | 0.1 |  |  |  |  | 0.2 |  |  |  |  | NO | NO | Average | Average | Superior | Superior | Repair chiller and attached piping. Chiller removed, repaired offsite, and reinstalled. |  |  |  |  | NO |  |  |  |  | NO |  |  |  |  | Not Applicable |  |  |  |  | 0% | 0 | [8 empty] | 0% | 0 | [8 empty] | NO |  |  |  |  | 0% |  |  |  |  | 0 |  |  |  |  | None | Not Given | By User | By User | Not Given | D3031.013a-DS1-1.JPG |  |  |  |  | No | 2016-10-25 - Repair method clarified. | YES
D3031.013c | D3031.013c | Chiller - Capacity: < 100 Ton - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | Costing is per unit and is based upon 75 Ton. | Normal - Designed for seismic loads but no special seismic certification | Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints | Each | Each | Peak Floor Acceleration | g | 3 | DS1 | DS2 | DS3 |  |  | Mutually Exclusive | Mutually Exclusive | Mutually Exclusive |  |  | MutEx(DS1,DS2,DS3) | 441 | TN 75 | YES | BLDG | Anchorage failure. | Anchorage failure & Equipment damaged beyond repair. | Damaged, Inoperative but anchorage is OK. |  |  | 0.35 | 0.15 | 0.5 |  |  | By User | By User | By User |  |  | User to Calculate | User to Calculate | User to Calculate |  |  | User to Calculate | User to Calculate | User to Calculate |  |  | By User | By User | By User |  |  | NO | NO | Average | Average | Superior | Superior | Repair anchorage and concrete pad and remount equipment. | Replace equipment including attached utilities in addition to repairing anchorage and concrete pad. Chiller removed, repaired offsite, and reinstalled. | Repair chiller and attached piping. Chiller removed, repaired offsite, and reinstalled. |  |  | NO | YES | NO |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | NO | NO |  |  | 0% | 0% | 0% |  |  | 0 | 0 | 0 |  |  | User to provide median demand and dispersion values. The values listed are default PACT values and do not represent the response of this component. | Not Given | By User | By User | Not Given | D3031.013a-DS1-1.JPG | none | none |  |  | No | 2016-10-25 - Repair method clarified. | YES
D3031.013d | D3031.013d | Chiller - Capacity: 100 to <350 Ton - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only | Costing is per unit and is based upon 250 Ton. | Normal - Designed for seismic loads but no special seismic certification | Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints | Each | Each | Peak Floor Acceleration | g | 2 | DS1 | DS2 |  |  |  | Mutually Exclusive | Mutually Exclusive |  |  |  | MutEx(DS1,DS2) | 442 | TN 250 | YES | BLDG | Anchorage failure. | Anchorage failure & Equipment damaged beyond repair. |  |  |  | 0.7 | 0.3 |  |  |  | By User | By User |  |  |  | User to Calculate | User to Calculate |  |  |  | User to Calculate | User to Calculate |  |  |  | By User | By User |  |  |  | NO | NO | Average | Average | Superior | Superior | Repair anchorage and concrete pad and remount equipment. | Replace equipment including attached utilities in addition to repairing anchorage and concrete pad. Chiller removed, repaired offsite, and reinstalled. |  |  |  | YES | YES |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | NO |  |  |  | 0% | 0% |  |  |  | 0 | 0 |  |  |  | User to provide median demand and dispersion values. The values listed are default PACT values and do not represent the response of this component. | Not Given | By User | By User | Not Given | D3031.013a-DS1-1.JPG | none |  |  |  | No | 2016-10-25 - Repair method clarified. | YES
D3031.013e | D3031.013e | Chiller - Capacity: 100 to <350 Ton - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only | Costing is per unit and is based upon 250 Ton. | Normal - Designed for seismic loads but no special seismic certification | Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints | Each | Each | Peak Floor Acceleration | g | 1 | DS1 |  |  |  |  | Sequential |  |  |  |  | Seq(DS1) | 443 | TN 250 | YES | BLDG | Damaged, inoperative but anchorage is OK. |  |  |  |  | 1 |  |  |  |  | 0.72 |  |  |  |  | 0.2 |  |  |  |  | 0.1 |  |  |  |  | 0.2 |  |  |  |  | NO | NO | Average | Average | Superior | Superior | Repair chiller and attached piping. Chiller removed, repaired offsite, and reinstalled. |  |  |  |  | YES |  |  |  |  | NO |  |  |  |  | Not Applicable |  |  |  |  | 0% | 0 | [8 empty] | 0% | 0 | [8 empty] | NO |  |  |  |  | 0% |  |  |  |  | 0 |  |  |  |  | None | Not Given | By User | By User | Not Given | D3031.013a-DS1-1.JPG |  |  |  |  | No | 2016-10-25 - Repair method clarified. | YES
D3031.013f | D3031.013f | Chiller - Capacity: 100 to <350 Ton - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | Costing is per unit and is based upon 250 Ton. | Normal - Designed for seismic loads but no special seismic certification | Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints | Each | Each | Peak Floor Acceleration | g | 3 | DS1 | DS2 | DS3 |  |  | Mutually Exclusive | Mutually Exclusive | Mutually Exclusive |  |  | MutEx(DS1,DS2,DS3) | 444 | TN 250 | YES | BLDG | Anchorage failure. | Anchorage failure & Equipment damaged beyond repair. | Damaged, Inoperative but anchorage is OK. |  |  | 0.35 | 0.15 | 0.5 |  |  | By User | By User | By User |  |  | User to Calculate | User to Calculate | User to Calculate |  |  | User to Calculate | User to Calculate | User to Calculate |  |  | By User | By User | By User |  |  | NO | NO | Average | Average | Superior | Superior | Repair anchorage and concrete pad and remount equipment. | Replace equipment including attached utilities in addition to repairing anchorage and concrete pad. Chiller removed, repaired offsite, and reinstalled. | Repair chiller and attached piping. Chiller removed, repaired offsite, and reinstalled. |  |  | YES | YES | YES |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | NO | NO |  |  | 0% | 0% | 0% |  |  | 0 | 0 | 0 |  |  | User to provide median demand and dispersion values. The values listed are default PACT values and do not represent the response of this component. | Not Given | By User | By User | Not Given | D3031.013a-DS1-1.JPG | none | none |  |  | No | 2016-10-25 - Repair method clarified. | YES
D3031.013g | D3031.013g | Chiller - Capacity: 350 to <750 Ton - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only | Costing is per unit and is based upon 500 Ton. | Normal - Designed for seismic loads but no special seismic certification | Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints | Each | Each | Peak Floor Acceleration | g | 2 | DS1 | DS2 |  |  |  | Mutually Exclusive | Mutually Exclusive |  |  |  | MutEx(DS1,DS2) | 445 | TN 500 | YES | BLDG | Anchorage failure. | Anchorage failure & Equipment damaged beyond repair. |  |  |  | 0.7 | 0.3 |  |  |  | By User | By User |  |  |  | User to Calculate | User to Calculate |  |  |  | User to Calculate | User to Calculate |  |  |  | By User | By User |  |  |  | NO | NO | Average | Average | Superior | Superior | Repair anchorage and concrete pad and remount equipment. | Replace equipment including attached utilities in addition to repairing anchorage and concrete pad. Chiller removed, repaired offsite, and reinstalled. |  |  |  | YES | YES |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | NO |  |  |  | 0% | 0% |  |  |  | 0 | 0 |  |  |  | User to provide median demand and dispersion values. The values listed are default PACT values and do not represent the response of this component. | Not Given | By User | By User | Not Given | D3031.013a-DS1-1.JPG | none |  |  |  | No | 2016-10-25 - Repair method clarified. | YES
D3031.013h | D3031.013h | Chiller - Capacity: 350 to <750 Ton - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only | Costing is per unit and is based upon 500 Ton. | Normal - Designed for seismic loads but no special seismic certification | Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints | Each | Each | Peak Floor Acceleration | g | 1 | DS1 |  |  |  |  | Sequential |  |  |  |  | Seq(DS1) | 446 | TN 500 | YES | BLDG | Damaged, inoperative but anchorage is OK. |  |  |  |  | 1 |  |  |  |  | 0.72 |  |  |  |  | 0.2 |  |  |  |  | 0.1 |  |  |  |  | 0.2 |  |  |  |  | NO | NO | Average | Average | Superior | Superior | Repair chiller and attached piping. Chiller removed, repaired offsite, and reinstalled. |  |  |  |  | YES |  |  |  |  | NO |  |  |  |  | Not Applicable |  |  |  |  | 0% | 0 | [8 empty] | 0% | 0 | [8 empty] | NO |  |  |  |  | 0% |  |  |  |  | 0 |  |  |  |  | None | Not Given | By User | By User | Not Given | D3031.013a-DS1-1.JPG |  |  |  |  | No | 2016-10-25 - Repair method clarified. | YES
D3031.013i | D3031.013i | Chiller - Capacity: 350 to <750 Ton - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | Costing is per unit and is based upon 500 Ton. | Normal - Designed for seismic loads but no special seismic certification | Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints | Each | Each | Peak Floor Acceleration | g | 3 | DS1 | DS2 | DS3 |  |  | Mutually Exclusive | Mutually Exclusive | Mutually Exclusive |  |  | MutEx(DS1,DS2,DS3) | 447 | TN 500 | YES | BLDG | Anchorage failure. | Anchorage failure & Equipment damaged beyond repair. | Damaged, Inoperative but anchorage is OK. |  |  | 0.35 | 0.15 | 0.5 |  |  | By User | By User | By User |  |  | User to Calculate | User to Calculate | User to Calculate |  |  | User to Calculate | User to Calculate | User to Calculate |  |  | By User | By User | By User |  |  | NO | NO | Average | Average | Superior | Superior | Repair anchorage and concrete pad and remount equipment. | Replace equipment including attached utilities in addition to repairing anchorage and concrete pad. Chiller removed, repaired offsite, and reinstalled. | Repair chiller and attached piping. Chiller removed, repaired offsite, and reinstalled. |  |  | YES | YES | YES |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | NO | NO |  |  | 0% | 0% | 0% |  |  | 0 | 0 | 0 |  |  | User to provide median demand and dispersion values. The values listed are default PACT values and do not represent the response of this component. | Not Given | By User | By User | Not Given | D3031.013a-DS1-1.JPG | none | none |  |  | No | 2016-10-25 - Repair method clarified. | YES
D3031.013j | D3031.013j | Chiller - Capacity: 750 to <1000 Ton - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only | Costing is per unit and is based upon 850 Ton. | Normal - Designed for seismic loads but no special seismic certification | Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints | Each | Each | Peak Floor Acceleration | g | 2 | DS1 | DS2 |  |  |  | Mutually Exclusive | Mutually Exclusive |  |  |  | MutEx(DS1,DS2) | 448 | TN 850 | YES | BLDG | Anchorage failure. | Anchorage failure & Equipment damaged beyond repair. |  |  |  | 0.7 | 0.3 |  |  |  | By User | By User |  |  |  | User to Calculate | User to Calculate |  |  |  | User to Calculate | User to Calculate |  |  |  | By User | By User |  |  |  | NO | NO | Average | Average | Superior | Superior | Repair anchorage and concrete pad and remount equipment. | Replace equipment including attached utilities in addition to repairing anchorage and concrete pad. Chiller removed, repaired offsite, and reinstalled. |  |  |  | YES | YES |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | NO |  |  |  | 0% | 0% |  |  |  | 0 | 0 |  |  |  | User to provide median demand and dispersion values. The values listed are default PACT values and do not represent the response of this component. | Not Given | By User | By User | Not Given | D3031.013a-DS1-1.JPG | none |  |  |  | No | 2016-10-25 - Repair method clarified. | YES
D3031.013k | D3031.013k | Chiller - Capacity: 750 to <1000 Ton - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only | Costing is per unit and is based upon 850 Ton. | Normal - Designed for seismic loads but no special seismic certification | Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints | Each | Each | Peak Floor Acceleration | g | 1 | DS1 |  |  |  |  | Sequential |  |  |  |  | Seq(DS1) | 449 | TN 850 | YES | BLDG | Damaged, inoperative but anchorage is OK. |  |  |  |  | 1 |  |  |  |  | 0.72 |  |  |  |  | 0.2 |  |  |  |  | 0.1 |  |  |  |  | 0.2 |  |  |  |  | NO | NO | Average | Average | Superior | Superior | Repair chiller and attached piping. Chiller removed, repaired offsite, and reinstalled. |  |  |  |  | YES |  |  |  |  | NO |  |  |  |  | Not Applicable |  |  |  |  | 0% | 0 | [8 empty] | 0% | 0 | [8 empty] | NO |  |  |  |  | 0% |  |  |  |  | 0 |  |  |  |  | None | Not Given | By User | By User | Not Given | D3031.013a-DS1-1.JPG |  |  |  |  | No | 2016-10-25 - Repair method clarified. | YES
D3031.013l | D3031.013l | Chiller - Capacity: 750 to <1000 Ton - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | Costing is per unit and is based upon 850 Ton. | Normal - Designed for seismic loads but no special seismic certification | Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints | Each | Each | Peak Floor Acceleration | g | 3 | DS1 | DS2 | DS3 |  |  | Mutually Exclusive | Mutually Exclusive | Mutually Exclusive |  |  | MutEx(DS1,DS2,DS3) | 450 | TN 850 | YES | BLDG | Anchorage failure. | Anchorage failure & Equipment damaged beyond repair. | Damaged, Inoperative but anchorage is OK. |  |  | 0.35 | 0.15 | 0.5 |  |  | By User | By User | By User |  |  | User to Calculate | User to Calculate | User to Calculate |  |  | User to Calculate | User to Calculate | User to Calculate |  |  | By User | By User | By User |  |  | NO | NO | Average | Average | Superior | Superior | Repair anchorage and concrete pad and remount equipment. | Replace equipment including attached utilities in addition to repairing anchorage and concrete pad. Chiller removed, repaired offsite, and reinstalled. | Repair chiller and attached piping. Chiller removed, repaired offsite, and reinstalled. |  |  | YES | YES | YES |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | NO | NO |  |  | 0% | 0% | 0% |  |  | 0 | 0 | 0 |  |  | User to provide median demand and dispersion values. The values listed are default PACT values and do not represent the response of this component. | Not Given | By User | By User | Not Given | D3031.013a-DS1-1.JPG | none | none |  |  | No | 2016-10-25 - Repair method clarified. | YES
D3031.021a | D3031.021a | Cooling Tower - Capacity: < 100 Ton - Unanchored equipment that is not vibration isolated - Equipment fragility only | Costing is per unit and is based upon 75 Ton. | Normal - Not designed for seismic loads | Unanchored equipment that is not vibration isolated | Each | Each | Peak Floor Acceleration | g | 1 | DS1 |  |  |  |  | Sequential |  |  |  |  | Seq(DS1) | 451 | TN 75 | YES | BLDG | Damaged equipment and attached piping. |  |  |  |  | 1 |  |  |  |  | 0.5 |  |  |  |  | 0.4 |  |  |  |  | 0.1 |  |  |  |  | 0.4 |  |  |  |  | NO | NO | Average | Average | Superior | Superior | Repair damaged equipment and attached piping. Cooling tower removed, repaired offsite, and reinstalled. |  |  |  |  | NO |  |  |  |  | NO |  |  |  |  | Not Applicable |  |  |  |  | 0% | 0 | [8 empty] | 0% | 0 | [8 empty] | NO |  |  |  |  | 0% |  |  |  |  | 0 |  |  |  |  | None | Not Given | By User | By User | Not Given | none |  |  |  |  | No | 2016-10-25 - Repair method clarified. | YES
D3031.021b | D3031.021b | Cooling Tower - Capacity: 100 to <350 Ton - Unanchored equipment that is not vibration isolated - Equipment fragility only | Costing is per unit and is based upon 250 Ton. | Normal - Not designed for seismic loads | Unanchored equipment that is not vibration isolated | Each | Each | Peak Floor Acceleration | g | 1 | DS1 |  |  |  |  | Sequential |  |  |  |  | Seq(DS1) | 452 | TN 250 | YES | BLDG | Damaged equipment and attached piping. |  |  |  |  | 1 |  |  |  |  | 0.5 |  |  |  |  | 0.4 |  |  |  |  | 0.1 |  |  |  |  | 0.4 |  |  |  |  | NO | NO | Average | Average | Superior | Superior | Repair damaged equipment and attached piping. Cooling tower removed, repaired offsite, and reinstalled. |  |  |  |  | YES |  |  |  |  | NO |  |  |  |  | Not Applicable |  |  |  |  | 0% | 0 | [8 empty] | 0% | 0 | [8 empty] | NO |  |  |  |  | 0% |  |  |  |  | 0 |  |  |  |  | None | Not Given | By User | By User | Not Given | none |  |  |  |  | No | 2016-10-25 - Repair method clarified. | YES
D3031.021c | D3031.021c | Cooling Tower - Capacity: 350 to <750 Ton - Unanchored equipment that is not vibration isolated - Equipment fragility only | Costing is per unit and is based upon 500 Ton. | Normal - Not designed for seismic loads | Unanchored equipment that is not vibration isolated | Each | Each | Peak Floor Acceleration | g | 1 | DS1 |  |  |  |  | Sequential |  |  |  |  | Seq(DS1) | 453 | TN 500 | YES | BLDG | Damaged equipment and attached piping. |  |  |  |  | 1 |  |  |  |  | 0.5 |  |  |  |  | 0.4 |  |  |  |  | 0.1 |  |  |  |  | 0.4 |  |  |  |  | NO | NO | Average | Average | Superior | Superior | Repair damaged equipment and attached piping. Cooling tower removed, repaired offsite, and reinstalled. |  |  |  |  | YES |  |  |  |  | NO |  |  |  |  | Not Applicable |  |  |  |  | 0% | 0 | [8 empty] | 0% | 0 | [8 empty] | NO |  |  |  |  | 0% |  |  |  |  | 0 |  |  |  |  | None | Not Given | By User | By User | Not Given | none |  |  |  |  | No | 2016-10-25 - Repair method clarified. | YES
D3031.021d | D3031.021d | Cooling Tower - Capacity: 750 to <1000 Ton - Unanchored equipment that is not vibration isolated - Equipment fragility only | Costing is per unit and is based upon 850 Ton. | Normal - Not designed for seismic loads | Unanchored equipment that is not vibration isolated | Each | Each | Peak Floor Acceleration | g | 1 | DS1 |  |  |  |  | Sequential |  |  |  |  | Seq(DS1) | 454 | TN 850 | YES | BLDG | Damaged equipment and attached piping. |  |  |  |  | 1 |  |  |  |  | 0.5 |  |  |  |  | 0.4 |  |  |  |  | 0.1 |  |  |  |  | 0.4 |  |  |  |  | NO | NO | Average | Average | Superior | Superior | Repair damaged equipment and attached piping. Cooling tower removed, repaired offsite, and reinstalled. |  |  |  |  | YES |  |  |  |  | NO |  |  |  |  | Not Applicable |  |  |  |  | 0% | 0 | [8 empty] | 0% | 0 | [8 empty] | NO |  |  |  |  | 0% |  |  |  |  | 0 |  |  |  |  | None | Not Given | By User | By User | Not Given | none |  |  |  |  | No | 2016-10-25 - Repair method clarified. | YES
D3031.022a | D3031.022a | Cooling Tower - Capacity: < 100 Ton - Vibration isolated equipment that is not snubbed or restrained - Anchorage fragility only | Costing is per unit and is based upon 75 Ton. | Normal - Not designed for seismic loads | Vibration isolated equipment that is not snubbed or restrained | Each | Each | Peak Floor Acceleration | g | 2 | DS1 | DS2 |  |  |  | Mutually Exclusive | Mutually Exclusive |  |  |  | MutEx(DS1,DS2) | 455 | TN 75 | YES | BLDG | Anchorage failure. | Anchorage failure & Equipment damaged beyond repair. |  |  |  | 0.7 | 0.3 |  |  |  | By User | By User |  |  |  | User to Calculate | User to Calculate |  |  |  | User to Calculate | User to Calculate |  |  |  | By User | By User |  |  |  | NO | NO | Average | Average | Superior | Superior | Repair anchorage and concrete pad and remount equipment. | Replace equipment including attached utilities in addition to repairing anchorage and concrete pad. Cooling tower removed, repaired offsite, and reinstalled. |  |  |  | NO | YES |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | NO |  |  |  | 0% | 0% |  |  |  | 0 | 0 |  |  |  | User to provide median demand and dispersion values. The values listed are default PACT values and do not represent the response of this component. | Not Given | By User | By User | Not Given | none | none |  |  |  | No | 2016-10-25 - Repair method clarified. | YES
D3031.022b | D3031.022b | Cooling Tower - Capacity: < 100 Ton - Vibration isolated equipment that is not snubbed or restrained - Equipment fragility only | Costing is per unit and is based upon 75 Ton. | Normal - Not designed for seismic loads | Vibration isolated equipment that is not snubbed or restrained | Each | Each | Peak Floor Acceleration | g | 1 | DS1 |  |  |  |  | Sequential |  |  |  |  | Seq(DS1) | 456 | TN 75 | YES | BLDG | Damaged equipment and attached piping but anchorage is OK. |  |  |  |  | 1 |  |  |  |  | 0.97 |  |  |  |  | 0.6 |  |  |  |  | 0.1 |  |  |  |  | 0.6 |  |  |  |  | NO | NO | Average | Average | Superior | Superior | Repair damaged equipment and attached piping. Cooling tower removed, repaired offsite, and reinstalled. |  |  |  |  | NO |  |  |  |  | NO |  |  |  |  | Not Applicable |  |  |  |  | 0% | 0 | [8 empty] | 0% | 0 | [8 empty] | NO |  |  |  |  | 0% |  |  |  |  | 0 |  |  |  |  | None | Not Given | By User | By User | Not Given | none |  |  |  |  | No | 2016-10-25 - Repair method clarified. | YES
D3031.022c | D3031.022c | Cooling Tower - Capacity: < 100 Ton - Vibration isolated equipment that is not snubbed or restrained - Combined anchorage/isolator & equipment fragility | Costing is per unit and is based upon 75 Ton. | Normal - Not designed for seismic loads | Vibration isolated equipment that is not snubbed or restrained | Each | Each | Peak Floor Acceleration | g | 3 | DS1 | DS2 | DS3 |  |  | Mutually Exclusive | Mutually Exclusive | Mutually Exclusive |  |  | MutEx(DS1,DS2,DS3) | 457 | TN 75 | YES | BLDG | Anchorage failure. | Anchorage failure & Equipment damaged beyond repair. | Damaged equipment and attached piping but anchorage OK. |  |  | 0.35 | 0.15 | 0.5 |  |  | By User | By User | By User |  |  | User to Calculate | User to Calculate | User to Calculate |  |  | User to Calculate | User to Calculate | User to Calculate |  |  | By User | By User | By User |  |  | NO | NO | Average | Average | Superior | Superior | Repair anchorage and concrete pad and remount equipment. | Replace equipment including attached utilities in addition to repairing anchorage and concrete pad. Cooling tower removed, repaired offsite, and reinstalled. | Repair damaged equipment and attached piping. Cooling tower removed, repaired offsite, and reinstalled. |  |  | NO | YES | NO |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | NO | NO |  |  | 0% | 0% | 0% |  |  | 0 | 0 | 0 |  |  | User to provide median demand and dispersion values. The values listed are default PACT values and do not represent the response of this component. | Not Given | By User | By User | Not Given | none | none | none |  |  | No | 2016-10-25 - Repair method clarified. | YES
D3031.022d | D3031.022d | Cooling Tower - Capacity: 100 to <350 Ton - Vibration isolated equipment that is not snubbed or restrained - Anchorage fragility only | Costing is per unit and is based upon 250 Ton. | Normal - Not designed for seismic loads | Vibration isolated equipment that is not snubbed or restrained | Each | Each | Peak Floor Acceleration | g | 2 | DS1 | DS2 |  |  |  | Mutually Exclusive | Mutually Exclusive |  |  |  | MutEx(DS1,DS2) | 458 | TN 250 | YES | BLDG | Anchorage failure. | Anchorage failure & Equipment damaged beyond repair. |  |  |  | 0.7 | 0.3 |  |  |  | By User | By User |  |  |  | User to Calculate | User to Calculate |  |  |  | User to Calculate | User to Calculate |  |  |  | By User | By User |  |  |  | NO | NO | Average | Average | Superior | Superior | Repair anchorage and concrete pad and remount equipment. | Replace equipment including attached utilities in addition to repairing anchorage and concrete pad. Cooling tower removed, repaired offsite, and reinstalled. |  |  |  | YES | YES |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | NO |  |  |  | 0% | 0% |  |  |  | 0 | 0 |  |  |  | User to provide median demand and dispersion values. The values listed are default PACT values and do not represent the response of this component. | Not Given | By User | By User | Not Given | none | none |  |  |  | No | 2016-10-25 - Repair method clarified. | YES
D3031.022e | D3031.022e | Cooling Tower - Capacity: 100 to <350 Ton - Vibration isolated equipment that is not snubbed or restrained - Equipment fragility only | Costing is per unit and is based upon 250 Ton. | Normal - Not designed for seismic loads | Vibration isolated equipment that is not snubbed or restrained | Each | Each | Peak Floor Acceleration | g | 1 | DS1 |  |  |  |  | Sequential |  |  |  |  | Seq(DS1) | 459 | TN 250 | YES | BLDG | Damaged equipment and attached piping but anchorage is OK. |  |  |  |  | 1 |  |  |  |  | 0.97 |  |  |  |  | 0.6 |  |  |  |  | 0.1 |  |  |  |  | 0.6 |  |  |  |  | NO | NO | Average | Average | Superior | Superior | Repair damaged equipment and attached piping. Cooling tower removed, repaired offsite, and reinstalled. |  |  |  |  | YES |  |  |  |  | NO |  |  |  |  | Not Applicable |  |  |  |  | 0% | 0 | [8 empty] | 0% | 0 | [8 empty] | NO |  |  |  |  | 0% |  |  |  |  | 0 |  |  |  |  | None | Not Given | By User | By User | Not Given | none |  |  |  |  | No | 2016-10-25 - Repair method clarified. | YES
D3031.022f | D3031.022f | Cooling Tower - Capacity: 100 to <350 Ton - Vibration isolated equipment that is not snubbed or restrained - Combined anchorage/isolator & equipment fragility | Costing is per unit and is based upon 250 Ton. | Normal - Not designed for seismic loads | Vibration isolated equipment that is not snubbed or restrained | Each | Each | Peak Floor Acceleration | g | 3 | DS1 | DS2 | DS3 |  |  | Mutually Exclusive | Mutually Exclusive | Mutually Exclusive |  |  | MutEx(DS1,DS2,DS3) | 460 | TN 250 | YES | BLDG | Anchorage failure. | Anchorage failure & Equipment damaged beyond repair. | Damaged equipment and attached piping but anchorage OK. |  |  | 0.35 | 0.15 | 0.5 |  |  | By User | By User | By User |  |  | User to Calculate | User to Calculate | User to Calculate |  |  | User to Calculate | User to Calculate | User to Calculate |  |  | By User | By User | By User |  |  | NO | NO | Average | Average | Superior | Superior | Repair anchorage and concrete pad and remount equipment. | Replace equipment including attached utilities in addition to repairing anchorage and concrete pad. Cooling tower removed, repaired offsite, and reinstalled. | Repair damaged equipment and attached piping. Cooling tower removed, repaired offsite, and reinstalled. |  |  | YES | YES | YES |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | NO | NO |  |  | 0% | 0% | 0% |  |  | 0 | 0 | 0 |  |  | User to provide median demand and dispersion values. The values listed are default PACT values and do not represent the response of this component. | Not Given | By User | By User | Not Given | none | none | none |  |  | No | 2016-10-25 - Repair method clarified. | YES
D3031.022g | D3031.022g | Cooling Tower - Capacity: 350 to <750 Ton - Vibration isolated equipment that is not snubbed or restrained - Anchorage fragility only | Costing is per unit and is based upon 500 Ton. | Normal - Not designed for seismic loads | Vibration isolated equipment that is not snubbed or restrained | Each | Each | Peak Floor Acceleration | g | 2 | DS1 | DS2 |  |  |  | Mutually Exclusive | Mutually Exclusive |  |  |  | MutEx(DS1,DS2) | 461 | TN 500 | YES | BLDG | Anchorage failure. | Anchorage failure & Equipment damaged beyond repair. |  |  |  | 0.7 | 0.3 |  |  |  | By User | By User |  |  |  | User to Calculate | User to Calculate |  |  |  | User to Calculate | User to Calculate |  |  |  | By User | By User |  |  |  | NO | NO | Average | Average | Superior | Superior | Repair anchorage and concrete pad and remount equipment. | Replace equipment including attached utilities in addition to repairing anchorage and concrete pad. Cooling tower removed, repaired offsite, and reinstalled. |  |  |  | YES | YES |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | NO |  |  |  | 0% | 0% |  |  |  | 0 | 0 |  |  |  | User to provide median demand and dispersion values. The values listed are default PACT values and do not represent the response of this component. | Not Given | By User | By User | Not Given | none | none |  |  |  | No | 2016-10-25 - Repair method clarified. | YES
D3031.022h | D3031.022h | Cooling Tower - Capacity: 350 to <750 Ton - Vibration isolated equipment that is not snubbed or restrained - Equipment fragility only | Costing is per unit and is based upon 500 Ton. | Normal - Not designed for seismic loads | Vibration isolated equipment that is not snubbed or restrained | Each | Each | Peak Floor Acceleration | g | 1 | DS1 |  |  |  |  | Sequential |  |  |  |  | Seq(DS1) | 462 | TN 500 | YES | BLDG | Damaged equipment and attached piping but anchorage is OK. |  |  |  |  | 1 |  |  |  |  | 0.97 |  |  |  |  | 0.6 |  |  |  |  | 0.1 |  |  |  |  | 0.6 |  |  |  |  | NO | NO | Average | Average | Superior | Superior | Repair damaged equipment and attached piping. Cooling tower removed, repaired offsite, and reinstalled. |  |  |  |  | YES |  |  |  |  | NO |  |  |  |  | Not Applicable |  |  |  |  | 0% | 0 | [8 empty] | 0% | 0 | [8 empty] | NO |  |  |  |  | 0% |  |  |  |  | 0 |  |  |  |  | None | Not Given | By User | By User | Not Given | none |  |  |  |  | No | 2016-10-25 - Repair method clarified. | YES
D3031.022i | D3031.022i | Cooling Tower - Capacity: 350 to <750 Ton - Vibration isolated equipment that is not snubbed or restrained - Combined anchorage/isolator & equipment fragility | Costing is per unit and is based upon 500 Ton. | Normal - Not designed for seismic loads | Vibration isolated equipment that is not snubbed or restrained | Each | Each | Peak Floor Acceleration | g | 3 | DS1 | DS2 | DS3 |  |  | Mutually Exclusive | Mutually Exclusive | Mutually Exclusive |  |  | MutEx(DS1,DS2,DS3) | 463 | TN 500 | YES | BLDG | Anchorage failure. | Anchorage failure & Equipment damaged beyond repair. | Damaged equipment and attached piping but anchorage OK. |  |  | 0.35 | 0.15 | 0.5 |  |  | By User | By User | By User |  |  | User to Calculate | User to Calculate | User to Calculate |  |  | User to Calculate | User to Calculate | User to Calculate |  |  | By User | By User | By User |  |  | NO | NO | Average | Average | Superior | Superior | Repair anchorage and concrete pad and remount equipment. | Replace equipment including attached utilities in addition to repairing anchorage and concrete pad. Cooling tower removed, repaired offsite, and reinstalled. | Repair damaged equipment and attached piping. Cooling tower removed, repaired offsite, and reinstalled. |  |  | YES | YES | YES |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | NO | NO |  |  | 0% | 0% | 0% |  |  | 0 | 0 | 0 |  |  | User to provide median demand and dispersion values. The values listed are default PACT values and do not represent the response of this component. | Not Given | By User | By User | Not Given | none | none | none |  |  | No | 2016-10-25 - Repair method clarified. | YES
D3031.022j | D3031.022j | Cooling Tower - Capacity: 750 to <1000 Ton - Vibration isolated equipment that is not snubbed or restrained - Anchorage fragility only | Costing is per unit and is based upon 850 Ton. | Normal - Not designed for seismic loads | Vibration isolated equipment that is not snubbed or restrained | Each | Each | Peak Floor Acceleration | g | 2 | DS1 | DS2 |  |  |  | Mutually Exclusive | Mutually Exclusive |  |  |  | MutEx(DS1,DS2) | 464 | TN 850 | YES | BLDG | Anchorage failure. | Anchorage failure & Equipment damaged beyond repair. |  |  |  | 0.7 | 0.3 |  |  |  | By User | By User |  |  |  | User to Calculate | User to Calculate |  |  |  | User to Calculate | User to Calculate |  |  |  | By User | By User |  |  |  | NO | NO | Average | Average | Superior | Superior | Repair anchorage and concrete pad and remount equipment. | Replace equipment including attached utilities in addition to repairing anchorage and concrete pad. Cooling tower removed, repaired offsite, and reinstalled. |  |  |  | YES | YES |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | NO |  |  |  | 0% | 0% |  |  |  | 0 | 0 |  |  |  | User to provide median demand and dispersion values. The values listed are default PACT values and do not represent the response of this component. | Not Given | By User | By User | Not Given | none | none |  |  |  | No | 2016-10-25 - Repair method clarified. | YES
D3031.022k | D3031.022k | Cooling Tower - Capacity: 750 to <1000 Ton - Vibration isolated equipment that is not snubbed or restrained - Equipment fragility only | Costing is per unit and is based upon 850 Ton. | Normal - Not designed for seismic loads | Vibration isolated equipment that is not snubbed or restrained | Each | Each | Peak Floor Acceleration | g | 1 | DS1 |  |  |  |  | Sequential |  |  |  |  | Seq(DS1) | 465 | TN 850 | YES | BLDG | Damaged equipment and attached piping but anchorage is OK. |  |  |  |  | 1 |  |  |  |  | 0.97 |  |  |  |  | 0.6 |  |  |  |  | 0.1 |  |  |  |  | 0.6 |  |  |  |  | NO | NO | Average | Average | Superior | Superior | Repair damaged equipment and attached piping. Cooling tower removed, repaired offsite, and reinstalled. |  |  |  |  | YES |  |  |  |  | NO |  |  |  |  | Not Applicable |  |  |  |  | 0% | 0 | [8 empty] | 0% | 0 | [8 empty] | NO |  |  |  |  | 0% |  |  |  |  | 0 |  |  |  |  | None | Not Given | By User | By User | Not Given | none |  |  |  |  | No | 2016-10-25 - Repair method clarified. | YES
D3031.022l | D3031.022l | Cooling Tower - Capacity: 750 to <1000 Ton - Vibration isolated equipment that is not snubbed or restrained - Combined anchorage/isolator & equipment fragility | Costing is per unit and is based upon 850 Ton. | Normal - Not designed for seismic loads | Vibration isolated equipment that is not snubbed or restrained | Each | Each | Peak Floor Acceleration | g | 3 | DS1 | DS2 | DS3 |  |  | Mutually Exclusive | Mutually Exclusive | Mutually Exclusive |  |  | MutEx(DS1,DS2,DS3) | 466 | TN 850 | YES | BLDG | Anchorage failure. | Anchorage failure & Equipment damaged beyond repair. | Damaged equipment and attached piping but anchorage OK. |  |  | 0.35 | 0.15 | 0.5 |  |  | By User | By User | By User |  |  | User to Calculate | User to Calculate | User to Calculate |  |  | User to Calculate | User to Calculate | User to Calculate |  |  | By User | By User | By User |  |  | NO | NO | Average | Average | Superior | Superior | Repair anchorage and concrete pad and remount equipment. | Replace equipment including attached utilities in addition to repairing anchorage and concrete pad. Cooling tower removed, repaired offsite, and reinstalled. | Repair damaged equipment and attached piping. Cooling tower removed, repaired offsite, and reinstalled. |  |  | YES | YES | YES |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | NO | NO |  |  | 0% | 0% | 0% |  |  | 0 | 0 | 0 |  |  | User to provide median demand and dispersion values. The values listed are default PACT values and do not represent the response of this component. | Not Given | By User | By User | Not Given | none | none | none |  |  | No | 2016-10-25 - Repair method clarified. | YES
D3031.023a | D3031.023a | Cooling Tower - Capacity: < 100 Ton - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only | Costing is per unit and is based upon 75 Ton. | Normal - Designed for seismic loads but no special seismic certification | Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints | Each | Each | Peak Floor Acceleration | g | 2 | DS1 | DS2 |  |  |  | Mutually Exclusive | Mutually Exclusive |  |  |  | MutEx(DS1,DS2) | 467 | TN 75 | YES | BLDG | Anchorage failure. | Anchorage failure & Equipment damaged beyond repair. |  |  |  | 0.7 | 0.3 |  |  |  | By User | By User |  |  |  | User to Calculate | User to Calculate |  |  |  | User to Calculate | User to Calculate |  |  |  | By User | By User |  |  |  | NO | NO | Average | Average | Superior | Superior | Repair anchorage and concrete pad and remount equipment. | Replace equipment including attached utilities in addition to repairing anchorage and concrete pad. Cooling tower removed, repaired offsite, and reinstalled. |  |  |  | NO | YES |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | NO |  |  |  | 0% | 0% |  |  |  | 0 | 0 |  |  |  | User to provide median demand and dispersion values. The values listed are default PACT values and do not represent the response of this component. | Not Given | By User | By User | Not Given | none | none |  |  |  | No | 2016-10-25 - Repair method clarified. | YES
D3031.023b | D3031.023b | Cooling Tower - Capacity: < 100 Ton - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only | Costing is per unit and is based upon 75 Ton. | Normal - Designed for seismic loads but no special seismic certification | Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints | Each | Each | Peak Floor Acceleration | g | 1 | DS1 |  |  |  |  | Sequential |  |  |  |  | Seq(DS1) | 468 | TN 75 | YES | BLDG | Damaged equipment and attached piping but anchorage is OK. |  |  |  |  | 1 |  |  |  |  | 1.52 |  |  |  |  | 0.4 |  |  |  |  | 0.1 |  |  |  |  | 0.4 |  |  |  |  | NO | NO | Average | Average | Superior | Superior | Repair damaged equipment and attached piping. Cooling tower removed, repaired offsite, and reinstalled. |  |  |  |  | NO |  |  |  |  | NO |  |  |  |  | Not Applicable |  |  |  |  | 0% | 0 | [8 empty] | 0% | 0 | [8 empty] | NO |  |  |  |  | 0% |  |  |  |  | 0 |  |  |  |  | None | Not Given | By User | By User | Not Given | none |  |  |  |  | No | 2016-10-25 - Repair method clarified. | YES
D3031.023c | D3031.023c | Cooling Tower - Capacity: < 100 Ton - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | Costing is per unit and is based upon 75 Ton. | Normal - Designed for seismic loads but no special seismic certification | Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints | Each | Each | Peak Floor Acceleration | g | 3 | DS1 | DS2 | DS3 |  |  | Mutually Exclusive | Mutually Exclusive | Mutually Exclusive |  |  | MutEx(DS1,DS2,DS3) | 469 | TN 75 | YES | BLDG | Anchorage failure. | Anchorage failure & Equipment damaged beyond repair. | Damaged equipment and attached piping but anchorage OK. |  |  | 0.35 | 0.15 | 0.5 |  |  | By User | By User | By User |  |  | User to Calculate | User to Calculate | User to Calculate |  |  | User to Calculate | User to Calculate | User to Calculate |  |  | By User | By User | By User |  |  | NO | NO | Average | Average | Superior | Superior | Repair anchorage and concrete pad and remount equipment. | Replace equipment including attached utilities in addition to repairing anchorage and concrete pad. Cooling tower removed, repaired offsite, and reinstalled. | Repair damaged equipment and attached piping. Cooling tower removed, repaired offsite, and reinstalled. |  |  | NO | YES | NO |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | NO | NO |  |  | 0% | 0% | 0% |  |  | 0 | 0 | 0 |  |  | User to provide median demand and dispersion values. The values listed are default PACT values and do not represent the response of this component. | Not Given | By User | By User | Not Given | none | none | none |  |  | No | 2016-10-25 - Repair method clarified. | YES
D3031.023d | D3031.023d | Cooling Tower - Capacity: 100 to <350 Ton - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only | Costing is per unit and is based upon 250 Ton. | Normal - Designed for seismic loads but no special seismic certification | Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints | Each | Each | Peak Floor Acceleration | g | 2 | DS1 | DS2 |  |  |  | Mutually Exclusive | Mutually Exclusive |  |  |  | MutEx(DS1,DS2) | 470 | TN 250 | YES | BLDG | Anchorage failure. | Anchorage failure & Equipment damaged beyond repair. |  |  |  | 0.7 | 0.3 |  |  |  | By User | By User |  |  |  | User to Calculate | User to Calculate |  |  |  | User to Calculate | User to Calculate |  |  |  | By User | By User |  |  |  | NO | NO | Average | Average | Superior | Superior | Repair anchorage and concrete pad and remount equipment. | Replace equipment including attached utilities in addition to repairing anchorage and concrete pad. Cooling tower removed, repaired offsite, and reinstalled. |  |  |  | YES | YES |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | NO |  |  |  | 0% | 0% |  |  |  | 0 | 0 |  |  |  | User to provide median demand and dispersion values. The values listed are default PACT values and do not represent the response of this component. | Not Given | By User | By User | Not Given | none | none |  |  |  | No | 2016-10-25 - Repair method clarified. | YES
D3031.023e | D3031.023e | Cooling Tower - Capacity: 100 to <350 Ton - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only | Costing is per unit and is based upon 250 Ton. | Normal - Designed for seismic loads but no special seismic certification | Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints | Each | Each | Peak Floor Acceleration | g | 1 | DS1 |  |  |  |  | Sequential |  |  |  |  | Seq(DS1) | 471 | TN 250 | YES | BLDG | Damaged equipment and attached piping but anchorage is OK. |  |  |  |  | 1 |  |  |  |  | 1.52 |  |  |  |  | 0.4 |  |  |  |  | 0.1 |  |  |  |  | 0.4 |  |  |  |  | NO | NO | Average | Average | Superior | Superior | Repair damaged equipment and attached piping. Cooling tower removed, repaired offsite, and reinstalled. |  |  |  |  | YES |  |  |  |  | NO |  |  |  |  | Not Applicable |  |  |  |  | 0% | 0 | [8 empty] | 0% | 0 | [8 empty] | NO |  |  |  |  | 0% |  |  |  |  | 0 |  |  |  |  | None | Not Given | By User | By User | Not Given | none |  |  |  |  | No | 2016-10-25 - Repair method clarified. | YES
D3031.023f | D3031.023f | Cooling Tower - Capacity: 100 to <350 Ton - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | Costing is per unit and is based upon 250 Ton. | Normal - Designed for seismic loads but no special seismic certification | Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints | Each | Each | Peak Floor Acceleration | g | 3 | DS1 | DS2 | DS3 |  |  | Mutually Exclusive | Mutually Exclusive | Mutually Exclusive |  |  | MutEx(DS1,DS2,DS3) | 472 | TN 250 | YES | BLDG | Anchorage failure. | Anchorage failure & Equipment damaged beyond repair. | Damaged equipment and attached piping but anchorage OK. |  |  | 0.35 | 0.15 | 0.5 |  |  | By User | By User | By User |  |  | User to Calculate | User to Calculate | User to Calculate |  |  | User to Calculate | User to Calculate | User to Calculate |  |  | By User | By User | By User |  |  | NO | NO | Average | Average | Superior | Superior | Repair anchorage and concrete pad and remount equipment. | Replace equipment including attached utilities in addition to repairing anchorage and concrete pad. Cooling tower removed, repaired offsite, and reinstalled. | Repair damaged equipment and attached piping. Cooling tower removed, repaired offsite, and reinstalled. |  |  | YES | YES | YES |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | NO | NO |  |  | 0% | 0% | 0% |  |  | 0 | 0 | 0 |  |  | User to provide median demand and dispersion values. The values listed are default PACT values and do not represent the response of this component. | Not Given | By User | By User | Not Given | none | none | none |  |  | No | 2016-10-25 - Repair method clarified. | YES
D3031.023g | D3031.023g | Cooling Tower - Capacity: 350 to <750 Ton - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only | Costing is per unit and is based upon 500 Ton. | Normal - Designed for seismic loads but no special seismic certification | Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints | Each | Each | Peak Floor Acceleration | g | 2 | DS1 | DS2 |  |  |  | Mutually Exclusive | Mutually Exclusive |  |  |  | MutEx(DS1,DS2) | 473 | TN 500 | YES | BLDG | Anchorage failure. | Anchorage failure & Equipment damaged beyond repair. |  |  |  | 0.7 | 0.3 |  |  |  | By User | By User |  |  |  | User to Calculate | User to Calculate |  |  |  | User to Calculate | User to Calculate |  |  |  | By User | By User |  |  |  | NO | NO | Average | Average | Superior | Superior | Repair anchorage and concrete pad and remount equipment. | Replace equipment including attached utilities in addition to repairing anchorage and concrete pad. Cooling tower removed, repaired offsite, and reinstalled. |  |  |  | YES | YES |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | NO |  |  |  | 0% | 0% |  |  |  | 0 | 0 |  |  |  | User to provide median demand and dispersion values. The values listed are default PACT values and do not represent the response of this component. | Not Given | By User | By User | Not Given | none | none |  |  |  | No | 2016-10-25 - Repair method clarified. | YES
D3031.023h | D3031.023h | Cooling Tower - Capacity: 350 to <750 Ton - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only | Costing is per unit and is based upon 500 Ton. | Normal - Designed for seismic loads but no special seismic certification | Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints | Each | Each | Peak Floor Acceleration | g | 1 | DS1 |  |  |  |  | Sequential |  |  |  |  | Seq(DS1) | 474 | TN 500 | YES | BLDG | Damaged equipment and attached piping but anchorage is OK. |  |  |  |  | 1 |  |  |  |  | 1.52 |  |  |  |  | 0.4 |  |  |  |  | 0.1 |  |  |  |  | 0.4 |  |  |  |  | NO | NO | Average | Average | Superior | Superior | Repair damaged equipment and attached piping. Cooling tower removed, repaired offsite, and reinstalled. |  |  |  |  | YES |  |  |  |  | NO |  |  |  |  | Not Applicable |  |  |  |  | 0% | 0 | [8 empty] | 0% | 0 | [8 empty] | NO |  |  |  |  | 0% |  |  |  |  | 0 |  |  |  |  | None | Not Given | By User | By User | Not Given | none |  |  |  |  | No | 2016-10-25 - Repair method clarified. | YES
D3031.023i | D3031.023i | Cooling Tower - Capacity: 350 to <750 Ton - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | Costing is per unit and is based upon 500 Ton. | Normal - Designed for seismic loads but no special seismic certification | Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints | Each | Each | Peak Floor Acceleration | g | 3 | DS1 | DS2 | DS3 |  |  | Mutually Exclusive | Mutually Exclusive | Mutually Exclusive |  |  | MutEx(DS1,DS2,DS3) | 475 | TN 500 | YES | BLDG | Anchorage failure. | Anchorage failure & Equipment damaged beyond repair. | Damaged equipment and attached piping but anchorage OK. |  |  | 0.35 | 0.15 | 0.5 |  |  | By User | By User | By User |  |  | User to Calculate | User to Calculate | User to Calculate |  |  | User to Calculate | User to Calculate | User to Calculate |  |  | By User | By User | By User |  |  | NO | NO | Average | Average | Superior | Superior | Repair anchorage and concrete pad and remount equipment. | Replace equipment including attached utilities in addition to repairing anchorage and concrete pad. Cooling tower removed, repaired offsite, and reinstalled. | Repair damaged equipment and attached piping. Cooling tower removed, repaired offsite, and reinstalled. |  |  | YES | YES | YES |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | NO | NO |  |  | 0% | 0% | 0% |  |  | 0 | 0 | 0 |  |  | User to provide median demand and dispersion values. The values listed are default PACT values and do not represent the response of this component. | Not Given | By User | By User | Not Given | none | none | none |  |  | No | 2016-10-25 - Repair method clarified. | YES
D3031.023j | D3031.023j | Cooling Tower - Capacity: 750 to <1000 Ton - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only | Costing is per unit and is based upon 850 Ton. | Normal - Designed for seismic loads but no special seismic certification | Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints | Each | Each | Peak Floor Acceleration | g | 2 | DS1 | DS2 |  |  |  | Mutually Exclusive | Mutually Exclusive |  |  |  | MutEx(DS1,DS2) | 476 | TN 850 | YES | BLDG | Anchorage failure. | Anchorage failure & Equipment damaged beyond repair. |  |  |  | 0.7 | 0.3 |  |  |  | By User | By User |  |  |  | User to Calculate | User to Calculate |  |  |  | User to Calculate | User to Calculate |  |  |  | By User | By User |  |  |  | NO | NO | Average | Average | Superior | Superior | Repair anchorage and concrete pad and remount equipment. | Replace equipment including attached utilities in addition to repairing anchorage and concrete pad. Cooling tower removed, repaired offsite, and reinstalled. |  |  |  | YES | YES |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | NO |  |  |  | 0% | 0% |  |  |  | 0 | 0 |  |  |  | User to provide median demand and dispersion values. The values listed are default PACT values and do not represent the response of this component. | Not Given | By User | By User | Not Given | none | none |  |  |  | No | 2016-10-25 - Repair method clarified. | YES
D3031.023k | D3031.023k | Cooling Tower - Capacity: 750 to <1000 Ton - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only | Costing is per unit and is based upon 850 Ton. | Normal - Designed for seismic loads but no special seismic certification | Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints | Each | Each | Peak Floor Acceleration | g | 1 | DS1 |  |  |  |  | Sequential |  |  |  |  | Seq(DS1) | 477 | TN 850 | YES | BLDG | Damaged equipment and attached piping but anchorage is OK. |  |  |  |  | 1 |  |  |  |  | 1.52 |  |  |  |  | 0.4 |  |  |  |  | 0.1 |  |  |  |  | 0.4 |  |  |  |  | NO | NO | Average | Average | Superior | Superior | Repair damaged equipment and attached piping. Cooling tower removed, repaired offsite, and reinstalled. |  |  |  |  | YES |  |  |  |  | NO |  |  |  |  | Not Applicable |  |  |  |  | 0% | 0 | [8 empty] | 0% | 0 | [8 empty] | NO |  |  |  |  | 0% |  |  |  |  | 0 |  |  |  |  | None | Not Given | By User | By User | Not Given | none |  |  |  |  | No | 2016-10-25 - Repair method clarified. | YES
D3031.023l | D3031.023l | Cooling Tower - Capacity: 750 to <1000 Ton - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | Costing is per unit and is based upon 850 Ton. | Normal - Designed for seismic loads but no special seismic certification | Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints | Each | Each | Peak Floor Acceleration | g | 3 | DS1 | DS2 | DS3 |  |  | Mutually Exclusive | Mutually Exclusive | Mutually Exclusive |  |  | MutEx(DS1,DS2,DS3) | 478 | TN 850 | YES | BLDG | Anchorage failure. | Anchorage failure & Equipment damaged beyond repair. | Damaged equipment and attached piping but anchorage OK. |  |  | 0.35 | 0.15 | 0.5 |  |  | By User | By User | By User |  |  | User to Calculate | User to Calculate | User to Calculate |  |  | User to Calculate | User to Calculate | User to Calculate |  |  | By User | By User | By User |  |  | NO | NO | Average | Average | Superior | Superior | Repair anchorage and concrete pad and remount equipment. | Replace equipment including attached utilities in addition to repairing anchorage and concrete pad. Cooling tower removed, repaired offsite, and reinstalled. | Repair damaged equipment and attached piping. Cooling tower removed, repaired offsite, and reinstalled. |  |  | YES | YES | YES |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | NO | NO |  |  | 0% | 0% | 0% |  |  | 0 | 0 | 0 |  |  | User to provide median demand and dispersion values. The values listed are default PACT values and do not represent the response of this component. | Not Given | By User | By User | Not Given | none | none | none |  |  | No | 2016-10-25 - Repair method clarified. | YES
D3032.011a | D3032.011a | Compressor - Capacity: Small non medical air supply - Unanchored equipment that is not vibration isolated - Equipment fragility only | Costing is per unit. | Normal - Not designed for seismic loads | Unanchored equipment that is not vibration isolated | Each | Each | Peak Floor Acceleration | g | 2 | DS1 | DS2 |  |  |  | Mutually Exclusive | Mutually Exclusive |  |  |  | MutEx(DS1,DS2) | 479 | EA 1 | YES | BLDG | Equipment does not function. Motor is damaged. | Equipment does not function. Equipment damaged beyond repair. |  |  |  | 0.5 | 0.5 |  |  |  | 0.25 | 0.25 |  |  |  | 0.4 | 0.4 |  |  |  | 0.25 | 0.25 |  |  |  | 0.45 | 0.45 |  |  |  | NO | NO | Average | Average | Superior | Superior | Repair motor. | Replace equipment. |  |  |  | NO | YES |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | NO |  |  |  | 0% | 0% |  |  |  | 0 | 0 |  |  |  | None | Not Given | By User | By User | Not Given | D3032.011a-DS1-1.JPG | none |  |  |  | No | None | YES
D3032.011b | D3032.011b | Compressor - Capacity: Large non medical air supply - Unanchored equipment that is not vibration isolated - Equipment fragility only | Costing is per unit. | Normal - Not designed for seismic loads | Unanchored equipment that is not vibration isolated | Each | Each | Peak Floor Acceleration | g | 2 | DS1 | DS2 |  |  |  | Mutually Exclusive | Mutually Exclusive |  |  |  | MutEx(DS1,DS2) | 480 | EA 1 | YES | BLDG | Equipment does not function. Motor is damaged. | Equipment does not function. Equipment damaged beyond repair. |  |  |  | 0.5 | 0.5 |  |  |  | 0.25 | 0.25 |  |  |  | 0.4 | 0.4 |  |  |  | 0.25 | 0.25 |  |  |  | 0.45 | 0.45 |  |  |  | NO | NO | Average | Average | Superior | Superior | Repair motor. | Replace equipment. |  |  |  | NO | YES |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | NO |  |  |  | 0% | 0% |  |  |  | 0 | 0 |  |  |  | None | Not Given | By User | By User | Not Given | D3032.011a-DS1-1.JPG | none |  |  |  | No | None | YES
D3032.011c | D3032.011c | Compressor - Capacity: Small medical quality air supply - Unanchored equipment that is not vibration isolated - Equipment fragility only | Costing is per unit. | Normal - Not designed for seismic loads | Unanchored equipment that is not vibration isolated | Each | Each | Peak Floor Acceleration | g | 2 | DS1 | DS2 |  |  |  | Mutually Exclusive | Mutually Exclusive |  |  |  | MutEx(DS1,DS2) | 481 | EA 1 | YES | BLDG | Equipment does not function. Motor is damaged. | Equipment does not function. Equipment damaged beyond repair. |  |  |  | 0.5 | 0.5 |  |  |  | 0.25 | 0.25 |  |  |  | 0.4 | 0.4 |  |  |  | 0.25 | 0.25 |  |  |  | 0.45 | 0.45 |  |  |  | NO | NO | Average | Average | Superior | Superior | Repair motor. | Replace equipment. |  |  |  | NO | YES |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | NO |  |  |  | 0% | 0% |  |  |  | 0 | 0 |  |  |  | None | Not Given | By User | By User | Not Given | D3032.011a-DS1-1.JPG | none |  |  |  | No | None | YES
D3032.011d | D3032.011d | Compressor - Capacity: Large medical quality air supply - Unanchored equipment that is not vibration isolated - Equipment fragility only | Costing is per unit. | Normal - Not designed for seismic loads | Unanchored equipment that is not vibration isolated | Each | Each | Peak Floor Acceleration | g | 2 | DS1 | DS2 |  |  |  | Mutually Exclusive | Mutually Exclusive |  |  |  | MutEx(DS1,DS2) | 482 | EA 1 | YES | BLDG | Equipment does not function. Motor is damaged. | Equipment does not function. Equipment damaged beyond repair. |  |  |  | 0.5 | 0.5 |  |  |  | 0.25 | 0.25 |  |  |  | 0.4 | 0.4 |  |  |  | 0.25 | 0.25 |  |  |  | 0.45 | 0.45 |  |  |  | NO | NO | Average | Average | Superior | Superior | Repair motor. | Replace equipment. |  |  |  | NO | YES |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | NO |  |  |  | 0% | 0% |  |  |  | 0 | 0 |  |  |  | None | Not Given | By User | By User | Not Given | D3032.011a-DS1-1.JPG | none |  |  |  | No | None | YES
D3032.012a | D3032.012a | Compressor - Capacity: Small non medical air supply - Vibration isolated equipment that is not snubbed or restrained - Anchorage fragility only | Costing is per unit. | Normal - Not designed for seismic loads | Vibration isolated equipment that is not snubbed or restrained | Each | Each | Peak Floor Acceleration | g | 2 | DS1 | DS2 |  |  |  | Mutually Exclusive | Mutually Exclusive |  |  |  | MutEx(DS1,DS2) | 483 | EA 1 | YES | BLDG | Anchorage failure. | Anchorage failure & Equipment damaged beyond repair. |  |  |  | 0.7 | 0.3 |  |  |  | By User | By User |  |  |  | User to Calculate | User to Calculate |  |  |  | User to Calculate | User to Calculate |  |  |  | By User | By User |  |  |  | NO | NO | Average | Average | Superior | Superior | Repair anchorage and concrete pad and remount equipment. | Replace equipment including attached utilities in addition to repairing anchorage and concrete pad. |  |  |  | NO | YES |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | NO |  |  |  | 0% | 0% |  |  |  | 0 | 0 |  |  |  | User to provide median demand and dispersion values. The values listed are default PACT values and do not represent the response of this component. | Not Given | By User | By User | Not Given | D3032.011a-DS1-1.JPG | none |  |  |  | No | None | YES
D3032.012b | D3032.012b | Compressor - Capacity: Small non medical air supply - Vibration isolated equipment that is not snubbed or restrained - Equipment fragility only | Costing is per unit. | Normal - Not designed for seismic loads | Vibration isolated equipment that is not snubbed or restrained | Each | Each | Peak Floor Acceleration | g | 2 | DS1 | DS2 |  |  |  | Mutually Exclusive | Mutually Exclusive |  |  |  | MutEx(DS1,DS2) | 484 | EA 1 | YES | BLDG | Equipment does not function but anchorage is OK. Motor is damaged. | Equipment does not function but anchorage is OK. Equipment damaged beyond repair. |  |  |  | 0.5 | 0.5 |  |  |  | 0.47 | 0.47 |  |  |  | 0.2 | 0.2 |  |  |  | 0.1 | 0.1 |  |  |  | 0.2 | 0.2 |  |  |  | NO | NO | Average | Average | Superior | Superior | Repair motor. | Replace equipment. |  |  |  | NO | YES |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | NO |  |  |  | 0% | 0% |  |  |  | 0 | 0 |  |  |  | None | Not Given | By User | By User | Not Given | D3032.011a-DS1-1.JPG | none |  |  |  | No | None | YES
D3032.012c | D3032.012c | Compressor - Capacity: Small non medical air supply - Vibration isolated equipment that is not snubbed or restrained - Combined anchorage/isolator & equipment fragility | Costing is per unit. | Normal - Not designed for seismic loads | Vibration isolated equipment that is not snubbed or restrained | Each | Each | Peak Floor Acceleration | g | 4 | DS1 | DS2 | DS3 | DS4 |  | Mutually Exclusive | Mutually Exclusive | Mutually Exclusive | Mutually Exclusive |  | MutEx(DS1,DS2,DS3,DS4) | 485 | EA 1 | YES | BLDG | Anchorage failure. | Anchorage failure & Equipment damaged beyond repair. | Motor damaged but anchorage is OK. | Equipment damaged beyond repair but anchorage is OK. |  | 0.35 | 0.15 | 0.25 | 0.25 |  | By User | By User | By User | By User |  | User to Calculate | User to Calculate | User to Calculate | User to Calculate |  | User to Calculate | User to Calculate | User to Calculate | User to Calculate |  | By User | By User | By User | By User |  | NO | NO | Average | Average | Superior | Superior | Repair anchorage and concrete pad and remount equipment. | Replace equipment including attached utilities in addition to repairing anchorage and concrete pad. | Repair Motor - Anchorage and Concrete do not require replacement | Replace and install equipment including new anchorage if anchorage is post-installed. |  | NO | YES | NO | YES |  | NO | NO | NO | NO |  | Not Applicable | Not Applicable | Not Applicable | Not Applicable |  | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 |  |  | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 |  |  | NO | NO | NO | NO |  | 0% | 0% | 0% | 0% |  | 0 | 0 | 0 | 0 |  | User to provide median demand and dispersion values. The values listed are default PACT values and do not represent the response of this component. | Not Given | By User | By User | Not Given | D3032.011a-DS1-1.JPG | none | none | none |  | No | None | YES
D3032.012d | D3032.012d | Compressor - Capacity: Large non medical air supply - Vibration isolated equipment that is not snubbed or restrained - Anchorage fragility only | Costing is per unit. | Normal - Not designed for seismic loads | Vibration isolated equipment that is not snubbed or restrained | Each | Each | Peak Floor Acceleration | g | 2 | DS1 | DS2 |  |  |  | Mutually Exclusive | Mutually Exclusive |  |  |  | MutEx(DS1,DS2) | 486 | EA 1 | YES | BLDG | Anchorage failure. | Anchorage failure & Equipment damaged beyond repair. |  |  |  | 0.7 | 0.3 |  |  |  | By User | By User |  |  |  | User to Calculate | User to Calculate |  |  |  | User to Calculate | User to Calculate |  |  |  | By User | By User |  |  |  | NO | NO | Average | Average | Superior | Superior | Repair anchorage and concrete pad and remount equipment. | Replace equipment including attached utilities in addition to repairing anchorage and concrete pad. |  |  |  | NO | YES |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | NO |  |  |  | 0% | 0% |  |  |  | 0 | 0 |  |  |  | User to provide median demand and dispersion values. The values listed are default PACT values and do not represent the response of this component. | Not Given | By User | By User | Not Given | D3032.011a-DS1-1.JPG | none |  |  |  | No | None | YES
D3032.012e | D3032.012e | Compressor - Capacity: Large non medical air supply - Vibration isolated equipment that is not snubbed or restrained - Equipment fragility only | Costing is per unit. | Normal - Not designed for seismic loads | Vibration isolated equipment that is not snubbed or restrained | Each | Each | Peak Floor Acceleration | g | 2 | DS1 | DS2 |  |  |  | Mutually Exclusive | Mutually Exclusive |  |  |  | MutEx(DS1,DS2) | 487 | EA 1 | YES | BLDG | Equipment does not function but anchorage is OK. Motor is damaged. | Equipment does not function but anchorage is OK. Equipment damaged beyond repair. |  |  |  | 0.5 | 0.5 |  |  |  | 0.47 | 0.47 |  |  |  | 0.2 | 0.2 |  |  |  | 0.1 | 0.1 |  |  |  | 0.2 | 0.2 |  |  |  | NO | NO | Average | Average | Superior | Superior | Repair motor. | Replace equipment. |  |  |  | NO | YES |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | NO |  |  |  | 0% | 0% |  |  |  | 0 | 0 |  |  |  | None | Not Given | By User | By User | Not Given | D3032.011a-DS1-1.JPG | none |  |  |  | No | None | YES
D3032.012f | D3032.012f | Compressor - Capacity: Large non medical air supply - Vibration isolated equipment that is not snubbed or restrained - Combined anchorage/isolator & equipment fragility | Costing is per unit. | Normal - Not designed for seismic loads | Vibration isolated equipment that is not snubbed or restrained | Each | Each | Peak Floor Acceleration | g | 4 | DS1 | DS2 | DS3 | DS4 |  | Mutually Exclusive | Mutually Exclusive | Mutually Exclusive | Mutually Exclusive |  | MutEx(DS1,DS2,DS3,DS4) | 488 | EA 1 | YES | BLDG | Anchorage failure. | Anchorage failure & Equipment damaged beyond repair. | Motor damaged but anchorage is OK. | Equipment damaged beyond repair but anchorage is OK. |  | 0.35 | 0.15 | 0.25 | 0.25 |  | By User | By User | By User | By User |  | User to Calculate | User to Calculate | User to Calculate | User to Calculate |  | User to Calculate | User to Calculate | User to Calculate | User to Calculate |  | By User | By User | By User | By User |  | NO | NO | Average | Average | Superior | Superior | Repair anchorage and concrete pad and remount equipment. | Replace equipment including attached utilities in addition to repairing anchorage and concrete pad. | Repair Motor - Anchorage and Concrete do not require replacement | Replace and install equipment including new anchorage if anchorage is post-installed. |  | NO | YES | NO | YES |  | NO | NO | NO | NO |  | Not Applicable | Not Applicable | Not Applicable | Not Applicable |  | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 |  |  | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 |  |  | NO | NO | NO | NO |  | 0% | 0% | 0% | 0% |  | 0 | 0 | 0 | 0 |  | User to provide median demand and dispersion values. The values listed are default PACT values and do not represent the response of this component. | Not Given | By User | By User | Not Given | D3032.011a-DS1-1.JPG | none | none | none |  | No | None | YES
D3032.012g | D3032.012g | Compressor - Capacity: Small medical quality air supply - Vibration isolated equipment that is not snubbed or restrained - Anchorage fragility only | Costing is per unit. | Normal - Not designed for seismic loads | Vibration isolated equipment that is not snubbed or restrained | Each | Each | Peak Floor Acceleration | g | 2 | DS1 | DS2 |  |  |  | Mutually Exclusive | Mutually Exclusive |  |  |  | MutEx(DS1,DS2) | 489 | EA 1 | YES | BLDG | Anchorage failure. | Anchorage failure & Equipment damaged beyond repair. |  |  |  | 0.7 | 0.3 |  |  |  | By User | By User |  |  |  | User to Calculate | User to Calculate |  |  |  | User to Calculate | User to Calculate |  |  |  | By User | By User |  |  |  | NO | NO | Average | Average | Superior | Superior | Repair anchorage and concrete pad and remount equipment. | Replace equipment including attached utilities in addition to repairing anchorage and concrete pad. |  |  |  | NO | YES |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | NO |  |  |  | 0% | 0% |  |  |  | 0 | 0 |  |  |  | User to provide median demand and dispersion values. The values listed are default PACT values and do not represent the response of this component. | Not Given | By User | By User | Not Given | D3032.011a-DS1-1.JPG | none |  |  |  | No | None | YES
D3032.012h | D3032.012h | Compressor - Capacity: Small medical quality air supply - Vibration isolated equipment that is not snubbed or restrained - Equipment fragility only | Costing is per unit. | Normal - Not designed for seismic loads | Vibration isolated equipment that is not snubbed or restrained | Each | Each | Peak Floor Acceleration | g | 2 | DS1 | DS2 |  |  |  | Mutually Exclusive | Mutually Exclusive |  |  |  | MutEx(DS1,DS2) | 490 | EA 1 | YES | BLDG | Equipment does not function but anchorage is OK. Motor is damaged. | Equipment does not function but anchorage is OK. Equipment damaged beyond repair. |  |  |  | 0.5 | 0.5 |  |  |  | 0.47 | 0.47 |  |  |  | 0.2 | 0.2 |  |  |  | 0.1 | 0.1 |  |  |  | 0.2 | 0.2 |  |  |  | NO | NO | Average | Average | Superior | Superior | Repair motor. | Replace equipment. |  |  |  | NO | YES |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | NO |  |  |  | 0% | 0% |  |  |  | 0 | 0 |  |  |  | None | Not Given | By User | By User | Not Given | D3032.011a-DS1-1.JPG | none |  |  |  | No | None | YES
D3032.012i | D3032.012i | Compressor - Capacity: Small medical quality air supply - Vibration isolated equipment that is not snubbed or restrained - Combined anchorage/isolator & equipment fragility | Costing is per unit. | Normal - Not designed for seismic loads | Vibration isolated equipment that is not snubbed or restrained | Each | Each | Peak Floor Acceleration | g | 4 | DS1 | DS2 | DS3 | DS4 |  | Mutually Exclusive | Mutually Exclusive | Mutually Exclusive | Mutually Exclusive |  | MutEx(DS1,DS2,DS3,DS4) | 491 | EA 1 | YES | BLDG | Anchorage failure. | Anchorage failure & Equipment damaged beyond repair. | Motor damaged but anchorage is OK. | Equipment damaged beyond repair but anchorage is OK. |  | 0.35 | 0.15 | 0.25 | 0.25 |  | By User | By User | By User | By User |  | User to Calculate | User to Calculate | User to Calculate | User to Calculate |  | User to Calculate | User to Calculate | User to Calculate | User to Calculate |  | By User | By User | By User | By User |  | NO | NO | Average | Average | Superior | Superior | Repair anchorage and concrete pad and remount equipment. | Replace equipment including attached utilities in addition to repairing anchorage and concrete pad. | Repair Motor - Anchorage and Concrete do not require replacement | Replace and install equipment including new anchorage if anchorage is post-installed. |  | NO | YES | NO | YES |  | NO | NO | NO | NO |  | Not Applicable | Not Applicable | Not Applicable | Not Applicable |  | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 |  |  | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 |  |  | NO | NO | NO | NO |  | 0% | 0% | 0% | 0% |  | 0 | 0 | 0 | 0 |  | User to provide median demand and dispersion values. The values listed are default PACT values and do not represent the response of this component. | Not Given | By User | By User | Not Given | D3032.011a-DS1-1.JPG | none | none | none |  | No | None | YES
D3032.012j | D3032.012j | Compressor - Capacity: Large medical quality air supply - Vibration isolated equipment that is not snubbed or restrained - Anchorage fragility only | Costing is per unit. | Normal - Not designed for seismic loads | Vibration isolated equipment that is not snubbed or restrained | Each | Each | Peak Floor Acceleration | g | 2 | DS1 | DS2 |  |  |  | Mutually Exclusive | Mutually Exclusive |  |  |  | MutEx(DS1,DS2) | 492 | EA 1 | YES | BLDG | Anchorage failure. | Anchorage failure & Equipment damaged beyond repair. |  |  |  | 0.7 | 0.3 |  |  |  | By User | By User |  |  |  | User to Calculate | User to Calculate |  |  |  | User to Calculate | User to Calculate |  |  |  | By User | By User |  |  |  | NO | NO | Average | Average | Superior | Superior | Repair anchorage and concrete pad and remount equipment. | Replace equipment including attached utilities in addition to repairing anchorage and concrete pad. |  |  |  | NO | YES |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | NO |  |  |  | 0% | 0% |  |  |  | 0 | 0 |  |  |  | User to provide median demand and dispersion values. The values listed are default PACT values and do not represent the response of this component. | Not Given | By User | By User | Not Given | D3032.011a-DS1-1.JPG | none |  |  |  | No | None | YES
D3032.012k | D3032.012k | Compressor - Capacity: Large medical quality air supply - Vibration isolated equipment that is not snubbed or restrained - Equipment fragility only | Costing is per unit. | Normal - Not designed for seismic loads | Vibration isolated equipment that is not snubbed or restrained | Each | Each | Peak Floor Acceleration | g | 2 | DS1 | DS2 |  |  |  | Mutually Exclusive | Mutually Exclusive |  |  |  | MutEx(DS1,DS2) | 493 | EA 1 | YES | BLDG | Equipment does not function but anchorage is OK. Motor is damaged. | Equipment does not function but anchorage is OK. Equipment damaged beyond repair. |  |  |  | 0.5 | 0.5 |  |  |  | 0.47 | 0.47 |  |  |  | 0.2 | 0.2 |  |  |  | 0.1 | 0.1 |  |  |  | 0.2 | 0.2 |  |  |  | NO | NO | Average | Average | Superior | Superior | Repair motor. | Replace equipment. |  |  |  | NO | YES |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | NO |  |  |  | 0% | 0% |  |  |  | 0 | 0 |  |  |  | None | Not Given | By User | By User | Not Given | D3032.011a-DS1-1.JPG | none |  |  |  | No | None | YES
D3032.012l | D3032.012l | Compressor - Capacity: Large medical quality air supply - Vibration isolated equipment that is not snubbed or restrained - Combined anchorage/isolator & equipment fragility | Costing is per unit. | Normal - Not designed for seismic loads | Vibration isolated equipment that is not snubbed or restrained | Each | Each | Peak Floor Acceleration | g | 4 | DS1 | DS2 | DS3 | DS4 |  | Mutually Exclusive | Mutually Exclusive | Mutually Exclusive | Mutually Exclusive |  | MutEx(DS1,DS2,DS3,DS4) | 494 | EA 1 | YES | BLDG | Anchorage failure. | Anchorage failure & Equipment damaged beyond repair. | Motor damaged but anchorage is OK. | Equipment damaged beyond repair but anchorage is OK. |  | 0.35 | 0.15 | 0.25 | 0.25 |  | By User | By User | By User | By User |  | User to Calculate | User to Calculate | User to Calculate | User to Calculate |  | User to Calculate | User to Calculate | User to Calculate | User to Calculate |  | By User | By User | By User | By User |  | NO | NO | Average | Average | Superior | Superior | Repair anchorage and concrete pad and remount equipment. | Replace equipment including attached utilities in addition to repairing anchorage and concrete pad. | Repair Motor - Anchorage and Concrete do not require replacement | Replace and install equipment including new anchorage if anchorage is post-installed. |  | NO | YES | NO | YES |  | NO | NO | NO | NO |  | Not Applicable | Not Applicable | Not Applicable | Not Applicable |  | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 |  |  | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 |  |  | NO | NO | NO | NO |  | 0% | 0% | 0% | 0% |  | 0 | 0 | 0 | 0 |  | User to provide median demand and dispersion values. The values listed are default PACT values and do not represent the response of this component. | Not Given | By User | By User | Not Given | D3032.011a-DS1-1.JPG | none | none | none |  | No | None | YES
D3032.013a | D3032.013a | Compressor - Capacity: Small non medical air supply - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only | Costing is per unit. | Normal - Designed for seismic loads but no special seismic certification | Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints | Each | Each | Peak Floor Acceleration | g | 2 | DS1 | DS2 |  |  |  | Mutually Exclusive | Mutually Exclusive |  |  |  | MutEx(DS1,DS2) | 495 | EA 1 | YES | BLDG | Anchorage failure. | Anchorage failure & Equipment damaged beyond repair. |  |  |  | 0.7 | 0.3 |  |  |  | By User | By User |  |  |  | User to Calculate | User to Calculate |  |  |  | User to Calculate | User to Calculate |  |  |  | By User | By User |  |  |  | NO | NO | Average | Average | Superior | Superior | Repair anchorage and concrete pad and remount equipment. | Replace equipment including attached utilities in addition to repairing anchorage and concrete pad. |  |  |  | NO | YES |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | NO |  |  |  | 0% | 0% |  |  |  | 0 | 0 |  |  |  | User to provide median demand and dispersion values. The values listed are default PACT values and do not represent the response of this component. | Not Given | By User | By User | Not Given | D3032.011a-DS1-1.JPG | none |  |  |  | No | None | YES
D3032.013b | D3032.013b | Compressor - Capacity: Small non medical air supply - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only | Costing is per unit. | Normal - Designed for seismic loads but no special seismic certification | Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints | Each | Each | Peak Floor Acceleration | g | 2 | DS1 | DS2 |  |  |  | Mutually Exclusive | Mutually Exclusive |  |  |  | MutEx(DS1,DS2) | 496 | EA 1 | YES | BLDG | Equipment does not function but anchorage is OK. Motor is damaged. | Equipment does not function but anchorage is OK. Equipment damaged beyond repair. |  |  |  | 0.5 | 0.5 |  |  |  | 1.84 | 1.84 |  |  |  | 0.6 | 0.6 |  |  |  | 0.1 | 0.1 |  |  |  | 0.6 | 0.6 |  |  |  | NO | NO | Average | Average | Superior | Superior | Repair motor. | Replace equipment. |  |  |  | NO | YES |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | NO |  |  |  | 0% | 0% |  |  |  | 0 | 0 |  |  |  | None | Not Given | By User | By User | Not Given | D3032.011a-DS1-1.JPG | none |  |  |  | No | None | YES
D3032.013c | D3032.013c | Compressor - Capacity: Small non medical air supply - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | Costing is per unit. | Normal - Designed for seismic loads but no special seismic certification | Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints | Each | Each | Peak Floor Acceleration | g | 4 | DS1 | DS2 | DS3 | DS4 |  | Mutually Exclusive | Mutually Exclusive | Mutually Exclusive | Mutually Exclusive |  | MutEx(DS1,DS2,DS3,DS4) | 497 | EA 1 | YES | BLDG | Anchorage failure. | Anchorage failure & Equipment damaged beyond repair. | Motor damaged but anchorage is OK. | Equipment damaged beyond repair but anchorage is OK. |  | 0.35 | 0.15 | 0.25 | 0.25 |  | By User | By User | By User | By User |  | User to Calculate | User to Calculate | User to Calculate | User to Calculate |  | User to Calculate | User to Calculate | User to Calculate | User to Calculate |  | By User | By User | By User | By User |  | NO | NO | Average | Average | Superior | Superior | Repair anchorage and concrete pad and remount equipment. | Replace equipment including attached utilities in addition to repairing anchorage and concrete pad. | Repair Motor - Anchorage and Concrete do not require repair. | Replace and install equipment including new anchorage if anchorage is post-installed. |  | NO | YES | NO | YES |  | NO | NO | NO | NO |  | Not Applicable | Not Applicable | Not Applicable | Not Applicable |  | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 |  |  | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 |  |  | NO | NO | NO | NO |  | 0% | 0% | 0% | 0% |  | 0 | 0 | 0 | 0 |  | User to provide median demand and dispersion values. The values listed are default PACT values and do not represent the response of this component. | Not Given | By User | By User | Not Given | D3032.011a-DS1-1.JPG | none | none | none |  | No | None | YES
D3032.013d | D3032.013d | Compressor - Capacity: Large non medical air supply - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only | Costing is per unit. | Normal - Designed for seismic loads but no special seismic certification | Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints | Each | Each | Peak Floor Acceleration | g | 2 | DS1 | DS2 |  |  |  | Mutually Exclusive | Mutually Exclusive |  |  |  | MutEx(DS1,DS2) | 498 | EA 1 | YES | BLDG | Anchorage failure. | Anchorage failure & Equipment damaged beyond repair. |  |  |  | 0.7 | 0.3 |  |  |  | By User | By User |  |  |  | User to Calculate | User to Calculate |  |  |  | User to Calculate | User to Calculate |  |  |  | By User | By User |  |  |  | NO | NO | Average | Average | Superior | Superior | Repair anchorage and concrete pad and remount equipment. | Replace equipment including attached utilities in addition to repairing anchorage and concrete pad. |  |  |  | NO | YES |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | NO |  |  |  | 0% | 0% |  |  |  | 0 | 0 |  |  |  | User to provide median demand and dispersion values. The values listed are default PACT values and do not represent the response of this component. | Not Given | By User | By User | Not Given | D3032.011a-DS1-1.JPG | none |  |  |  | No | None | YES
D3032.013e | D3032.013e | Compressor - Capacity: Large non medical air supply - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only | Costing is per unit. | Normal - Designed for seismic loads but no special seismic certification | Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints | Each | Each | Peak Floor Acceleration | g | 2 | DS1 | DS2 |  |  |  | Mutually Exclusive | Mutually Exclusive |  |  |  | MutEx(DS1,DS2) | 499 | EA 1 | YES | BLDG | Equipment does not function but anchorage is OK. Motor is damaged. | Equipment does not function but anchorage is OK. Equipment damaged beyond repair. |  |  |  | 0.5 | 0.5 |  |  |  | 1.84 | 1.84 |  |  |  | 0.6 | 0.6 |  |  |  | 0.1 | 0.1 |  |  |  | 0.6 | 0.6 |  |  |  | NO | NO | Average | Average | Superior | Superior | Repair motor. | Replace equipment. |  |  |  | NO | YES |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | NO |  |  |  | 0% | 0% |  |  |  | 0 | 0 |  |  |  | None | Not Given | By User | By User | Not Given | D3032.011a-DS1-1.JPG | none |  |  |  | No | None | YES
D3032.013f | D3032.013f | Compressor - Capacity: Large non medical air supply - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | Costing is per unit. | Normal - Designed for seismic loads but no special seismic certification | Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints | Each | Each | Peak Floor Acceleration | g | 4 | DS1 | DS2 | DS3 | DS4 |  | Mutually Exclusive | Mutually Exclusive | Mutually Exclusive | Mutually Exclusive |  | MutEx(DS1,DS2,DS3,DS4) | 500 | EA 1 | YES | BLDG | Anchorage failure. | Anchorage failure & Equipment damaged beyond repair. | Motor damaged but anchorage is OK. | Equipment damaged beyond repair but anchorage is OK. |  | 0.35 | 0.15 | 0.25 | 0.25 |  | By User | By User | By User | By User |  | User to Calculate | User to Calculate | User to Calculate | User to Calculate |  | User to Calculate | User to Calculate | User to Calculate | User to Calculate |  | By User | By User | By User | By User |  | NO | NO | Average | Average | Superior | Superior | Repair anchorage and concrete pad and remount equipment. | Replace equipment including attached utilities in addition to repairing anchorage and concrete pad. | Repair Motor - Anchorage and Concrete do not require repair. | Replace and install equipment including new anchorage if anchorage is post-installed. |  | NO | YES | NO | YES |  | NO | NO | NO | NO |  | Not Applicable | Not Applicable | Not Applicable | Not Applicable |  | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 |  |  | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 |  |  | NO | NO | NO | NO |  | 0% | 0% | 0% | 0% |  | 0 | 0 | 0 | 0 |  | User to provide median demand and dispersion values. The values listed are default PACT values and do not represent the response of this component. | Not Given | By User | By User | Not Given | D3032.011a-DS1-1.JPG | none | none | none |  | No | None | YES
D3032.013g | D3032.013g | Compressor - Capacity: Small medical quality air supply - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only | Costing is per unit. | Normal - Designed for seismic loads but no special seismic certification | Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints | Each | Each | Peak Floor Acceleration | g | 2 | DS1 | DS2 |  |  |  | Mutually Exclusive | Mutually Exclusive |  |  |  | MutEx(DS1,DS2) | 501 | EA 1 | YES | BLDG | Anchorage failure. | Anchorage failure & Equipment damaged beyond repair. |  |  |  | 0.7 | 0.3 |  |  |  | By User | By User |  |  |  | User to Calculate | User to Calculate |  |  |  | User to Calculate | User to Calculate |  |  |  | By User | By User |  |  |  | NO | NO | Average | Average | Superior | Superior | Repair anchorage and concrete pad and remount equipment. | Replace equipment including attached utilities in addition to repairing anchorage and concrete pad. |  |  |  | NO | YES |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | NO |  |  |  | 0% | 0% |  |  |  | 0 | 0 |  |  |  | User to provide median demand and dispersion values. The values listed are default PACT values and do not represent the response of this component. | Not Given | By User | By User | Not Given | D3032.011a-DS1-1.JPG | none |  |  |  | No | None | YES
D3032.013h | D3032.013h | Compressor - Capacity: Small medical quality air supply - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only | Costing is per unit. | Normal - Designed for seismic loads but no special seismic certification | Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints | Each | Each | Peak Floor Acceleration | g | 2 | DS1 | DS2 |  |  |  | Mutually Exclusive | Mutually Exclusive |  |  |  | MutEx(DS1,DS2) | 502 | EA 1 | YES | BLDG | Equipment does not function but anchorage is OK. Motor is damaged. | Equipment does not function but anchorage is OK. Equipment damaged beyond repair. |  |  |  | 0.5 | 0.5 |  |  |  | 1.84 | 1.84 |  |  |  | 0.6 | 0.6 |  |  |  | 0.1 | 0.1 |  |  |  | 0.6 | 0.6 |  |  |  | NO | NO | Average | Average | Superior | Superior | Repair motor. | Replace equipment. |  |  |  | NO | YES |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | NO |  |  |  | 0% | 0% |  |  |  | 0 | 0 |  |  |  | None | Not Given | By User | By User | Not Given | D3032.011a-DS1-1.JPG | none |  |  |  | No | None | YES
D3032.013i | D3032.013i | Compressor - Capacity: Small medical quality air supply - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | Costing is per unit. | Normal - Designed for seismic loads but no special seismic certification | Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints | Each | Each | Peak Floor Acceleration | g | 4 | DS1 | DS2 | DS3 | DS4 |  | Mutually Exclusive | Mutually Exclusive | Mutually Exclusive | Mutually Exclusive |  | MutEx(DS1,DS2,DS3,DS4) | 503 | EA 1 | YES | BLDG | Anchorage failure. | Anchorage failure & Equipment damaged beyond repair. | Motor damaged but anchorage is OK. | Equipment damaged beyond repair but anchorage is OK. |  | 0.35 | 0.15 | 0.25 | 0.25 |  | By User | By User | By User | By User |  | User to Calculate | User to Calculate | User to Calculate | User to Calculate |  | User to Calculate | User to Calculate | User to Calculate | User to Calculate |  | By User | By User | By User | By User |  | NO | NO | Average | Average | Superior | Superior | Repair anchorage and concrete pad and remount equipment. | Replace equipment including attached utilities in addition to repairing anchorage and concrete pad. | Repair Motor - Anchorage and Concrete do not require repair. | Replace and install equipment including new anchorage if anchorage is post-installed. |  | NO | YES | NO | YES |  | NO | NO | NO | NO |  | Not Applicable | Not Applicable | Not Applicable | Not Applicable |  | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 |  |  | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 |  |  | NO | NO | NO | NO |  | 0% | 0% | 0% | 0% |  | 0 | 0 | 0 | 0 |  | User to provide median demand and dispersion values. The values listed are default PACT values and do not represent the response of this component. | Not Given | By User | By User | Not Given | D3032.011a-DS1-1.JPG | none | none | none |  | No | None | YES
D3032.013j | D3032.013j | Compressor - Capacity: Large medical quality air supply - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only | Costing is per unit. | Normal - Designed for seismic loads but no special seismic certification | Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints | Each | Each | Peak Floor Acceleration | g | 2 | DS1 | DS2 |  |  |  | Mutually Exclusive | Mutually Exclusive |  |  |  | MutEx(DS1,DS2) | 504 | EA 1 | YES | BLDG | Anchorage failure. | Anchorage failure & Equipment damaged beyond repair. |  |  |  | 0.7 | 0.3 |  |  |  | By User | By User |  |  |  | User to Calculate | User to Calculate |  |  |  | User to Calculate | User to Calculate |  |  |  | By User | By User |  |  |  | NO | NO | Average | Average | Superior | Superior | Repair anchorage and concrete pad and remount equipment. | Replace equipment including attached utilities in addition to repairing anchorage and concrete pad. |  |  |  | NO | YES |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | NO |  |  |  | 0% | 0% |  |  |  | 0 | 0 |  |  |  | User to provide median demand and dispersion values. The values listed are default PACT values and do not represent the response of this component. | Not Given | By User | By User | Not Given | D3032.011a-DS1-1.JPG | none |  |  |  | No | None | YES
D3032.013k | D3032.013k | Compressor - Capacity: Large medical quality air supply - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only | Costing is per unit. | Normal - Designed for seismic loads but no special seismic certification | Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints | Each | Each | Peak Floor Acceleration | g | 2 | DS1 | DS2 |  |  |  | Mutually Exclusive | Mutually Exclusive |  |  |  | MutEx(DS1,DS2) | 505 | EA 1 | YES | BLDG | Equipment does not function but anchorage is OK. Motor is damaged. | Equipment does not function but anchorage is OK. Equipment damaged beyond repair. |  |  |  | 0.5 | 0.5 |  |  |  | 1.84 | 1.84 |  |  |  | 0.6 | 0.6 |  |  |  | 0.1 | 0.1 |  |  |  | 0.6 | 0.6 |  |  |  | NO | NO | Average | Average | Superior | Superior | Repair motor. | Replace equipment. |  |  |  | NO | YES |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | NO |  |  |  | 0% | 0% |  |  |  | 0 | 0 |  |  |  | None | Not Given | By User | By User | Not Given | D3032.011a-DS1-1.JPG | none |  |  |  | No | None | YES
D3032.013l | D3032.013l | Compressor - Capacity: Large medical quality air supply - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | Costing is per unit. | Normal - Designed for seismic loads but no special seismic certification | Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints | Each | Each | Peak Floor Acceleration | g | 4 | DS1 | DS2 | DS3 | DS4 |  | Mutually Exclusive | Mutually Exclusive | Mutually Exclusive | Mutually Exclusive |  | MutEx(DS1,DS2,DS3,DS4) | 506 | EA 1 | YES | BLDG | Anchorage failure. | Anchorage failure & Equipment damaged beyond repair. | Motor damaged but anchorage is OK. | Equipment damaged beyond repair but anchorage is OK. |  | 0.35 | 0.15 | 0.25 | 0.25 |  | By User | By User | By User | By User |  | User to Calculate | User to Calculate | User to Calculate | User to Calculate |  | User to Calculate | User to Calculate | User to Calculate | User to Calculate |  | By User | By User | By User | By User |  | NO | NO | Average | Average | Superior | Superior | Repair anchorage and concrete pad and remount equipment. | Replace equipment including attached utilities in addition to repairing anchorage and concrete pad. | Repair Motor - Anchorage and Concrete do not require repair. | Replace and install equipment including new anchorage if anchorage is post-installed. |  | NO | YES | NO | YES |  | NO | NO | NO | NO |  | Not Applicable | Not Applicable | Not Applicable | Not Applicable |  | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 |  |  | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 |  |  | NO | NO | NO | NO |  | 0% | 0% | 0% | 0% |  | 0 | 0 | 0 | 0 |  | User to provide median demand and dispersion values. The values listed are default PACT values and do not represent the response of this component. | Not Given | By User | By User | Not Given | D3032.011a-DS1-1.JPG | none | none | none |  | No | None | YES
D3041.001a | D3041.001a | HVAC Fan In Line Fan, Fan independently supported and vibration isolators, SDC A or B | Costing per 10 units | Normal | Normal - SDC A or B | Each | Each | Peak Floor Acceleration | g | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 507 | EA 10 | NO | NO | Bellows fails at fans. | Fan dislodges from isolators and drops. |  |  |  | 1 | 1 |  |  |  | 1.92 | 2.4 |  |  |  | Not Specified | Not Specified |  |  |  | Not Specified | Not Specified |  |  |  | 0.5 | 0.5 |  |  |  | NO | NO | Marginal | Superior | Marginal | Marginal | Replace failed bellows. | Replace fan, isolators and section of ducting to which fan is connected. |  |  |  | NO | NO |  |  |  | NO | YES |  |  |  | Not Applicable | 10 SF |  |  |  | 0% | 0 | 10% | 0.5 | [6 empty] | 0% | 0 | 5% | 0.5 | [6 empty] | NO | NO |  |  |  | 0% | 0% |  |  |  | 0 | 0 |  |  |  | One failure is expected per 10 units. | Not Given | By User | By User | Not Given | none | none |  |  |  | Yes | None | YES
D3041.001b | D3041.001b | HVAC Fan In Line Fan, Fan independently supported and vibration isolators, SDC C | Costing per 10 units | Normal | Normal - SDC C | Each | Each | Peak Floor Acceleration | g | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 508 | EA 10 | NO | NO | Bellows fails at fans. | Fan dislodges from isolators and drops. |  |  |  | 1 | 1 |  |  |  | 1.92 | 2.4 |  |  |  | Not Specified | Not Specified |  |  |  | Not Specified | Not Specified |  |  |  | 0.5 | 0.5 |  |  |  | NO | NO | Marginal | Superior | Marginal | Marginal | Replace failed bellows. | Replace fan, isolators and section of ducting to which fan is connected. |  |  |  | NO | NO |  |  |  | NO | YES |  |  |  | Not Applicable | 10 SF |  |  |  | 0% | 0 | 10% | 0.5 | [6 empty] | 0% | 0 | 5% | 0.5 | [6 empty] | NO | NO |  |  |  | 0% | 0% |  |  |  | 0 | 0 |  |  |  | One failure is expected per 10 units. | Not Given | By User | By User | Not Given | none | none |  |  |  | Yes | None | YES
D3041.001c | D3041.001c | HVAC Fan In Line Fan, Fan independently supported and vibration isolators, SDC D, E, F | Costing per 10 units | Normal | Normal - SDC D, E or F | Each | Each | Peak Floor Acceleration | g | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 509 | EA 10 | NO | NO | Bellows fails at fans. | Fan dislodges from isolators and drops. |  |  |  | 1 | 1 |  |  |  | 2.25 | 2.6 |  |  |  | Not Specified | Not Specified |  |  |  | Not Specified | Not Specified |  |  |  | 0.4 | 0.4 |  |  |  | NO | NO | Marginal | Superior | Marginal | Marginal | Replace failed bellows. | Replace fan, isolators and section of ducting to which fan is connected. |  |  |  | NO | NO |  |  |  | NO | YES |  |  |  | Not Applicable | 10 SF |  |  |  | 0% | 0 | 10% | 0.5 | [6 empty] | 0% | 0 | 5% | 0.5 | [6 empty] | NO | NO |  |  |  | 0% | 0% |  |  |  | 0 | 0 |  |  |  | One failure is expected per 10 units. | Not Given | By User | By User | Not Given | none | none |  |  |  | Yes | None | YES
D3041.001d | D3041.001d | HVAC Fan In Line Fan, Fan independently supported and vibration isolators, SDC D, E, F (OSHPD or sim) | Costing per 10 units | Special Regulation (e.g. OSHPD) for HVAC installations | Special Regulation (e.g. OSHPD) for HVAC installations - SDC D, E or F (high seismic design) | Each | Each | Peak Floor Acceleration | g | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 510 | EA 10 | NO | NO | Bellows fails at fans. | Fan dislodges from isolators and drops. |  |  |  | 1 | 1 |  |  |  | 2.25 | 2.6 |  |  |  | Not Specified | Not Specified |  |  |  | Not Specified | Not Specified |  |  |  | 0.4 | 0.4 |  |  |  | NO | NO | Marginal | Superior | Marginal | Marginal | Replace failed bellows. | Replace fan, isolators and section of ducting to which fan is connected. |  |  |  | NO | NO |  |  |  | NO | YES |  |  |  | Not Applicable | 10 SF |  |  |  | 0% | 0 | 10% | 0.5 | [6 empty] | 0% | 0 | 5% | 0.5 | [6 empty] | NO | NO |  |  |  | 0% | 0% |  |  |  | 0 | 0 |  |  |  | One failure is expected per 10 units. | Not Given | By User | By User | Not Given | none | none |  |  |  | Yes | None | YES
D3041.002a | D3041.002a | HVAC Fan In Line Fan, Fan independently supported but not on vibration isolators, SDC A or B | Costing per 10 units | Normal | Normal - SDC A or B | Each | Each | Peak Floor Acceleration | g | 1 | DS1 |  |  |  |  | Sequential |  |  |  |  | Seq(DS1) | 511 | EA 10 | NO | NO | Bellows fails at fans. |  |  |  |  | 1 |  |  |  |  | 1.9 |  |  |  |  | Not Specified |  |  |  |  | Not Specified |  |  |  |  | 0.4 |  |  |  |  | NO | NO | Marginal | Superior | Marginal | Marginal | Replace failed bellows. |  |  |  |  | NO |  |  |  |  | NO |  |  |  |  | Not Applicable |  |  |  |  | 0% | 0 | [8 empty] | 0% | 0 | [8 empty] | NO |  |  |  |  | 0% |  |  |  |  | 0 |  |  |  |  | One failure is expected per 10 units. | Not Given | By User | By User | Not Given | none |  |  |  |  | Yes | None | YES
D3041.002b | D3041.002b | HVAC Fan In Line Fan, Fan independently supported but not on vibration isolators, SDC C | Costing per 10 units | Normal | Normal - SDC C | Each | Each | Peak Floor Acceleration | g | 1 | DS1 |  |  |  |  | Sequential |  |  |  |  | Seq(DS1) | 512 | EA 10 | NO | NO | Bellows fails at fans. |  |  |  |  | 1 |  |  |  |  | 1.9 |  |  |  |  | Not Specified |  |  |  |  | Not Specified |  |  |  |  | 0.4 |  |  |  |  | NO | NO | Marginal | Superior | Marginal | Marginal | Replace failed bellows. |  |  |  |  | NO |  |  |  |  | NO |  |  |  |  | Not Applicable |  |  |  |  | 0% | 0 | [8 empty] | 0% | 0 | [8 empty] | NO |  |  |  |  | 0% |  |  |  |  | 0 |  |  |  |  | One failure is expected per 10 units. | Not Given | By User | By User | Not Given | none |  |  |  |  | Yes | None | YES
D3041.002c | D3041.002c | HVAC Fan In Line Fan, Fan independently supported but not on vibration isolators, SDC D, E, F | Costing per 10 units | Normal | Normal - SDC D, E or F | Each | Each | Peak Floor Acceleration | g | 1 | DS1 |  |  |  |  | Sequential |  |  |  |  | Seq(DS1) | 513 | EA 10 | NO | NO | Bellows fails at fans. |  |  |  |  | 1 |  |  |  |  | 2.25 |  |  |  |  | Not Specified |  |  |  |  | Not Specified |  |  |  |  | 0.4 |  |  |  |  | NO | NO | Marginal | Superior | Marginal | Marginal | Replace failed bellows. |  |  |  |  | NO |  |  |  |  | NO |  |  |  |  | Not Applicable |  |  |  |  | 0% | 0 | [8 empty] | 0% | 0 | [8 empty] | NO |  |  |  |  | 0% |  |  |  |  | 0 |  |  |  |  | One failure is expected per 10 units. | Not Given | By User | By User | Not Given | none |  |  |  |  | Yes | None | YES
D3041.002d | D3041.002d | HVAC Fan In Line Fan, Fan independently supported but not on vibration isolators, SDC D, E, F (OSHPD or sim) | Costing per 10 units | Special Regulation (e.g. OSHPD) for HVAC installations | Special Regulation (e.g. OSHPD) for HVAC installations - SDC D, E or F (high seismic design) | Each | Each | Peak Floor Acceleration | g | 1 | DS1 |  |  |  |  | Sequential |  |  |  |  | Seq(DS1) | 514 | EA 10 | NO | NO | Bellows fails at fans. |  |  |  |  | 1 |  |  |  |  | 2.25 |  |  |  |  | Not Specified |  |  |  |  | Not Specified |  |  |  |  | 0.4 |  |  |  |  | NO | NO | Marginal | Superior | Marginal | Marginal | Replace failed bellows. |  |  |  |  | NO |  |  |  |  | NO |  |  |  |  | Not Applicable |  |  |  |  | 0% | 0 | [8 empty] | 0% | 0 | [8 empty] | NO |  |  |  |  | 0% |  |  |  |  | 0 |  |  |  |  | One failure is expected per 10 units. | Not Given | By User | By User | Not Given | none |  |  |  |  | Yes | None | YES
D3041.011a | D3041.011a | HVAC Galvanized Sheet Metal Ducting less than 6 sq. ft in cross sectional area, SDC A or B | Costing based upon 1000 ft segments of duct | Normal | Normal - SDC A or B | Each | Each | Peak Floor Acceleration | g | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 515 | LF 1000 | NO | NO | Individual supports fail and duct sags - 1 failed support per 1000 feet of ducting. | Several adjacent supports fail and sections of ducting fall - 60 feet of ducting fail and fall per 1000 foot of ducting. |  |  |  | 1 | 1 |  |  |  | 1.5 | 2.25 |  |  |  | Not Specified | Not Specified |  |  |  | Not Specified | Not Specified |  |  |  | 0.4 | 0.4 |  |  |  | NO | NO | Marginal | Superior | Marginal | Marginal | Replace failed supports and repair ducting in vicinity of failed supports. | Replace sections of failed ducting and supports. |  |  |  | NO | NO |  |  |  | NO | YES |  |  |  | Not Applicable | 15 SF |  |  |  | 0% | 0 | 5% | 0.5 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | NO |  |  |  | 0% | 0% |  |  |  | 0 | 0 |  |  |  | None | Not Given | By User | By User | Not Given | none | none |  |  |  | Yes | None | YES
D3041.011b | D3041.011b | HVAC Galvanized Sheet Metal Ducting less than 6 sq. ft in cross sectional area, SDC C | Costing based upon 1000 ft segments of duct | Normal | Normal - SDC C | Each | Each | Peak Floor Acceleration | g | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 516 | LF 1000 | NO | NO | Individual supports fail and duct sags - 1 failed support per 1000 feet of ducting. | Several adjacent supports fail and sections of ducting fall - 60 feet of ducting fail and fall per 1000 foot of ducting. |  |  |  | 1 | 1 |  |  |  | 1.5 | 2.25 |  |  |  | Not Specified | Not Specified |  |  |  | Not Specified | Not Specified |  |  |  | 0.4 | 0.4 |  |  |  | NO | NO | Marginal | Superior | Marginal | Marginal | Replace failed supports and repair ducting in vicinity of failed supports. | Replace sections of failed ducting and supports. |  |  |  | NO | NO |  |  |  | NO | YES |  |  |  | Not Applicable | 15 SF |  |  |  | 0% | 0 | 5% | 0.5 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | NO |  |  |  | 0% | 0% |  |  |  | 0 | 0 |  |  |  | None | Not Given | By User | By User | Not Given | none | none |  |  |  | Yes | None | YES
D3041.011c | D3041.011c | HVAC Galvanized Sheet Metal Ducting less than 6 sq. ft in cross sectional area, SDC D, E, or F | Costing based upon 1000 ft segments of duct | Normal | Normal - SDC D, E or F | Each | Each | Peak Floor Acceleration | g | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 517 | LF 1000 | NO | NO | Individual supports fail and duct sags - 1 failed support per 1000 feet of ducting. | Several adjacent supports fail and sections of ducting fall - 60 feet of ducting fail and fall per 1000 foot of ducting. |  |  |  | 1 | 1 |  |  |  | 1.5 | 2.25 |  |  |  | Not Specified | Not Specified |  |  |  | Not Specified | Not Specified |  |  |  | 0.4 | 0.4 |  |  |  | NO | NO | Marginal | Superior | Marginal | Marginal | Replace failed supports and repair ducting in vicinity of failed supports. | Replace sections of failed ducting and supports. |  |  |  | NO | NO |  |  |  | NO | YES |  |  |  | Not Applicable | 15 SF |  |  |  | 0% | 0 | 5% | 0.5 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | NO |  |  |  | 0% | 0% |  |  |  | 0 | 0 |  |  |  | None | Not Given | By User | By User | Not Given | none | none |  |  |  | Yes | None | YES
D3041.011d | D3041.011d | HVAC Galvanized Sheet Metal Ducting less than 6 sq. ft in cross sectional area, SDC D, E, or F (OSHPD or sim) | Costing based upon 1000 ft segments of duct | Special Regulation (e.g. OSHPD) for HVAC ducting installation | Special Regulation (e.g. OSHPD) for HVAC ducting installation - SDC D, E or F (high seismic design) | Each | Each | Peak Floor Acceleration | g | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 518 | LF 1000 | NO | NO | Individual supports fail and duct sags - 1 failed support per 1000 feet of ducting. | Several adjacent supports fail and sections of ducting fall - 60 feet of ducting fail and fall per 1000 foot of ducting. |  |  |  | 1 | 1 |  |  |  | 1.5 | 2.25 |  |  |  | Not Specified | Not Specified |  |  |  | Not Specified | Not Specified |  |  |  | 0.4 | 0.4 |  |  |  | NO | NO | Marginal | Superior | Marginal | Marginal | Replace failed supports and repair ducting in vicinity of failed supports. | Replace sections of failed ducting and supports. |  |  |  | NO | NO |  |  |  | NO | YES |  |  |  | Not Applicable | 15 SF |  |  |  | 0% | 0 | 5% | 0.5 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | NO |  |  |  | 0% | 0% |  |  |  | 0 | 0 |  |  |  | None | Not Given | By User | By User | Not Given | none | none |  |  |  | Yes | None | YES
D3041.012a | D3041.012a | HVAC Galvanized Sheet Metal Ducting - 6 sq. ft cross sectional area or greater, SDC A or B | Costing based upon 1000 ft segments of duct | Normal | Normal - SDC A or B | Each | Each | Peak Floor Acceleration | g | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 519 | LF 1000 | NO | NO | Individual supports fail and duct sags - 1 failed support per 1000 feet of ducting. | Several adjacent supports fail and sections of ducting fall - 60 feet of ducting fail and fall per 1000 foot of ducting. |  |  |  | 1 | 1 |  |  |  | 1.5 | 2.25 |  |  |  | Not Specified | Not Specified |  |  |  | Not Specified | Not Specified |  |  |  | 0.4 | 0.4 |  |  |  | NO | NO | Marginal | Superior | Marginal | Marginal | Replace failed supports and repair ducting in vicinity of failed supports. | Replace sections of failed ducting and supports. |  |  |  | NO | NO |  |  |  | NO | YES |  |  |  | Not Applicable | 50 SF |  |  |  | 0% | 0 | 10% | 0.5 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | NO |  |  |  | 0% | 0% |  |  |  | 0 | 0 |  |  |  | None | Not Given | By User | By User | Not Given | none | none |  |  |  | Yes | None | YES
D3041.012b | D3041.012b | HVAC Galvanized Sheet Metal Ducting - 6 sq. ft cross sectional area or greater, SDC C | Costing based upon 1000 ft segments of duct | Normal | Normal - SDC C | Each | Each | Peak Floor Acceleration | g | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 520 | LF 1000 | NO | NO | Individual supports fail and duct sags - 1 failed support per 1000 feet of ducting. | Several adjacent supports fail and sections of ducting fall - 60 feet of ducting fail and fall per 1000 foot of ducting. |  |  |  | 1 | 1 |  |  |  | 1.5 | 2.25 |  |  |  | Not Specified | Not Specified |  |  |  | Not Specified | Not Specified |  |  |  | 0.4 | 0.4 |  |  |  | NO | NO | Marginal | Superior | Marginal | Marginal | Replace failed supports and repair ducting in vicinity of failed supports. | Replace sections of failed ducting and supports. |  |  |  | NO | NO |  |  |  | NO | YES |  |  |  | Not Applicable | 50 SF |  |  |  | 0% | 0 | 10% | 0.5 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | NO |  |  |  | 0% | 0% |  |  |  | 0 | 0 |  |  |  | None | Not Given | By User | By User | Not Given | none | none |  |  |  | Yes | None | YES
D3041.012c | D3041.012c | HVAC Galvanized Sheet Metal Ducting - 6 sq. ft cross sectional area or greater, SDC D, E, or F | Costing based upon 1000 ft segments of duct | Normal | Normal - SDC D, E or F | Each | Each | Peak Floor Acceleration | g | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 521 | LF 1000 | NO | NO | Individual supports fail and duct sags - 1 failed support per 1000 feet of ducting. | Several adjacent supports fail and sections of ducting fall - 60 feet of ducting fail and fall per 1000 foot of ducting. |  |  |  | 1 | 1 |  |  |  | 3.75 | 4.5 |  |  |  | Not Specified | Not Specified |  |  |  | Not Specified | Not Specified |  |  |  | 0.4 | 0.4 |  |  |  | NO | NO | Marginal | Superior | Marginal | Marginal | Replace failed supports and repair ducting in vicinity of failed supports. | Replace sections of failed ducting and supports. |  |  |  | NO | NO |  |  |  | NO | YES |  |  |  | Not Applicable | 50 SF |  |  |  | 0% | 0 | 10% | 0.5 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | NO |  |  |  | 0% | 0% |  |  |  | 0 | 0 |  |  |  | None | Not Given | By User | By User | Not Given | none | none |  |  |  | Yes | None | YES
D3041.012d | D3041.012d | HVAC Galvanized Sheet Metal Ducting - 6 sq. ft cross sectional area or greater, SDC D, E, or F (OSHPD or sim) | Costing based upon 1000 ft segments of duct | Special Regulation (e.g. OSHPD) for HVAC ducting installation | Special Regulation (e.g. OSHPD) for HVAC ducting installation - SDC D, E or F (high seismic design) | Each | Each | Peak Floor Acceleration | g | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 522 | LF 1000 | NO | NO | Individual supports fail and duct sags - 1 failed support per 1000 feet of ducting. | Several adjacent supports fail and sections of ducting fall - 60 feet of ducting fail and fall per 1000 foot of ducting. |  |  |  | 1 | 1 |  |  |  | 3.75 | 4.5 |  |  |  | Not Specified | Not Specified |  |  |  | Not Specified | Not Specified |  |  |  | 0.4 | 0.4 |  |  |  | NO | NO | Marginal | Superior | Marginal | Marginal | Replace failed supports and repair ducting in vicinity of failed supports. | Replace sections of failed ducting and supports. |  |  |  | NO | NO |  |  |  | NO | YES |  |  |  | Not Applicable | 50 SF |  |  |  | 0% | 0 | 10% | 0.5 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | NO |  |  |  | 0% | 0% |  |  |  | 0 | 0 |  |  |  | None | Not Given | By User | By User | Not Given | none | none |  |  |  | Yes | None | YES
D3041.021a | D3041.021a | HVAC Stainless Steel Ducting less than 6 sq. ft in cross sectional area, SDC A or B | Costing based upon 1000 ft segments of duct | Normal | Normal - SDC A or B | Each | Each | Peak Floor Acceleration | g | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 523 | LF 1000 | NO | NO | Individual supports fail and duct sags - 1 failed support per 1000 feet of ducting. | Several adjacent supports fail and sections of ducting fall - 60 feet of ducting fail and fall per 1000 foot of ducting. |  |  |  | 1 | 1 |  |  |  | 1.5 | 2.25 |  |  |  | Not Specified | Not Specified |  |  |  | Not Specified | Not Specified |  |  |  | 0.4 | 0.4 |  |  |  | NO | NO | Marginal | Superior | Marginal | Marginal | Replace failed supports and repair ducting in vicinity of failed supports. | Replace sections of failed ducting and supports. |  |  |  | NO | NO |  |  |  | NO | YES |  |  |  | Not Applicable | 15 SF |  |  |  | 0% | 0 | 5% | 0.5 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | NO |  |  |  | 0% | 0% |  |  |  | 0 | 0 |  |  |  | None | Not Given | By User | By User | Not Given | none | none |  |  |  | Yes | None | YES
D3041.021b | D3041.021b | HVAC Stainless Steel Ducting less than 6 sq. ft in cross sectional area, SDC C | Costing based upon 1000 ft segments of duct | Normal | Normal - SDC C | Each | Each | Peak Floor Acceleration | g | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 524 | LF 1000 | NO | NO | Individual supports fail and duct sags - 1 failed support per 1000 feet of ducting. | Several adjacent supports fail and sections of ducting fall - 60 feet of ducting fail and fall per 1000 foot of ducting. |  |  |  | 1 | 1 |  |  |  | 1.5 | 2.25 |  |  |  | Not Specified | Not Specified |  |  |  | Not Specified | Not Specified |  |  |  | 0.4 | 0.4 |  |  |  | NO | NO | Marginal | Superior | Marginal | Marginal | Replace failed supports and repair ducting in vicinity of failed supports. | Replace sections of failed ducting and supports. |  |  |  | NO | NO |  |  |  | NO | YES |  |  |  | Not Applicable | 15 SF |  |  |  | 0% | 0 | 5% | 0.5 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | NO |  |  |  | 0% | 0% |  |  |  | 0 | 0 |  |  |  | None | Not Given | By User | By User | Not Given | none | none |  |  |  | Yes | None | YES
D3041.021c | D3041.021c | HVAC Stainless Steel Ducting less than 6 sq. ft in cross sectional area, SDC D, E, or F | Costing based upon 1000 ft segments of duct | Normal | Normal - SDC D, E or F | Each | Each | Peak Floor Acceleration | g | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 525 | LF 1000 | NO | NO | Individual supports fail and duct sags - 1 failed support per 1000 feet of ducting. | Several adjacent supports fail and sections of ducting fall - 60 feet of ducting fail and fall per 1000 foot of ducting. |  |  |  | 1 | 1 |  |  |  | 1.5 | 2.25 |  |  |  | Not Specified | Not Specified |  |  |  | Not Specified | Not Specified |  |  |  | 0.4 | 0.4 |  |  |  | NO | NO | Marginal | Superior | Marginal | Marginal | Replace failed supports and repair ducting in vicinity of failed supports. | Replace sections of failed ducting and supports. |  |  |  | NO | NO |  |  |  | NO | YES |  |  |  | Not Applicable | 15 SF |  |  |  | 0% | 0 | 5% | 0.5 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | NO |  |  |  | 0% | 0% |  |  |  | 0 | 0 |  |  |  | None | Not Given | By User | By User | Not Given | none | none |  |  |  | Yes | None | YES
D3041.021d | D3041.021d | HVAC Stainless Steel Ducting less than 6 sq. ft in cross sectional area, SDC D, E, or F (OSHPD or sim) | Costing based upon 1000 ft segments of duct | Special Regulation (e.g. OSHPD) for HVAC ducting installation | Special Regulation (e.g. OSHPD) for HVAC ducting installation - SDC D, E or F (high seismic design) | Each | Each | Peak Floor Acceleration | g | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 526 | LF 1000 | NO | NO | Individual supports fail and duct sags - 1 failed support per 1000 feet of ducting. | Several adjacent supports fail and sections of ducting fall - 60 feet of ducting fail and fall per 1000 foot of ducting. |  |  |  | 1 | 1 |  |  |  | 1.5 | 2.25 |  |  |  | Not Specified | Not Specified |  |  |  | Not Specified | Not Specified |  |  |  | 0.4 | 0.4 |  |  |  | NO | NO | Marginal | Superior | Marginal | Marginal | Replace failed supports and repair ducting in vicinity of failed supports. | Replace sections of failed ducting and supports. |  |  |  | NO | NO |  |  |  | NO | YES |  |  |  | Not Applicable | 15 SF |  |  |  | 0% | 0 | 5% | 0.5 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | NO |  |  |  | 0% | 0% |  |  |  | 0 | 0 |  |  |  | None | Not Given | By User | By User | Not Given | none | none |  |  |  | Yes | None | YES
D3041.022a | D3041.022a | HVAC Stainless Steel Ducting - 6 sq. ft cross sectional area or greater, SDC A or B | Costing based upon 1000 ft segments of duct | Normal | Normal - SDC A or B | Each | Each | Peak Floor Acceleration | g | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 527 | LF 1000 | NO | NO | Individual supports fail and duct sags - 1 failed support per 1000 feet of ducting. | Several adjacent supports fail and sections of ducting fall - 60 feet of ducting fail and fall per 1000 foot of ducting. |  |  |  | 1 | 1 |  |  |  | 1.5 | 2.25 |  |  |  | Not Specified | Not Specified |  |  |  | Not Specified | Not Specified |  |  |  | 0.4 | 0.4 |  |  |  | NO | NO | Marginal | Superior | Marginal | Marginal | Replace failed supports and repair ducting in vicinity of failed supports. | Replace sections of failed ducting and supports. |  |  |  | NO | NO |  |  |  | NO | YES |  |  |  | Not Applicable | 50 SF |  |  |  | 0% | 0 | 10% | 0.5 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | NO |  |  |  | 0% | 0% |  |  |  | 0 | 0 |  |  |  | None | Not Given | By User | By User | Not Given | none | none |  |  |  | Yes | None | YES
D3041.022b | D3041.022b | HVAC Stainless Steel Ducting - 6 sq. ft cross sectional area or greater, SDC C | Costing based upon 1000 ft segments of duct | Normal | Normal - SDC C | Each | Each | Peak Floor Acceleration | g | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 528 | LF 1000 | NO | NO | Individual supports fail and duct sags - 1 failed support per 1000 feet of ducting. | Several adjacent supports fail and sections of ducting fall - 60 feet of ducting fail and fall per 1000 foot of ducting. |  |  |  | 1 | 1 |  |  |  | 1.5 | 2.25 |  |  |  | Not Specified | Not Specified |  |  |  | Not Specified | Not Specified |  |  |  | 0.4 | 0.4 |  |  |  | NO | NO | Marginal | Superior | Marginal | Marginal | Replace failed supports and repair ducting in vicinity of failed supports. | Replace sections of failed ducting and supports. |  |  |  | NO | NO |  |  |  | NO | YES |  |  |  | Not Applicable | 50 SF |  |  |  | 0% | 0 | 10% | 0.5 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | NO |  |  |  | 0% | 0% |  |  |  | 0 | 0 |  |  |  | None | Not Given | By User | By User | Not Given | none | none |  |  |  | Yes | None | YES
D3041.022c | D3041.022c | HVAC Stainless Steel Ducting - 6 sq. ft cross sectional area or greater, SDC D, E, or F | Costing based upon 1000 ft segments of duct | Normal | Normal - SDC D, E or F | Each | Each | Peak Floor Acceleration | g | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 529 | LF 1000 | NO | NO | Individual supports fail and duct sags - 1 failed support per 1000 feet of ducting. | Several adjacent supports fail and sections of ducting fall - 60 feet of ducting fail and fall per 1000 foot of ducting. |  |  |  | 1 | 1 |  |  |  | 3.75 | 4.5 |  |  |  | Not Specified | Not Specified |  |  |  | Not Specified | Not Specified |  |  |  | 0.4 | 0.4 |  |  |  | NO | NO | Marginal | Superior | Marginal | Marginal | Replace failed supports and repair ducting in vicinity of failed supports. | Replace sections of failed ducting and supports. |  |  |  | NO | NO |  |  |  | NO | YES |  |  |  | Not Applicable | 50 SF |  |  |  | 0% | 0 | 10% | 0.5 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | NO |  |  |  | 0% | 0% |  |  |  | 0 | 0 |  |  |  | None | Not Given | By User | By User | Not Given | none | none |  |  |  | Yes | None | YES
D3041.022d | D3041.022d | HVAC Stainless Steel Ducting - 6 sq. ft cross sectional area or greater, SDC D, E, or F (OSHPD or sim) | Costing based upon 1000 ft segments of duct | Special Regulation (e.g. OSHPD) for HVAC ducting installation | Special Regulation (e.g. OSHPD) for HVAC ducting installation - SDC D, E or F (high seismic design) | Each | Each | Peak Floor Acceleration | g | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 530 | LF 1000 | NO | NO | Individual supports fail and duct sags - 1 failed support per 1000 feet of ducting. | Several adjacent supports fail and sections of ducting fall - 60 feet of ducting fail and fall per 1000 foot of ducting. |  |  |  | 1 | 1 |  |  |  | 3.75 | 4.5 |  |  |  | Not Specified | Not Specified |  |  |  | Not Specified | Not Specified |  |  |  | 0.4 | 0.4 |  |  |  | NO | NO | Marginal | Superior | Marginal | Marginal | Replace failed supports and repair ducting in vicinity of failed supports. | Replace sections of failed ducting and supports. |  |  |  | NO | NO |  |  |  | NO | YES |  |  |  | Not Applicable | 50 SF |  |  |  | 0% | 0 | 10% | 0.5 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | NO |  |  |  | 0% | 0% |  |  |  | 0 | 0 |  |  |  | None | Not Given | By User | By User | Not Given | none | none |  |  |  | Yes | None | YES
D3041.031a | D3041.031a | HVAC Drops / Diffusers in suspended ceilings - No independent safety wires, SDC A or B | Costing per 10 units, No independent safety wires | Normal | Normal - SDC A or B | Each | Each | Peak Floor Acceleration | g | 1 | DS1 |  |  |  |  | Sequential |  |  |  |  | Seq(DS1) | 531 | EA 10 | NO | NO | HVAC drops or diffusers dislodges and falls. |  |  |  |  | 1 |  |  |  |  | 1.3 |  |  |  |  | Not Specified |  |  |  |  | Not Specified |  |  |  |  | 0.4 |  |  |  |  | NO | NO | Marginal | Superior | Marginal | Marginal | Replace diffuser/drop and sections of ceiling and ducting in vicinity to which diffuser/drop is connected. |  |  |  |  | NO |  |  |  |  | YES |  |  |  |  | 4 SF |  |  |  |  | 10% | 0.5 | [8 empty] | 0% | 0 | [8 empty] | NO |  |  |  |  | 0% |  |  |  |  | 0 |  |  |  |  | One failure is expected per 10 units. | Not Given | By User | By User | Not Given | none |  |  |  |  | Yes | None | YES
D3041.031b | D3041.031b | HVAC Drops / Diffusers in suspended ceilings - No independent safety wires, SDC C | Costing per 10 units, No independent safety wires | Normal | Normal - SDC C | Each | Each | Peak Floor Acceleration | g | 1 | DS1 |  |  |  |  | Sequential |  |  |  |  | Seq(DS1) | 532 | EA 10 | NO | NO | HVAC drops or diffusers dislodges and falls. |  |  |  |  | 1 |  |  |  |  | 1.3 |  |  |  |  | Not Specified |  |  |  |  | Not Specified |  |  |  |  | 0.4 |  |  |  |  | NO | NO | Marginal | Superior | Marginal | Marginal | Replace diffuser/drop and sections of ceiling and ducting in vicinity to which diffuser/drop is connected. |  |  |  |  | NO |  |  |  |  | YES |  |  |  |  | 4 SF |  |  |  |  | 10% | 0.5 | [8 empty] | 0% | 0 | [8 empty] | NO |  |  |  |  | 0% |  |  |  |  | 0 |  |  |  |  | One failure is expected per 10 units. | Not Given | By User | By User | Not Given | none |  |  |  |  | Yes | None | YES
D3041.032a | D3041.032a | HVAC Drops / Diffusers without ceilings - supported by ducting only - No independent safety wires, SDC A or B | Costing per 10 units, unit supported by ducting only, no independent safety wires | Normal | Normal - SDC A or B | Each | Each | Peak Floor Acceleration | g | 1 | DS1 |  |  |  |  | Sequential |  |  |  |  | Seq(DS1) | 533 | EA 10 | NO | NO | HVAC drops or diffusers dislodges and falls. |  |  |  |  | 1 |  |  |  |  | 1.5 |  |  |  |  | Not Specified |  |  |  |  | Not Specified |  |  |  |  | 0.4 |  |  |  |  | NO | NO | Marginal | Superior | Marginal | Marginal | Replace diffuser/drop and sections of ceiling and ducting in vicinity to which diffuser/drop is connected. |  |  |  |  | NO |  |  |  |  | YES |  |  |  |  | 4 SF |  |  |  |  | 10% | 0.5 | [8 empty] | 0% | 0 | [8 empty] | NO |  |  |  |  | 0% |  |  |  |  | 0 |  |  |  |  | One failure is expected per 10 units. | Not Given | By User | By User | Not Given | none |  |  |  |  | Yes | None | YES
D3041.032b | D3041.032b | HVAC Drops / Diffusers without ceilings - supported by ducting only - No independent safety wires, SDC C | Costing per 10 units, unit supported by ducting only, no independent safety wires | Normal | Normal - SDC C | Each | Each | Peak Floor Acceleration | g | 1 | DS1 |  |  |  |  | Sequential |  |  |  |  | Seq(DS1) | 534 | EA 10 | NO | NO | HVAC drops or diffusers dislodges and falls. |  |  |  |  | 1 |  |  |  |  | 1.5 |  |  |  |  | Not Specified |  |  |  |  | Not Specified |  |  |  |  | 0.4 |  |  |  |  | NO | NO | Marginal | Superior | Marginal | Marginal | Replace diffuser/drop and sections of ceiling and ducting in vicinity to which diffuser/drop is connected. |  |  |  |  | NO |  |  |  |  | YES |  |  |  |  | 4 SF |  |  |  |  | 10% | 0.5 | [8 empty] | 0% | 0 | [8 empty] | NO |  |  |  |  | 0% |  |  |  |  | 0 |  |  |  |  | One failure is expected per 10 units. | Not Given | By User | By User | Not Given | none |  |  |  |  | Yes | None | YES
D3041.032c | D3041.032c | HVAC Drops / Diffusers without ceilings - supported by ducting only - No independent safety wires, SDC D, E, or F | Costing per 10 units, unit supported by ducting only, no independent safety wires | Normal | Normal - SDC D, E or F | Each | Each | Peak Floor Acceleration | g | 1 | DS1 |  |  |  |  | Sequential |  |  |  |  | Seq(DS1) | 535 | EA 10 | NO | NO | HVAC drops or diffusers dislodges and falls. |  |  |  |  | 1 |  |  |  |  | 1.5 |  |  |  |  | Not Specified |  |  |  |  | Not Specified |  |  |  |  | 0.4 |  |  |  |  | NO | NO | Marginal | Superior | Marginal | Marginal | Replace diffuser/drop and sections of ceiling and ducting in vicinity to which diffuser/drop is connected. |  |  |  |  | NO |  |  |  |  | YES |  |  |  |  | 4 SF |  |  |  |  | 10% | 0.5 | [8 empty] | 0% | 0 | [8 empty] | NO |  |  |  |  | 0% |  |  |  |  | 0 |  |  |  |  | One failure is expected per 10 units. | Not Given | By User | By User | Not Given | none |  |  |  |  | Yes | None | YES
D3041.032d | D3041.032d | HVAC Drops / Diffusers without ceilings - supported by ducting only - No independent safety wires, SDC D, E, or F (OSHPD or sim) | Costing per 10 units, unit supported by ducting only, no independent safety wires | Special Regulation (e.g. OSHPD) for HVAC Ducting Installation | Special Regulation (e.g. OSHPD) for HVAC Ducting Installation - SDC D, E or F (high seismic design) | Each | Each | Peak Floor Acceleration | g | 1 | DS1 |  |  |  |  | Sequential |  |  |  |  | Seq(DS1) | 536 | EA 10 | NO | NO | HVAC drops or diffusers dislodges and falls. |  |  |  |  | 1 |  |  |  |  | 1.5 |  |  |  |  | Not Specified |  |  |  |  | Not Specified |  |  |  |  | 0.4 |  |  |  |  | NO | NO | Marginal | Superior | Marginal | Marginal | Replace diffuser/drop and sections of ceiling and ducting in vicinity to which diffuser/drop is connected. |  |  |  |  | NO |  |  |  |  | YES |  |  |  |  | 4 SF |  |  |  |  | 10% | 0.5 | [8 empty] | 0% | 0 | [8 empty] | NO |  |  |  |  | 0% |  |  |  |  | 0 |  |  |  |  | One failure is expected per 10 units. | Not Given | By User | By User | Not Given | none |  |  |  |  | Yes | None | YES
D3041.041a | D3041.041a | Variable Air Volume (VAV) box with in-line coil, SDC A or B | Costing per 10 units | Normal | Normal - SDC A or B | Each | Each | Peak Floor Acceleration | g | 1 | DS1 |  |  |  |  | Sequential |  |  |  |  | Seq(DS1) | 537 | EA 10 | NO | NO | Coil damages connection to plumbing. Leakage of hot water. |  |  |  |  | 1 |  |  |  |  | 1.9 |  |  |  |  | Not Specified |  |  |  |  | Not Specified |  |  |  |  | 0.4 |  |  |  |  | NO | NO | Marginal | Superior | Marginal | Marginal | Replace coil and cleanup water damage. |  |  |  |  | NO |  |  |  |  | NO |  |  |  |  | Not Applicable |  |  |  |  | 0% | 0 | [8 empty] | 0% | 0 | [8 empty] | NO |  |  |  |  | 0% |  |  |  |  | 0 |  |  |  |  | One failure is expected per 10 units. | Not Given | By User | By User | Not Given | none |  |  |  |  | Yes | None | YES
D3041.041b | D3041.041b | Variable Air Volume (VAV) box with in-line coil, SDC C | Costing per 10 units | Normal | Normal - SDC C | Each | Each | Peak Floor Acceleration | g | 1 | DS1 |  |  |  |  | Sequential |  |  |  |  | Seq(DS1) | 538 | EA 10 | NO | NO | Coil damages connection to plumbing. Leakage of hot water. |  |  |  |  | 1 |  |  |  |  | 1.9 |  |  |  |  | Not Specified |  |  |  |  | Not Specified |  |  |  |  | 0.4 |  |  |  |  | NO | NO | Marginal | Superior | Marginal | Marginal | Replace coil and cleanup water damage. |  |  |  |  | NO |  |  |  |  | NO |  |  |  |  | Not Applicable |  |  |  |  | 0% | 0 | [8 empty] | 0% | 0 | [8 empty] | NO |  |  |  |  | 0% |  |  |  |  | 0 |  |  |  |  | One failure is expected per 10 units. | Not Given | By User | By User | Not Given | none |  |  |  |  | Yes | None | YES
D3041.101a | D3041.101a | HVAC Fan - Capacity: all - Unanchored equipment that is not vibration isolated - Equipment fragility only | Costing is per unit. | Normal - Not designed for seismic loads | Unanchored equipment that is not vibration isolated | Each | Each | Peak Floor Acceleration | g | 1 | DS1 |  |  |  |  | Sequential |  |  |  |  | Seq(DS1) | 539 | EA 1 | NO | BLDG | Damaged, inoperative. |  |  |  |  | 1 |  |  |  |  | 0.5 |  |  |  |  | 0.4 |  |  |  |  | 0.1 |  |  |  |  | 0.4 |  |  |  |  | NO | NO | Average | Average | Superior | Superior | Replace equipment. |  |  |  |  | YES |  |  |  |  | NO |  |  |  |  | Not Applicable |  |  |  |  | 0% | 0 | [8 empty] | 0% | 0 | [8 empty] | NO |  |  |  |  | 0% |  |  |  |  | 0 |  |  |  |  | None | Not Given | By User | By User | Not Given | D3041.101a-DS1-1.JPG |  |  |  |  | No | None | YES
D3041.102a | D3041.102a | HVAC Fan - Capacity: all - Vibration isolated equipment that is not snubbed or restrained - Anchorage fragility only | Costing is per unit. | Normal - Not designed for seismic loads | Vibration isolated equipment that is not snubbed or restrained | Each | Each | Peak Floor Acceleration | g | 2 | DS1 | DS2 |  |  |  | Mutually Exclusive | Mutually Exclusive |  |  |  | MutEx(DS1,DS2) | 540 | EA 1 | NO | BLDG | Anchorage failure. | Anchorage failure & Equipment damaged beyond repair. |  |  |  | 0.7 | 0.3 |  |  |  | By User | By User |  |  |  | User to Calculate | User to Calculate |  |  |  | User to Calculate | User to Calculate |  |  |  | By User | By User |  |  |  | NO | NO | Average | Average | Superior | Superior | Repair anchorage and remount equipment. | Repair anchorage and replace equipment. |  |  |  | NO | YES |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | NO |  |  |  | 0% | 0% |  |  |  | 0 | 0 |  |  |  | User to provide median demand and dispersion values. The values listed are default PACT values and do not represent the response of this component. | Not Given | By User | By User | Not Given | D3041.101a-DS1-1.JPG | none |  |  |  | No | None | YES
D3041.102b | D3041.102b | HVAC Fan - Capacity: all - Vibration isolated equipment that is not snubbed or restrained - Equipment fragility only | Costing is per unit. | Normal - Not designed for seismic loads | Vibration isolated equipment that is not snubbed or restrained | Each | Each | Peak Floor Acceleration | g | 1 | DS1 |  |  |  |  | Sequential |  |  |  |  | Seq(DS1) | 541 | EA 1 | NO | BLDG | Damaged, inoperative but anchorage is OK. |  |  |  |  | 1 |  |  |  |  | 1 |  |  |  |  | 0.6 |  |  |  |  | 0.1 |  |  |  |  | 0.6 |  |  |  |  | NO | NO | Average | Average | Superior | Superior | Replace equipment. |  |  |  |  | YES |  |  |  |  | NO |  |  |  |  | Not Applicable |  |  |  |  | 0% | 0 | [8 empty] | 0% | 0 | [8 empty] | NO |  |  |  |  | 0% |  |  |  |  | 0 |  |  |  |  | None | Not Given | By User | By User | Not Given | D3041.101a-DS1-1.JPG |  |  |  |  | No | None | YES
D3041.102c | D3041.102c | HVAC Fan - Capacity: all - Vibration isolated equipment that is not snubbed or restrained - Combined anchorage/isolator & equipment fragility | Costing is per unit. | Normal - Not designed for seismic loads | Vibration isolated equipment that is not snubbed or restrained | Each | Each | Peak Floor Acceleration | g | 3 | DS1 | DS2 | DS3 |  |  | Mutually Exclusive | Mutually Exclusive | Mutually Exclusive |  |  | MutEx(DS1,DS2,DS3) | 542 | EA 1 | NO | BLDG | Anchorage failure. | Anchorage failure & Equipment damaged beyond repair. | Damaged, Inoperative but anchorage is OK |  |  | 0.35 | 0.15 | 0.5 |  |  | By User | By User | By User |  |  | User to Calculate | User to Calculate | User to Calculate |  |  | User to Calculate | User to Calculate | User to Calculate |  |  | By User | By User | By User |  |  | NO | NO | Average | Average | Superior | Superior | Repair anchorage and remount equipment. | Repair anchorage and replace equipment. | Repair equipment. |  |  | NO | YES | NO |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | NO | NO |  |  | 0% | 0% | 0% |  |  | 0 | 0 | 0 |  |  | User to provide median demand and dispersion values. The values listed are default PACT values and do not represent the response of this component. | Not Given | By User | By User | Not Given | D3041.101a-DS1-1.JPG | none | none |  |  | No | None | YES
D3041.103a | D3041.103a | HVAC Fan - Capacity: all - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only | Costing is per unit. | Normal - Designed for seismic loads but no special seismic certification | Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints | Each | Each | Peak Floor Acceleration | g | 2 | DS1 | DS2 |  |  |  | Mutually Exclusive | Mutually Exclusive |  |  |  | MutEx(DS1,DS2) | 543 | EA 1 | NO | BLDG | Anchorage failure. | Anchorage failure & Equipment damaged beyond repair. |  |  |  | 0.7 | 0.3 |  |  |  | By User | By User |  |  |  | User to Calculate | User to Calculate |  |  |  | User to Calculate | User to Calculate |  |  |  | By User | By User |  |  |  | NO | NO | Average | Average | Superior | Superior | Repair anchorage and remount equipment. | Repair anchorage and replace equipment. |  |  |  | NO | YES |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | NO |  |  |  | 0% | 0% |  |  |  | 0 | 0 |  |  |  | User to provide median demand and dispersion values. The values listed are default PACT values and do not represent the response of this component. | Not Given | By User | By User | Not Given | D3041.101a-DS1-1.JPG | none |  |  |  | No | None | YES
D3041.103b | D3041.103b | HVAC Fan - Capacity: all - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only | Costing is per unit. | Normal - Designed for seismic loads but no special seismic certification | Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints | Each | Each | Peak Floor Acceleration | g | 1 | DS1 |  |  |  |  | Sequential |  |  |  |  | Seq(DS1) | 544 | EA 1 | NO | BLDG | Damaged, inoperative but anchorage is OK. |  |  |  |  | 1 |  |  |  |  | 4.8 |  |  |  |  | 0.6 |  |  |  |  | 0.1 |  |  |  |  | 0.6 |  |  |  |  | NO | NO | Average | Average | Superior | Superior | Repair equipment. |  |  |  |  | NO |  |  |  |  | NO |  |  |  |  | Not Applicable |  |  |  |  | 0% | 0 | [8 empty] | 0% | 0 | [8 empty] | NO |  |  |  |  | 0% |  |  |  |  | 0 |  |  |  |  | None | Not Given | By User | By User | Not Given | D3041.101a-DS1-1.JPG |  |  |  |  | No | None | YES
D3041.103c | D3041.103c | HVAC Fan - Capacity: all - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | Costing is per unit. | Normal - Designed for seismic loads but no special seismic certification | Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints | Each | Each | Peak Floor Acceleration | g | 3 | DS1 | DS2 | DS3 |  |  | Mutually Exclusive | Mutually Exclusive | Mutually Exclusive |  |  | MutEx(DS1,DS2,DS3) | 545 | EA 1 | NO | BLDG | Anchorage failure. | Anchorage failure & Equipment damaged beyond repair. | Damaged, Inoperative but anchorage is OK |  |  | 0.35 | 0.15 | 0.5 |  |  | By User | By User | By User |  |  | User to Calculate | User to Calculate | User to Calculate |  |  | User to Calculate | User to Calculate | User to Calculate |  |  | By User | By User | By User |  |  | NO | NO | Average | Average | Superior | Superior | Repair anchorage and remount equipment. | Repair anchorage and replace equipment. | Repair equipment. |  |  | NO | YES | NO |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | NO | NO |  |  | 0% | 0% | 0% |  |  | 0 | 0 | 0 |  |  | User to provide median demand and dispersion values. The values listed are default PACT values and do not represent the response of this component. | Not Given | By User | By User | Not Given | D3041.101a-DS1-1.JPG | none | none |  |  | No | None | YES
D3052.011a | D3052.011a | Air Handling Unit - Capacity: <5000 CFM - Unanchored equipment that is not vibration isolated - Equipment fragility only | Costing is per unit and is based upon 4000 CFM. | Normal - Not designed for seismic loads | Unanchored equipment that is not vibration isolated | Each | Each | Peak Floor Acceleration | g | 2 | DS1 | DS2 |  |  |  | Mutually Exclusive | Mutually Exclusive |  |  |  | MutEx(DS1,DS2) | 546 | CF 4000 | YES | BLDG | Equipment does not function. Damage to attached ducting or piping. | Equipment does not function Equipment damaged beyond repair. |  |  |  | 0.67 | 0.33 |  |  |  | 0.25 | 0.25 |  |  |  | 0.4 | 0.4 |  |  |  | 0.1 | 0.1 |  |  |  | 0.4 | 0.4 |  |  |  | NO | NO | Average | Average | Superior | Superior | Repair attached ducting or piping. | Replace equipment. Remove, repair offsite, and reinstall air handler. |  |  |  | NO | YES |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | NO |  |  |  | 0% | 0% |  |  |  | 0 | 0 |  |  |  | None | Not Given | By User | By User | Not Given | D3052.011b-DS1-1.JPG | none |  |  |  | No | 2016-10-25 - Clarified repair. | YES
D3052.011b | D3052.011b | Air Handling Unit - Capacity: 5000 to <10000 CFM - Unanchored equipment that is not vibration isolated - Equipment fragility only | Costing is per unit and is based upon 8000 CFM. | Normal - Not designed for seismic loads | Unanchored equipment that is not vibration isolated | Each | Each | Peak Floor Acceleration | g | 2 | DS1 | DS2 |  |  |  | Mutually Exclusive | Mutually Exclusive |  |  |  | MutEx(DS1,DS2) | 547 | CF 8000 | YES | BLDG | Equipment does not function. Damage to attached ducting or piping. | Equipment does not function Equipment damaged beyond repair. |  |  |  | 0.67 | 0.33 |  |  |  | 0.25 | 0.25 |  |  |  | 0.4 | 0.4 |  |  |  | 0.1 | 0.1 |  |  |  | 0.4 | 0.4 |  |  |  | NO | NO | Average | Average | Superior | Superior | Repair attached ducting or piping. | Replace equipment. Remove, repair offsite, and reinstall air handler. |  |  |  | NO | YES |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | NO |  |  |  | 0% | 0% |  |  |  | 0 | 0 |  |  |  | None | Not Given | By User | By User | Not Given | D3052.011b-DS1-1.JPG | none |  |  |  | No | 2016-10-25 - Clarified repair. | YES
D3052.011c | D3052.011c | Air Handling Unit - Capacity: 10000 to <25000 CFM - Unanchored equipment that is not vibration isolated - Equipment fragility only | Costing is per unit and is based upon 20000 CFM. | Normal - Not designed for seismic loads | Unanchored equipment that is not vibration isolated | Each | Each | Peak Floor Acceleration | g | 2 | DS1 | DS2 |  |  |  | Mutually Exclusive | Mutually Exclusive |  |  |  | MutEx(DS1,DS2) | 548 | CF 20000 | YES | BLDG | Equipment does not function. Damage to attached ducting or piping. | Equipment does not function Equipment damaged beyond repair. |  |  |  | 0.67 | 0.33 |  |  |  | 0.25 | 0.25 |  |  |  | 0.4 | 0.4 |  |  |  | 0.1 | 0.1 |  |  |  | 0.4 | 0.4 |  |  |  | NO | NO | Average | Average | Superior | Superior | Repair attached ducting or piping. | Replace equipment. Remove, repair offsite, and reinstall air handler. |  |  |  | NO | YES |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | NO |  |  |  | 0% | 0% |  |  |  | 0 | 0 |  |  |  | None | Not Given | By User | By User | Not Given | D3052.011b-DS1-1.JPG | none |  |  |  | No | 2016-10-25 - Clarified repair. | YES
D3052.011d | D3052.011d | Air Handling Unit - Capacity: 25000 to <40000 CFM - Unanchored equipment that is not vibration isolated - Equipment fragility only | Costing is per unit and is based upon 30000 CFM. | Normal - Not designed for seismic loads | Unanchored equipment that is not vibration isolated | Each | Each | Peak Floor Acceleration | g | 2 | DS1 | DS2 |  |  |  | Mutually Exclusive | Mutually Exclusive |  |  |  | MutEx(DS1,DS2) | 549 | CF 30000 | YES | BLDG | Equipment does not function. Damage to attached ducting or piping. | Equipment does not function Equipment damaged beyond repair. |  |  |  | 0.67 | 0.33 |  |  |  | 0.25 | 0.25 |  |  |  | 0.4 | 0.4 |  |  |  | 0.1 | 0.1 |  |  |  | 0.4 | 0.4 |  |  |  | NO | NO | Average | Average | Superior | Superior | Repair attached ducting or piping. | Replace equipment. Remove, repair offsite, and reinstall air handler. |  |  |  | NO | YES |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | NO |  |  |  | 0% | 0% |  |  |  | 0 | 0 |  |  |  | None | Not Given | By User | By User | Not Given | D3052.011b-DS1-1.JPG | none |  |  |  | No | 2016-10-25 - Clarified repair. | YES
D3052.013a | D3052.013a | Air Handling Unit - Capacity: <5000 CFM - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only | Costing is per unit and is based upon 4000 CFM. | Normal - Designed for seismic loads but no special seismic certification | Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints | Each | Each | Peak Floor Acceleration | g | 2 | DS1 | DS2 |  |  |  | Mutually Exclusive | Mutually Exclusive |  |  |  | MutEx(DS1,DS2) | 550 | CF 4000 | YES | BLDG | Anchorage failure. | Anchorage failure & Equipment damaged beyond repair. |  |  |  | 0.7 | 0.3 |  |  |  | By User | By User |  |  |  | User to Calculate | User to Calculate |  |  |  | User to Calculate | User to Calculate |  |  |  | By User | By User |  |  |  | NO | NO | Average | Average | Superior | Superior | Repair anchorage and concrete pad and remount equipment. | Replace equipment including attached utilities in addition to repairing anchorage and concrete pad. Remove, repair offsite, and reinstall air handler. |  |  |  | NO | YES |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | NO |  |  |  | 0% | 0% |  |  |  | 0 | 0 |  |  |  | User to provide median demand and dispersion values. The values listed are default PACT values and do not represent the response of this component. | Not Given | By User | By User | Not Given | D3052.011c-DS1-1.JPG | none |  |  |  | No | 2016-10-25 - Clarified repair. | YES
D3052.013b | D3052.013b | Air Handling Unit - Capacity: <5000 CFM - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only | Costing is per unit and is based upon 4000 CFM. | Normal - Designed for seismic loads but no special seismic certification | Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints | Each | Each | Peak Floor Acceleration | g | 2 | DS1 | DS2 |  |  |  | Mutually Exclusive | Mutually Exclusive |  |  |  | MutEx(DS1,DS2) | 551 | CF 4000 | YES | BLDG | Equipment does not function but anchorage is OK. Damage to attached ducting or piping. | Equipment does not function but anchorage is OK. Equipment damaged beyond repair. |  |  |  | 0.67 | 0.33 |  |  |  | 1.54 | 1.54 |  |  |  | 0.6 | 0.6 |  |  |  | 0.1 | 0.1 |  |  |  | 0.6 | 0.6 |  |  |  | NO | NO | Average | Average | Superior | Superior | Repair attached ducting or piping. | Replace equipment. Remove, repair offsite, and reinstall air handler. |  |  |  | NO | YES |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | NO |  |  |  | 0% | 0% |  |  |  | 0 | 0 |  |  |  | None | Not Given | By User | By User | Not Given | D3052.011b-DS1-1.JPG | none |  |  |  | No | 2016-10-25 - Clarified repair. | YES
D3052.013c | D3052.013c | Air Handling Unit - Capacity: <5000 CFM - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | Costing is per unit and is based upon 4000 CFM. | Normal - Designed for seismic loads but no special seismic certification | Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints | Each | Each | Peak Floor Acceleration | g | 4 | DS1 | DS2 | DS3 | DS4 |  | Mutually Exclusive | Mutually Exclusive | Mutually Exclusive | Mutually Exclusive |  | MutEx(DS1,DS2,DS3,DS4) | 552 | CF 4000 | YES | BLDG | Anchorage failure. | Anchorage failure & Equipment damaged beyond repair. | Damage to attached ducting or piping but anchorage is OK. | Equipment damaged beyond repair but anchorage is OK. |  | 0.35 | 0.15 | 0.35 | 0.15 |  | By User | By User | By User | By User |  | User to Calculate | User to Calculate | User to Calculate | User to Calculate |  | User to Calculate | User to Calculate | User to Calculate | User to Calculate |  | By User | By User | By User | By User |  | NO | NO | Average | Average | Superior | Superior | Repair anchorage and concrete pad and remount equipment. | Replace equipment including attached utilities in addition to repairing anchorage and concrete pad. Remove, repair offsite, and reinstall air handler. | Repair attached ducting or piping - equipment does not require replacement and anchorage does not require repair | Replace and install equipment including new anchorage if anchorage is post-installed. |  | NO | YES | NO | YES |  | NO | NO | NO | NO |  | Not Applicable | Not Applicable | Not Applicable | Not Applicable |  | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 |  |  | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 |  |  | NO | NO | NO | NO |  | 0% | 0% | 0% | 0% |  | 0 | 0 | 0 | 0 |  | User to provide median demand and dispersion values. The values listed are default PACT values and do not represent the response of this component. | Not Given | By User | By User | Not Given | D3052.011a-DS1-1.JPG | none | D3052.011b-DS1-1.JPG | none |  | No | 2016-10-25 - Clarified repair. | YES
D3052.013d | D3052.013d | Air Handling Unit - Capacity: 5000 to <10000 CFM - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only | Costing is per unit and is based upon 8000 CFM. | Normal - Designed for seismic loads but no special seismic certification | Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints | Each | Each | Peak Floor Acceleration | g | 2 | DS1 | DS2 |  |  |  | Mutually Exclusive | Mutually Exclusive |  |  |  | MutEx(DS1,DS2) | 553 | CF 8000 | YES | BLDG | Anchorage failure. | Anchorage failure & Equipment damaged beyond repair. |  |  |  | 0.7 | 0.3 |  |  |  | By User | By User |  |  |  | User to Calculate | User to Calculate |  |  |  | User to Calculate | User to Calculate |  |  |  | By User | By User |  |  |  | NO | NO | Average | Average | Superior | Superior | Repair anchorage and concrete pad and remount equipment. | Replace equipment including attached utilities in addition to repairing anchorage and concrete pad. Remove, repair offsite, and reinstall air handler. |  |  |  | NO | YES |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | NO |  |  |  | 0% | 0% |  |  |  | 0 | 0 |  |  |  | User to provide median demand and dispersion values. The values listed are default PACT values and do not represent the response of this component. | Not Given | By User | By User | Not Given | D3052.011c-DS1-1.JPG | none |  |  |  | No | 2016-10-25 - Clarified repair. | YES
D3052.013e | D3052.013e | Air Handling Unit - Capacity: 5000 to <10000 CFM - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only | Costing is per unit and is based upon 8000 CFM. | Normal - Designed for seismic loads but no special seismic certification | Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints | Each | Each | Peak Floor Acceleration | g | 2 | DS1 | DS2 |  |  |  | Mutually Exclusive | Mutually Exclusive |  |  |  | MutEx(DS1,DS2) | 554 | CF 8000 | YES | BLDG | Equipment does not function but anchorage is OK. Damage to attached ducting or piping. | Equipment does not function but anchorage is OK. Equipment damaged beyond repair. |  |  |  | 0.67 | 0.33 |  |  |  | 1.54 | 1.54 |  |  |  | 0.6 | 0.6 |  |  |  | 0.1 | 0.1 |  |  |  | 0.6 | 0.6 |  |  |  | NO | NO | Average | Average | Superior | Superior | Repair attached ducting or piping. | Replace equipment. Remove, repair offsite, and reinstall air handler. |  |  |  | NO | YES |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | NO |  |  |  | 0% | 0% |  |  |  | 0 | 0 |  |  |  | None | Not Given | By User | By User | Not Given | D3052.011b-DS1-1.JPG | none |  |  |  | No | 2016-10-25 - Clarified repair. | YES
D3052.013f | D3052.013f | Air Handling Unit - Capacity: 5000 to <10000 CFM - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | Costing is per unit and is based upon 8000 CFM. | Normal - Designed for seismic loads but no special seismic certification | Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints | Each | Each | Peak Floor Acceleration | g | 4 | DS1 | DS2 | DS3 | DS4 |  | Mutually Exclusive | Mutually Exclusive | Mutually Exclusive | Mutually Exclusive |  | MutEx(DS1,DS2,DS3,DS4) | 555 | CF 8000 | YES | BLDG | Anchorage failure. | Anchorage failure & Equipment damaged beyond repair. | Damage to attached ducting or piping but anchorage is OK. | Equipment damaged beyond repair but anchorage is OK. |  | 0.35 | 0.15 | 0.35 | 0.15 |  | By User | By User | By User | By User |  | User to Calculate | User to Calculate | User to Calculate | User to Calculate |  | User to Calculate | User to Calculate | User to Calculate | User to Calculate |  | By User | By User | By User | By User |  | NO | NO | Average | Average | Superior | Superior | Repair anchorage and concrete pad and remount equipment. | Replace equipment including attached utilities in addition to repairing anchorage and concrete pad. Remove, repair offsite, and reinstall air handler. | Repair attached ducting or piping - equipment does not require replacement and anchorage does not require repair | Replace and install equipment including new anchorage if anchorage is post-installed. |  | NO | YES | NO | YES |  | NO | NO | NO | NO |  | Not Applicable | Not Applicable | Not Applicable | Not Applicable |  | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 |  |  | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 |  |  | NO | NO | NO | NO |  | 0% | 0% | 0% | 0% |  | 0 | 0 | 0 | 0 |  | User to provide median demand and dispersion values. The values listed are default PACT values and do not represent the response of this component. | Not Given | By User | By User | Not Given | D3052.011a-DS1-1.JPG | none | D3052.011b-DS1-1.JPG | none |  | No | 2016-10-25 - Clarified repair. | YES
D3052.013g | D3052.013g | Air Handling Unit - Capacity: 10000 to <25000 CFM - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only | Costing is per unit and is based upon 20000 CFM. | Normal - Designed for seismic loads but no special seismic certification | Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints | Each | Each | Peak Floor Acceleration | g | 2 | DS1 | DS2 |  |  |  | Mutually Exclusive | Mutually Exclusive |  |  |  | MutEx(DS1,DS2) | 556 | CF 20000 | YES | BLDG | Anchorage failure. | Anchorage failure & Equipment damaged beyond repair. |  |  |  | 0.7 | 0.3 |  |  |  | By User | By User |  |  |  | User to Calculate | User to Calculate |  |  |  | User to Calculate | User to Calculate |  |  |  | By User | By User |  |  |  | NO | NO | Average | Average | Superior | Superior | Repair anchorage and concrete pad and remount equipment. | Replace equipment including attached utilities in addition to repairing anchorage and concrete pad. Remove, repair offsite, and reinstall air handler. |  |  |  | NO | YES |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | NO |  |  |  | 0% | 0% |  |  |  | 0 | 0 |  |  |  | User to provide median demand and dispersion values. The values listed are default PACT values and do not represent the response of this component. | Not Given | By User | By User | Not Given | D3052.011c-DS1-1.JPG | none |  |  |  | No | 2016-10-25 - Clarified repair. | YES
D3052.013h | D3052.013h | Air Handling Unit - Capacity: 10000 to <25000 CFM - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only | Costing is per unit and is based upon 20000 CFM. | Normal - Designed for seismic loads but no special seismic certification | Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints | Each | Each | Peak Floor Acceleration | g | 2 | DS1 | DS2 |  |  |  | Mutually Exclusive | Mutually Exclusive |  |  |  | MutEx(DS1,DS2) | 557 | CF 20000 | YES | BLDG | Equipment does not function but anchorage is OK. Damage to attached ducting or piping. | Equipment does not function but anchorage is OK. Equipment damaged beyond repair. |  |  |  | 0.67 | 0.33 |  |  |  | 1.54 | 1.54 |  |  |  | 0.6 | 0.6 |  |  |  | 0.1 | 0.1 |  |  |  | 0.6 | 0.6 |  |  |  | NO | NO | Average | Average | Superior | Superior | Repair attached ducting or piping. | Replace equipment. Remove, repair offsite, and reinstall air handler. |  |  |  | NO | YES |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | NO |  |  |  | 0% | 0% |  |  |  | 0 | 0 |  |  |  | None | Not Given | By User | By User | Not Given | D3052.011b-DS1-1.JPG | none |  |  |  | No | 2016-10-25 - Clarified repair. | YES
D3052.013i | D3052.013i | Air Handling Unit - Capacity: 10000 to <25000 CFM - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | Costing is per unit and is based upon 20000 CFM. | Normal - Designed for seismic loads but no special seismic certification | Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints | Each | Each | Peak Floor Acceleration | g | 4 | DS1 | DS2 | DS3 | DS4 |  | Mutually Exclusive | Mutually Exclusive | Mutually Exclusive | Mutually Exclusive |  | MutEx(DS1,DS2,DS3,DS4) | 558 | CF 20000 | YES | BLDG | Anchorage failure. | Anchorage failure & Equipment damaged beyond repair. | Damage to attached ducting or piping but anchorage is OK. | Equipment damaged beyond repair but anchorage is OK. |  | 0.35 | 0.15 | 0.35 | 0.15 |  | By User | By User | By User | By User |  | User to Calculate | User to Calculate | User to Calculate | User to Calculate |  | User to Calculate | User to Calculate | User to Calculate | User to Calculate |  | By User | By User | By User | By User |  | NO | NO | Average | Average | Superior | Superior | Repair anchorage and concrete pad and remount equipment. | Replace equipment including attached utilities in addition to repairing anchorage and concrete pad. Remove, repair offsite, and reinstall air handler. | Repair attached ducting or piping - equipment does not require replacement and anchorage does not require repair | Replace and install equipment including new anchorage if anchorage is post-installed. |  | NO | YES | NO | YES |  | NO | NO | NO | NO |  | Not Applicable | Not Applicable | Not Applicable | Not Applicable |  | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 |  |  | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 |  |  | NO | NO | NO | NO |  | 0% | 0% | 0% | 0% |  | 0 | 0 | 0 | 0 |  | User to provide median demand and dispersion values. The values listed are default PACT values and do not represent the response of this component. | Not Given | By User | By User | Not Given | D3052.011a-DS1-1.JPG | none | D3052.011b-DS1-1.JPG | none |  | No | 2016-10-25 - Clarified repair. | YES
D3052.013j | D3052.013j | Air Handling Unit - Capacity: 25000 to <40000 CFM - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only | Costing is per unit and is based upon 30000 CFM. | Normal - Designed for seismic loads but no special seismic certification | Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints | Each | Each | Peak Floor Acceleration | g | 2 | DS1 | DS2 |  |  |  | Mutually Exclusive | Mutually Exclusive |  |  |  | MutEx(DS1,DS2) | 559 | CF 30000 | YES | BLDG | Anchorage failure. | Anchorage failure & Equipment damaged beyond repair. |  |  |  | 0.7 | 0.3 |  |  |  | By User | By User |  |  |  | User to Calculate | User to Calculate |  |  |  | User to Calculate | User to Calculate |  |  |  | By User | By User |  |  |  | NO | NO | Average | Average | Superior | Superior | Repair anchorage and concrete pad and remount equipment. | Replace equipment including attached utilities in addition to repairing anchorage and concrete pad. Remove, repair offsite, and reinstall air handler. |  |  |  | NO | YES |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | NO |  |  |  | 0% | 0% |  |  |  | 0 | 0 |  |  |  | User to provide median demand and dispersion values. The values listed are default PACT values and do not represent the response of this component. | Not Given | By User | By User | Not Given | D3052.011c-DS1-1.JPG | none |  |  |  | No | 2016-10-25 - Clarified repair. | YES
D3052.013k | D3052.013k | Air Handling Unit - Capacity: 25000 to <40000 CFM - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only | Costing is per unit and is based upon 30000 CFM. | Normal - Designed for seismic loads but no special seismic certification | Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints | Each | Each | Peak Floor Acceleration | g | 2 | DS1 | DS2 |  |  |  | Mutually Exclusive | Mutually Exclusive |  |  |  | MutEx(DS1,DS2) | 560 | CF 30000 | YES | BLDG | Equipment does not function but anchorage is OK. Damage to attached ducting or piping. | Equipment does not function but anchorage is OK. Equipment damaged beyond repair. |  |  |  | 0.67 | 0.33 |  |  |  | 1.54 | 1.54 |  |  |  | 0.6 | 0.6 |  |  |  | 0.1 | 0.1 |  |  |  | 0.6 | 0.6 |  |  |  | NO | NO | Average | Average | Superior | Superior | Repair attached ducting or piping. | Replace equipment. Remove, repair offsite, and reinstall air handler. |  |  |  | NO | YES |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | NO |  |  |  | 0% | 0% |  |  |  | 0 | 0 |  |  |  | None | Not Given | By User | By User | Not Given | D3052.011b-DS1-1.JPG | none |  |  |  | No | 2016-10-25 - Clarified repair. | YES
D3052.013l | D3052.013l | Air Handling Unit - Capacity: 25000 to <40000 CFM - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | Costing is per unit and is based upon 30000 CFM. | Normal - Designed for seismic loads but no special seismic certification | Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints | Each | Each | Peak Floor Acceleration | g | 4 | DS1 | DS2 | DS3 | DS4 |  | Mutually Exclusive | Mutually Exclusive | Mutually Exclusive | Mutually Exclusive |  | MutEx(DS1,DS2,DS3,DS4) | 561 | CF 30000 | YES | BLDG | Anchorage failure. | Anchorage failure & Equipment damaged beyond repair. | Damage to attached ducting or piping but anchorage is OK. | Equipment damaged beyond repair but anchorage is OK. |  | 0.35 | 0.15 | 0.35 | 0.15 |  | By User | By User | By User | By User |  | User to Calculate | User to Calculate | User to Calculate | User to Calculate |  | User to Calculate | User to Calculate | User to Calculate | User to Calculate |  | By User | By User | By User | By User |  | NO | NO | Average | Average | Superior | Superior | Repair anchorage and concrete pad and remount equipment. | Replace equipment including attached utilities in addition to repairing anchorage and concrete pad. Remove, repair offsite, and reinstall air handler. | Repair attached ducting or piping - equipment does not require replacement and anchorage does not require repair | Replace and install equipment including new anchorage if anchorage is post-installed. |  | NO | YES | NO | YES |  | NO | NO | NO | NO |  | Not Applicable | Not Applicable | Not Applicable | Not Applicable |  | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 |  |  | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 |  |  | NO | NO | NO | NO |  | 0% | 0% | 0% | 0% |  | 0 | 0 | 0 | 0 |  | User to provide median demand and dispersion values. The values listed are default PACT values and do not represent the response of this component. | Not Given | By User | By User | Not Given | D3052.011a-DS1-1.JPG | none | D3052.011b-DS1-1.JPG | none |  | No | 2016-10-25 - Clarified repair. | YES
D3067.011a | D3067.011a | Control Panel - Capacity: all - Unanchored equipment that is not vibration isolated - Equipment fragility only | Costing is per unit. | Normal - Not designed for seismic loads | Unanchored equipment that is not vibration isolated | Each | Each | Peak Floor Acceleration | g | 1 | DS1 |  |  |  |  | Sequential |  |  |  |  | Seq(DS1) | 562 | EA 1 | YES | BLDG | Damaged, inoperative. |  |  |  |  | 1 |  |  |  |  | 0.69 |  |  |  |  | 0.4 |  |  |  |  | 0.1 |  |  |  |  | 0.4 |  |  |  |  | NO | NO | Superior | Average | Superior | Superior | Replace some components (relays, circuit boards). |  |  |  |  | NO |  |  |  |  | NO |  |  |  |  | Not Applicable |  |  |  |  | 0% | 0 | [8 empty] | 0% | 0 | [8 empty] | NO |  |  |  |  | 0% |  |  |  |  | 0 |  |  |  |  | None | Not Given | By User | By User | Not Given | D3067.011a-DS1-1.JPG |  |  |  |  | No | None | YES
D3067.012a | D3067.012a | Control Panel - Capacity: all - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only | Costing is per unit. | Normal - Designed for seismic loads but no special seismic certification | Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints | Each | Each | Peak Floor Acceleration | g | 2 | DS1 | DS2 |  |  |  | Mutually Exclusive | Mutually Exclusive |  |  |  | MutEx(DS1,DS2) | 563 | EA 1 | YES | BLDG | Anchorage failure. | Anchorage failure & Equipment damaged beyond repair. |  |  |  | 0.7 | 0.3 |  |  |  | By User | By User |  |  |  | User to Calculate | User to Calculate |  |  |  | User to Calculate | User to Calculate |  |  |  | By User | By User |  |  |  | NO | NO | Superior | Average | Superior | Superior | Repair anchorage and concrete pad and remount equipment. | Replace equipment including attached utilities in addition to repairing anchorage and concrete pad. |  |  |  | NO | NO |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | NO |  |  |  | 0% | 0% |  |  |  | 0 | 0 |  |  |  | User to provide median demand and dispersion values. The values listed are default PACT values and do not represent the response of this component. | Not Given | By User | By User | Not Given | D3067.011a-DS1-1.JPG | none |  |  |  | No | None | YES
D3067.012b | D3067.012b | Control Panel - Capacity: all - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only | Costing is per unit. | Normal - Designed for seismic loads but no special seismic certification | Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints | Each | Each | Peak Floor Acceleration | g | 1 | DS1 |  |  |  |  | Sequential |  |  |  |  | Seq(DS1) | 564 | EA 1 | YES | BLDG | Damaged, inoperative but anchorage is OK. |  |  |  |  | 1 |  |  |  |  | 3 |  |  |  |  | 0.4 |  |  |  |  | 0.1 |  |  |  |  | 0.4 |  |  |  |  | NO | NO | Superior | Average | Superior | Superior | Replace some components (relays, circuit boards). |  |  |  |  | NO |  |  |  |  | NO |  |  |  |  | Not Applicable |  |  |  |  | 0% | 0 | [8 empty] | 0% | 0 | [8 empty] | NO |  |  |  |  | 0% |  |  |  |  | 0 |  |  |  |  | None | Not Given | By User | By User | Not Given | D3067.011a-DS1-1.JPG |  |  |  |  | No | None | YES
D3067.012c | D3067.012c | Control Panel - Capacity: all - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | Costing is per unit. | Normal - Designed for seismic loads but no special seismic certification | Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints | Each | Each | Peak Floor Acceleration | g | 3 | DS1 | DS2 | DS3 |  |  | Mutually Exclusive | Mutually Exclusive | Mutually Exclusive |  |  | MutEx(DS1,DS2,DS3) | 565 | EA 1 | YES | BLDG | Anchorage failure. | Anchorage failure & Equipment damaged beyond repair. | Damaged, Inoperative but anchorage is OK |  |  | 0.35 | 0.15 | 0.5 |  |  | By User | By User | By User |  |  | User to Calculate | User to Calculate | User to Calculate |  |  | User to Calculate | User to Calculate | User to Calculate |  |  | By User | By User | By User |  |  | NO | NO | Superior | Average | Superior | Superior | Repair anchorage and concrete pad and remount equipment. | Replace equipment including attached utilities in addition to repairing anchorage and concrete pad. | Replace some components (relays, circuit boards |  |  | NO | NO | NO |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | NO | NO |  |  | 0% | 0% | 0% |  |  | 0 | 0 | 0 |  |  | User to provide median demand and dispersion values. The values listed are default PACT values and do not represent the response of this component. | Not Given | By User | By User | Not Given | none | D5010.011a-DS1-1.JPG | none |  |  | No | None | YES
D4011.021a | D4011.021a | Fire Sprinkler Water Piping - Horizontal Mains and Branches - Old Style Victaulic - Thin Wall Steel - No bracing, SDC A or B, PIPING FRAGILITY | Costing based upon 1000 ft segments of pipe, horizontal main and branches | Normal | SDC A or B (no seismic design) | Each | Each | Peak Floor Acceleration | g | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 566 | LF 1000 | NO | NO | Spraying & Dripping Leakage at joints - 0.02 leaks per 20 ft section of pipe. | Joints Break - Major Leakage - 0.02 breaks per 20 ft section of pipe. |  |  |  | 1 | 1 |  |  |  | 1.1 | 2.4 |  |  |  | Not Specified | Not Specified |  |  |  | Not Specified | Not Specified |  |  |  | 0.4 | 0.5 |  |  |  | NO | NO | Marginal | Marginal | Marginal | Marginal | Replace leaking joints and minor water cleanup. | Replace 20 ft section of pipe, joints and major water cleanup at leaking joints. |  |  |  | NO | NO |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | NO |  |  |  | 0% | 0% |  |  |  | 0 | 0 |  |  |  | One failure is expected per 1000 feet of pipe. Allowance included for MEP modifications for repair. | Not Given | By User | By User | Not Given | none | none |  |  |  | Yes | 2011-08-24 Negative probability below 0.5 g - overlap deemed acceptable. 2016-10-25 Clarification of cost added. | YES
D4011.022a | D4011.022a | Fire Sprinkler Water Piping - Horizontal Mains and Branches - Old Style Victaulic - Thin Wall Steel - No bracing, SDC C, PIPING FRAGILITY | Costing based upon 1000 ft segments of pipe, horizontal main and branches | Normal | SDC C (low seismic design) | Each | Each | Peak Floor Acceleration | g | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 567 | LF 1000 | NO | NO | Spraying & Dripping Leakage at joints - 0.02 leaks per 20 ft section of pipe. | Joints Break - Major Leakage - 0.02 breaks per 20 ft section of pipe. |  |  |  | 1 | 1 |  |  |  | 1.1 | 2.4 |  |  |  | Not Specified | Not Specified |  |  |  | Not Specified | Not Specified |  |  |  | 0.4 | 0.5 |  |  |  | NO | NO | Marginal | Marginal | Marginal | Marginal | Replace leaking joints and minor water cleanup. | Replace 20 ft section of pipe, joints and major water cleanup at leaking joints. |  |  |  | NO | NO |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | NO |  |  |  | 0% | 0% |  |  |  | 0 | 0 |  |  |  | One failure is expected per 1000 feet of pipe. Allowance included for MEP modifications for repair. | Not Given | By User | By User | Not Given | none | none |  |  |  | Yes | 2011-08-24 Negative probability below 0.5 g - overlap deemed acceptable. 2016-10-25 Clarification of cost added. | YES
D4011.023a | D4011.023a | Fire Sprinkler Water Piping - Horizontal Mains and Branches - Old Style Victaulic - Thin Wall Steel - Poorly designed bracing, SDC D, E, or F , PIPING FRAGILITY | Costing based upon 1000 ft segments of pipe, horizontal main and branches | Normal | SDC D,E,F (high seismic design) | Each | Each | Peak Floor Acceleration | g | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 568 | LF 1000 | NO | NO | Spraying & Dripping Leakage at joints - 0.02 leaks per 20 ft section of pipe. | Joints Break - Major Leakage - 0.02 breaks per 20 ft section of pipe. |  |  |  | 1 | 1 |  |  |  | 1.5 | 2.6 |  |  |  | Not Specified | Not Specified |  |  |  | Not Specified | Not Specified |  |  |  | 0.4 | 0.4 |  |  |  | NO | NO | Marginal | Marginal | Marginal | Marginal | Replace leaking joints and minor water cleanup. | Replace 20 ft section of pipe, joints and major water cleanup at leaking joints. |  |  |  | NO | NO |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | NO |  |  |  | 0% | 0% |  |  |  | 0 | 0 |  |  |  | One failure is expected per 1000 feet of pipe. Allowance included for MEP modifications for repair. | Not Given | By User | By User | Not Given | none | none |  |  |  | Yes | 2016-10-25 Clarification of cost added. | YES
D4011.024a | D4011.024a | Fire Sprinkler Water Piping - Horizontal Mains and Branches - Old Style Victaulic - Thin Wall Steel - with designed bracing, SDC D, E, or F (OSHPD or sim), PIPING FRAGILITY | Costing based upon 1000 ft segments of pipe, horizontal main and branches | Special Regulation (e.g. OSHPD) for sprinkler installations | SDC D,E,F (high seismic design) | Each | Each | Peak Floor Acceleration | g | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 569 | LF 1000 | NO | NO | Spraying & Dripping Leakage at joints - 0.02 leaks per 20 ft section of pipe. | Joints Break - Major Leakage - 0.02 breaks per 20 ft section of pipe. |  |  |  | 1 | 1 |  |  |  | 1.9 | 3.4 |  |  |  | Not Specified | Not Specified |  |  |  | Not Specified | Not Specified |  |  |  | 0.4 | 0.4 |  |  |  | NO | NO | Marginal | Marginal | Marginal | Marginal | Replace leaking joints and minor water cleanup. | Replace 20 ft section of pipe, joints and major water cleanup at leaking joints. |  |  |  | NO | NO |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | NO |  |  |  | 0% | 0% |  |  |  | 0 | 0 |  |  |  | One failure is expected per 1000 feet of pipe. Allowance included for MEP modifications for repair. | Not Given | By User | By User | Not Given | none | none |  |  |  | Yes | 2016-10-25 Clarification of cost added. | YES
D4011.031a | D4011.031a | Fire Sprinkler Drop Standard Threaded Steel - Dropping into unbraced lay-in tile SOFT ceiling - 6 ft. long drop maximum, SDC A or B | Costing per 100 units, Standard threaded steel drop, 6 ft. long drop maximum | Normal | SDC A or B (no seismic design) | Each | Each | Peak Floor Acceleration | g | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 570 | EA 100 | NO | NO | Spraying & Dripping Leakage at drop joints - 0.01 leaks per drop. | Drop Joints Break - Major Leakage - 0.01 breaks per drop. |  |  |  | 1 | 1 |  |  |  | 0.75 | 0.95 |  |  |  | Not Specified | Not Specified |  |  |  | Not Specified | Not Specified |  |  |  | 0.4 | 0.4 |  |  |  | NO | NO | Marginal | Marginal | Marginal | Marginal | Replace sprinkler drops and minor water cleanup at broken joints. | Replace sprinkler drops and major water cleanup at broken joints |  |  |  | NO | NO |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | NO |  |  |  | 0% | 0% |  |  |  | 0 | 0 |  |  |  | One failure is expected per 100 units. Allowance included for MEP modifications for repair. | Not Given | By User | By User | Not Given | none | none |  |  |  | Yes | 2016-10-25 Clarification of cost added. | YES
D4011.032a | D4011.032a | Fire Sprinkler Drop Standard Threaded Steel - Dropping into unbraced lay-in tile SOFT ceiling - 6 ft. long drop maximum, SDC C | Costing per 100 units, Standard threaded steel drop, 6 ft. long drop maximum | Normal | SDC C (low seismic design) | Each | Each | Peak Floor Acceleration | g | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 571 | EA 100 | NO | NO | Spraying & Dripping Leakage at drop joints - 0.01 leaks per drop. | Drop Joints Break - Major Leakage - 0.01 breaks per drop. |  |  |  | 1 | 1 |  |  |  | 0.75 | 0.95 |  |  |  | Not Specified | Not Specified |  |  |  | Not Specified | Not Specified |  |  |  | 0.4 | 0.4 |  |  |  | NO | NO | Marginal | Marginal | Marginal | Marginal | Replace sprinkler drops and minor water cleanup at broken joints. | Replace sprinkler drops and major water cleanup at broken joints |  |  |  | NO | NO |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | NO |  |  |  | 0% | 0% |  |  |  | 0 | 0 |  |  |  | One failure is expected per 100 units. Allowance included for MEP modifications for repair. | Not Given | By User | By User | Not Given | none | none |  |  |  | Yes | 2016-10-25 Clarification of cost added. | YES
D4011.033a | D4011.033a | Fire Sprinkler Drop Standard Threaded Steel - Dropping into unbraced lay-in tile SOFT ceiling - 6 ft. long drop maximum, SDC D, E, or F | Costing per 100 units, Standard threaded steel drop, 6 ft. long drop maximum | Normal | SDC D,E,F (high seismic design) | Each | Each | Peak Floor Acceleration | g | 1 | DS1 |  |  |  |  | Sequential |  |  |  |  | Seq(DS1) | 572 | EA 100 | NO | NO | Spraying & Dripping Leakage at drop joints - 0.01 leaks per drop. |  |  |  |  | 1 |  |  |  |  | 0.95 |  |  |  |  | Not Specified |  |  |  |  | Not Specified |  |  |  |  | 0.4 |  |  |  |  | NO | NO | Marginal | Marginal | Marginal | Marginal | Replace sprinkler drops and minor water cleanup at broken joints. |  |  |  |  | NO |  |  |  |  | NO |  |  |  |  | Not Applicable |  |  |  |  | 0% | 0 | [8 empty] | 0% | 0 | [8 empty] | NO |  |  |  |  | 0% |  |  |  |  | 0 |  |  |  |  | One failure is expected per 100 units. Allowance included for MEP modifications for repair. | Not Given | By User | By User | Not Given | none |  |  |  |  | Yes | 2016-10-25 Clarification of cost added. | YES
D4011.034a | D4011.034a | Fire Sprinkler Drop Standard Threaded Steel - Dropping into unbraced lay-in tile SOFT ceiling - 6 ft. long drop maximum, SDC D, E, or F (OSHPD or sim) | Costing per 100 units, Standard threaded steel drop, 6 ft. long drop maximum | Special Regulation (e.g. OSHPD) for sprinkler installations | SDC D,E,F (high seismic design) | Each | Each | Peak Floor Acceleration | g | 1 | DS1 |  |  |  |  | Sequential |  |  |  |  | Seq(DS1) | 573 | EA 100 | NO | NO | Spraying & Dripping Leakage at drop joints - 0.01 leaks per drop. |  |  |  |  | 1 |  |  |  |  | 1.3 |  |  |  |  | Not Specified |  |  |  |  | Not Specified |  |  |  |  | 0.4 |  |  |  |  | NO | NO | Marginal | Marginal | Marginal | Marginal | Replace sprinkler drops and minor water cleanup at broken joints. |  |  |  |  | NO |  |  |  |  | NO |  |  |  |  | Not Applicable |  |  |  |  | 0% | 0 | [8 empty] | 0% | 0 | [8 empty] | NO |  |  |  |  | 0% |  |  |  |  | 0 |  |  |  |  | One failure is expected per 100 units. Allowance included for MEP modifications for repair. | Not Given | By User | By User | Not Given | none |  |  |  |  | Yes | 2016-10-25 Clarification of cost added. | YES
D4011.041a | D4011.041a | Fire Sprinkler Drop Standard Threaded Steel - Dropping into unbraced lay-in tile HARD ceiling - 6 ft. long drop maximum, SDC A or B | Costing per 100 units, Standard threaded steel drop, 6 ft. long drop maximum | Normal | SDC A or B (no seismic design) | Each | Each | Peak Floor Acceleration | g | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 574 | EA 100 | NO | NO | Spraying & Dripping Leakage at drop joints - 0.01 leaks per drop. | Drop Joints Break - Major Leakage - 0.01 breaks per drop. |  |  |  | 1 | 1 |  |  |  | 0.55 | 0.95 |  |  |  | Not Specified | Not Specified |  |  |  | Not Specified | Not Specified |  |  |  | 0.4 | 0.4 |  |  |  | NO | NO | Marginal | Marginal | Marginal | Marginal | Replace sprinkler drops and minor water cleanup at broken joints. | Replace sprinkler drops and major water cleanup at broken joints |  |  |  | NO | NO |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | NO |  |  |  | 0% | 0% |  |  |  | 0 | 0 |  |  |  | One failure is expected per 100 units. Allowance included for MEP modifications for repair. | Not Given | By User | By User | Not Given | none | none |  |  |  | Yes | 2016-10-25 Clarification of cost added. | YES
D4011.042a | D4011.042a | Fire Sprinkler Drop Standard Threaded Steel - Dropping into unbraced lay-in tile HARD ceiling - 6 ft. long drop maximum, SDC C | Costing per 100 units, Standard threaded steel drop, 6 ft. long drop maximum | Normal | SDC C (low seismic design) | Each | Each | Peak Floor Acceleration | g | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 575 | EA 100 | NO | NO | Spraying & Dripping Leakage at drop joints - 0.01 leaks per drop. | Drop Joints Break - Major Leakage - 0.01 breaks per drop. |  |  |  | 1 | 1 |  |  |  | 0.55 | 0.95 |  |  |  | Not Specified | Not Specified |  |  |  | Not Specified | Not Specified |  |  |  | 0.4 | 0.4 |  |  |  | NO | NO | Marginal | Marginal | Marginal | Marginal | Replace sprinkler drops and minor water cleanup at broken joints. | Replace sprinkler drops and major water cleanup at broken joints |  |  |  | NO | NO |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | NO |  |  |  | 0% | 0% |  |  |  | 0 | 0 |  |  |  | One failure is expected per 100 units. Allowance included for MEP modifications for repair. | Not Given | By User | By User | Not Given | none | none |  |  |  | Yes | 2016-10-25 Clarification of cost added. | YES
D4011.053a | D4011.053a | Fire Sprinkler Drop Standard Threaded Steel - Dropping into braced lay-in tile SOFT ceiling - 6 ft. long drop maximum, SDC D, E, or F | Costing per 100 units, Standard threaded steel drop, 6 ft. long drop maximum | Normal | SDC D,E,F (high seismic design) | Each | Each | Peak Floor Acceleration | g | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 576 | EA 100 | NO | NO | Spraying & Dripping Leakage at drop joints - 0.01 leaks per drop. | Drop Joints Break - Major Leakage - 0.01 breaks per drop. |  |  |  | 1 | 1 |  |  |  | 1.5 | 2.25 |  |  |  | Not Specified | Not Specified |  |  |  | Not Specified | Not Specified |  |  |  | 0.4 | 0.4 |  |  |  | NO | NO | Marginal | Marginal | Marginal | Marginal | Replace sprinkler drops and minor water cleanup at broken joints. | Replace sprinkler drops and major water cleanup at broken joints |  |  |  | NO | NO |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | NO |  |  |  | 0% | 0% |  |  |  | 0 | 0 |  |  |  | One failure is expected per 100 units. Allowance included for MEP modifications for repair. | Not Given | By User | By User | Not Given | none | none |  |  |  | Yes | 2016-10-25 Clarification of cost added. | YES
D4011.054a | D4011.054a | Fire Sprinkler Drop Standard Threaded Steel - Dropping into braced lay-in tile SOFT ceiling - 6 ft. long drop maximum, SDC D, E, or F (OSHPD or sim) | Costing per 100 units, Standard threaded steel drop, 6 ft. long drop maximum | Special Regulation (e.g. OSHPD) for sprinkler installations | SDC D,E,F (high seismic design) | Each | Each | Peak Floor Acceleration | g | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 577 | EA 100 | NO | NO | Spraying & Dripping Leakage at drop joints - 0.01 leaks per drop. | Drop Joints Break - Major Leakage - 0.01 breaks per drop. |  |  |  | 1 | 1 |  |  |  | 1.9 | 3 |  |  |  | Not Specified | Not Specified |  |  |  | Not Specified | Not Specified |  |  |  | 0.4 | 0.4 |  |  |  | NO | NO | Marginal | Marginal | Marginal | Marginal | Replace sprinkler drops and minor water cleanup at broken joints. | Replace sprinkler drops and major water cleanup at broken joints |  |  |  | NO | NO |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | NO |  |  |  | 0% | 0% |  |  |  | 0 | 0 |  |  |  | One failure is expected per 100 units. Allowance included for MEP modifications for repair. | Not Given | By User | By User | Not Given | none | none |  |  |  | Yes | 2016-10-25 Clarification of cost added. | YES
D4011.063a | D4011.063a | Fire Sprinkler Drop Standard Threaded Steel - Dropping into braced lay-in tile HARD ceiling - 6 ft. long drop maximum, SDC D, E, or F | Costing per 100 units, Standard threaded steel drop, 6 ft. long drop maximum | Normal | SDC D,E,F (high seismic design) | Each | Each | Peak Floor Acceleration | g | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 578 | EA 100 | NO | NO | Spraying & Dripping Leakage at drop joints - 0.01 leaks per drop. | Drop Joints Break - Major Leakage - 0.01 breaks per drop. |  |  |  | 1 | 1 |  |  |  | 0.55 | 1.3 |  |  |  | Not Specified | Not Specified |  |  |  | Not Specified | Not Specified |  |  |  | 0.4 | 0.4 |  |  |  | NO | NO | Marginal | Marginal | Marginal | Marginal | Replace sprinkler drops and minor water cleanup at broken joints. | Replace sprinkler drops and major water cleanup at broken joints |  |  |  | NO | NO |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | NO |  |  |  | 0% | 0% |  |  |  | 0 | 0 |  |  |  | One failure is expected per 100 units. Allowance included for MEP modifications for repair. | Not Given | By User | By User | Not Given | none | none |  |  |  | Yes | 2016-10-25 Clarification of cost added. | YES
D4011.064a | D4011.064a | Fire Sprinkler Drop Standard Threaded Steel - Dropping into braced lay-in tile HARD ceiling - 6 ft. long drop maximum, SDC D, E, or F (OSHPD or sim) | Costing per 100 units, Standard threaded steel drop, 6 ft. long drop maximum | Special Regulation (e.g. OSHPD) for sprinkler installations | SDC D,E,F (high seismic design) | Each | Each | Peak Floor Acceleration | g | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 579 | EA 100 | NO | NO | Spraying & Dripping Leakage at drop joints - 0.01 leaks per drop. | Drop Joints Break - Major Leakage - 0.01 breaks per drop. |  |  |  | 1 | 1 |  |  |  | 1.1 | 2.25 |  |  |  | Not Specified | Not Specified |  |  |  | Not Specified | Not Specified |  |  |  | 0.4 | 0.4 |  |  |  | NO | NO | Marginal | Marginal | Marginal | Marginal | Replace sprinkler drops and minor water cleanup at broken joints. | Replace sprinkler drops and major water cleanup at broken joints |  |  |  | NO | NO |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | NO |  |  |  | 0% | 0% |  |  |  | 0 | 0 |  |  |  | One failure is expected per 100 units. Allowance included for MEP modifications for repair. | Not Given | By User | By User | Not Given | none | none |  |  |  | Yes | 2016-10-25 Clarification of cost added. | YES
D4011.071a | D4011.071a | Fire Sprinkler Drop Standard Threaded Steel - No Ceiling - 6 ft. long drop maximum, SDC A or B | Costing per 100 units, Standard threaded steel drop, 6 ft. long drop maximum | Normal | SDC A, B ( no seismic design) | Each | Each | Peak Floor Acceleration | g | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 580 | EA 100 | NO | NO | Spraying & Dripping Leakage at drop joints - 0.01 leaks per drop. | Drop Joints Break - Major Leakage - 0.01 breaks per drop. |  |  |  | 1 | 1 |  |  |  | 1.5 | 2.25 |  |  |  | Not Specified | Not Specified |  |  |  | Not Specified | Not Specified |  |  |  | 0.4 | 0.4 |  |  |  | NO | NO | Marginal | Marginal | Marginal | Marginal | Replace sprinkler drops and minor water cleanup at broken joints. | Replace sprinkler drops and major water cleanup at broken joints |  |  |  | NO | NO |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | NO |  |  |  | 0% | 0% |  |  |  | 0 | 0 |  |  |  | One failure is expected per 100 units. Allowance included for MEP modifications for repair. | Not Given | By User | By User | Not Given | none | none |  |  |  | Yes | 2016-10-25 Clarification of cost added. | YES
D4011.072a | D4011.072a | Fire Sprinkler Drop Standard Threaded Steel - No Ceiling - 6 ft. long drop maximum, SDC C | Costing per 100 units, Standard threaded steel drop, 6 ft. long drop maximum | Normal | SDC C ( low seismic design) | Each | Each | Peak Floor Acceleration | g | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 581 | EA 100 | NO | NO | Spraying & Dripping Leakage at drop joints - 0.01 leaks per drop. | Drop Joints Break - Major Leakage - 0.01 breaks per drop. |  |  |  | 1 | 1 |  |  |  | 1.5 | 2.25 |  |  |  | Not Specified | Not Specified |  |  |  | Not Specified | Not Specified |  |  |  | 0.4 | 0.4 |  |  |  | NO | NO | Marginal | Marginal | Marginal | Marginal | Replace sprinkler drops and minor water cleanup at broken joints. | Replace sprinkler drops and major water cleanup at broken joints |  |  |  | NO | NO |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | NO |  |  |  | 0% | 0% |  |  |  | 0 | 0 |  |  |  | One failure is expected per 100 units. Allowance included for MEP modifications for repair. | Not Given | By User | By User | Not Given | none | none |  |  |  | Yes | 2016-10-25 Clarification of cost added. | YES
D4011.073a | D4011.073a | Fire Sprinkler Drop Standard Threaded Steel - No Ceiling - 6 ft. long drop maximum, SDC D, E, or F | Costing per 100 units, Standard threaded steel drop, 6 ft. long drop maximum | Normal | SDC D,E,F (high seismic design) | Each | Each | Peak Floor Acceleration | g | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 582 | EA 100 | NO | NO | Spraying & Dripping Leakage at drop joints - 0.01 leaks per drop. | Drop Joints Break - Major Leakage - 0.01 breaks per drop. |  |  |  | 1 | 1 |  |  |  | 2.6 | 3 |  |  |  | Not Specified | Not Specified |  |  |  | Not Specified | Not Specified |  |  |  | 0.4 | 0.4 |  |  |  | NO | NO | Marginal | Marginal | Marginal | Marginal | Replace sprinkler drops and minor water cleanup at broken joints. | Replace sprinkler drops and major water cleanup at broken joints |  |  |  | NO | NO |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | NO |  |  |  | 0% | 0% |  |  |  | 0 | 0 |  |  |  | One failure is expected per 100 units. Allowance included for MEP modifications for repair. | Not Given | By User | By User | Not Given | none | none |  |  |  | Yes | 2016-10-25 Clarification of cost added. | YES
D4011.074a | D4011.074a | Fire Sprinkler Drop Standard Threaded Steel - No Ceiling - 6 ft. long drop maximum, SDC D, E, or F (OSHPD or sim) | Costing per 100 units, Standard threaded steel drop, 6 ft. long drop maximum | Special Regulation (e.g. OSHPD) for sprinkler installations | SDC D,E,F ( high seismic design) | Each | Each | Peak Floor Acceleration | g | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 583 | EA 100 | NO | NO | Spraying & Dripping Leakage at drop joints - 0.01 leaks per drop. | Drop Joints Break - Major Leakage - 0.01 breaks per drop. |  |  |  | 1 | 1 |  |  |  | 3.75 | 4.5 |  |  |  | Not Specified | Not Specified |  |  |  | Not Specified | Not Specified |  |  |  | 0.4 | 0.4 |  |  |  | NO | NO | Marginal | Marginal | Marginal | Marginal | Replace sprinkler drops and minor water cleanup at broken joints. | Replace sprinkler drops and major water cleanup at broken joints |  |  |  | NO | NO |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | NO |  |  |  | 0% | 0% |  |  |  | 0 | 0 |  |  |  | One failure is expected per 100 units. Allowance included for MEP modifications for repair. | Not Given | By User | By User | Not Given | none | none |  |  |  | Yes | 2016-10-25 Clarification of cost added. | YES
D5011.011a | D5011.011a | Transformer/primary service - Capacity: <100 kVA - Unanchored equipment that is not vibration isolated - Equipment fragility only | Costing is per unit and is based upon 75 kVa. | Normal - Not designed for seismic loads | Unanchored equipment that is not vibration isolated | Each | Each | Peak Floor Acceleration | g | 1 | DS1 |  |  |  |  | Sequential |  |  |  |  | Seq(DS1) | 584 | KV 75 | YES | BLDG | Damaged, inoperative. |  |  |  |  | 1 |  |  |  |  | 1.01 |  |  |  |  | 0.6 |  |  |  |  | 0.1 |  |  |  |  | 0.6 |  |  |  |  | NO | NO | Superior | Average | Superior | Superior | Service and repair existing transformer. Transformer tower removed, repaired offsite, and reinstalled. |  |  |  |  | NO |  |  |  |  | NO |  |  |  |  | Not Applicable |  |  |  |  | 0% | 0 | [8 empty] | 0% | 0 | [8 empty] | NO |  |  |  |  | 0% |  |  |  |  | 0 |  |  |  |  | None | Not Given | By User | By User | Not Given | none |  |  |  |  | No | 2016-10-25 Clarification of cost added. | YES
D5011.011b | D5011.011b | Transformer/primary service - Capacity: 100 to <350 kVA - Unanchored equipment that is not vibration isolated - Equipment fragility only | Costing is per unit and is based upon 250 kVa. | Normal - Not designed for seismic loads | Unanchored equipment that is not vibration isolated | Each | Each | Peak Floor Acceleration | g | 1 | DS1 |  |  |  |  | Sequential |  |  |  |  | Seq(DS1) | 585 | KV 250 | YES | BLDG | Damaged, inoperative. |  |  |  |  | 1 |  |  |  |  | 1.01 |  |  |  |  | 0.6 |  |  |  |  | 0.1 |  |  |  |  | 0.6 |  |  |  |  | NO | NO | Superior | Average | Superior | Superior | Service and repair existing transformer. Transformer tower removed, repaired offsite, and reinstalled. |  |  |  |  | NO |  |  |  |  | NO |  |  |  |  | Not Applicable |  |  |  |  | 0% | 0 | [8 empty] | 0% | 0 | [8 empty] | NO |  |  |  |  | 0% |  |  |  |  | 0 |  |  |  |  | None | Not Given | By User | By User | Not Given | none |  |  |  |  | No | 2016-10-25 Clarification of cost added. | YES
D5011.011c | D5011.011c | Transformer/primary service - Capacity: 350 to <750 kVA - Unanchored equipment that is not vibration isolated - Equipment fragility only | Costing is per unit and is based upon 500 kVa. | Normal - Not designed for seismic loads | Unanchored equipment that is not vibration isolated | Each | Each | Peak Floor Acceleration | g | 1 | DS1 |  |  |  |  | Sequential |  |  |  |  | Seq(DS1) | 586 | KV 500 | YES | BLDG | Damaged, inoperative. |  |  |  |  | 1 |  |  |  |  | 1.01 |  |  |  |  | 0.6 |  |  |  |  | 0.1 |  |  |  |  | 0.6 |  |  |  |  | NO | NO | Superior | Average | Superior | Superior | Service and repair existing transformer. Transformer tower removed, repaired offsite, and reinstalled. |  |  |  |  | NO |  |  |  |  | NO |  |  |  |  | Not Applicable |  |  |  |  | 0% | 0 | [8 empty] | 0% | 0 | [8 empty] | NO |  |  |  |  | 0% |  |  |  |  | 0 |  |  |  |  | None | Not Given | By User | By User | Not Given | none |  |  |  |  | No | 2016-10-25 Clarification of cost added. | YES
D5011.011d | D5011.011d | Transformer/primary service - Capacity: 750 to 1500 kVA - Unanchored equipment that is not vibration isolated - Equipment fragility only | Costing is per unit and is based upon 1000 kVa. | Normal - Not designed for seismic loads | Unanchored equipment that is not vibration isolated | Each | Each | Peak Floor Acceleration | g | 1 | DS1 |  |  |  |  | Sequential |  |  |  |  | Seq(DS1) | 587 | KV 1000 | YES | BLDG | Damaged, inoperative. |  |  |  |  | 1 |  |  |  |  | 1.01 |  |  |  |  | 0.6 |  |  |  |  | 0.1 |  |  |  |  | 0.6 |  |  |  |  | NO | NO | Superior | Average | Superior | Superior | Service and repair existing transformer. Transformer tower removed, repaired offsite, and reinstalled. |  |  |  |  | NO |  |  |  |  | NO |  |  |  |  | Not Applicable |  |  |  |  | 0% | 0 | [8 empty] | 0% | 0 | [8 empty] | NO |  |  |  |  | 0% |  |  |  |  | 0 |  |  |  |  | None | Not Given | By User | By User | Not Given | none |  |  |  |  | No | 2016-10-25 Clarification of cost added. | YES
D5011.013a | D5011.013a | Transformer/primary service - Capacity: <100 kVA - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only | Costing is per unit and is based upon 75 kVa. | Normal - Designed for seismic loads but no special seismic certification | Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints | Each | Each | Peak Floor Acceleration | g | 2 | DS1 | DS2 |  |  |  | Mutually Exclusive | Mutually Exclusive |  |  |  | MutEx(DS1,DS2) | 588 | KV 75 | YES | BLDG | Anchorage failure. | Anchorage failure & Equipment damaged beyond repair. |  |  |  | 0.7 | 0.3 |  |  |  | By User | By User |  |  |  | User to Calculate | User to Calculate |  |  |  | User to Calculate | User to Calculate |  |  |  | By User | By User |  |  |  | NO | NO | Superior | Average | Superior | Superior | Repair anchorage and concrete pad and remount equipment. | Replace equipment including attached utilities in addition to repairing anchorage and concrete pad. Transformer tower removed, repaired offsite, and reinstalled. |  |  |  | NO | YES |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | NO |  |  |  | 0% | 0% |  |  |  | 0 | 0 |  |  |  | User to provide median demand and dispersion values. The values listed are default PACT values and do not represent the response of this component. | Not Given | By User | By User | Not Given | none | D5011.011a-DS1-1.JPG |  |  |  | No | 2016-10-25 Clarification of cost added. | YES
D5011.013b | D5011.013b | Transformer/primary service - Capacity: <100 kVA - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only | Costing is per unit and is based upon 75 kVa. | Normal - Designed for seismic loads but no special seismic certification | Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints | Each | Each | Peak Floor Acceleration | g | 1 | DS1 |  |  |  |  | Sequential |  |  |  |  | Seq(DS1) | 589 | KV 75 | YES | BLDG | Damaged, inoperative but anchorage is OK. |  |  |  |  | 1 |  |  |  |  | 3.05 |  |  |  |  | 0.6 |  |  |  |  | 0.1 |  |  |  |  | 0.5 |  |  |  |  | NO | NO | Superior | Average | Superior | Superior | Service and repair existing transformer. Transformer tower removed, repaired offsite, and reinstalled. |  |  |  |  | NO |  |  |  |  | NO |  |  |  |  | Not Applicable |  |  |  |  | 0% | 0 | [8 empty] | 0% | 0 | [8 empty] | NO |  |  |  |  | 0% |  |  |  |  | 0 |  |  |  |  | None | Not Given | By User | By User | Not Given | none |  |  |  |  | No | 2016-10-25 Clarification of cost added. | YES
D5011.013c | D5011.013c | Transformer/primary service - Capacity: <100 kVA - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | Costing is per unit and is based upon 75 kVa. | Normal - Designed for seismic loads but no special seismic certification | Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints | Each | Each | Peak Floor Acceleration | g | 3 | DS1 | DS2 | DS3 |  |  | Mutually Exclusive | Mutually Exclusive | Mutually Exclusive |  |  | MutEx(DS1,DS2,DS3) | 590 | KV 75 | YES | BLDG | Anchorage failure. | Anchorage failure & Equipment damaged beyond repair. | Damaged, Inoperative but anchorage is OK. |  |  | 0.35 | 0.15 | 0.5 |  |  | By User | By User | By User |  |  | User to Calculate | User to Calculate | User to Calculate |  |  | User to Calculate | User to Calculate | User to Calculate |  |  | By User | By User | By User |  |  | NO | NO | Superior | Average | Superior | Superior | Repair anchorage and concrete pad and remount equipment. | Replace equipment including attached utilities in addition to repairing anchorage and concrete pad. Transformer tower removed, repaired offsite, and reinstalled. | Service and repair existing transformer. Transformer tower removed, repaired offsite, and reinstalled. |  |  | NO | YES | NO |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | NO | NO |  |  | 0% | 0% | 0% |  |  | 0 | 0 | 0 |  |  | User to provide median demand and dispersion values. The values listed are default PACT values and do not represent the response of this component. | Not Given | By User | By User | Not Given | none | D5011.011a-DS1-1.JPG | none |  |  | No | 2016-10-25 Clarification of cost added. | YES
D5011.013d | D5011.013d | Transformer/primary service - Capacity: 100 to <350 kVA - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only | Costing is per unit and is based upon 250 kVa. | Normal - Designed for seismic loads but no special seismic certification | Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints | Each | Each | Peak Floor Acceleration | g | 2 | DS1 | DS2 |  |  |  | Mutually Exclusive | Mutually Exclusive |  |  |  | MutEx(DS1,DS2) | 591 | KV 250 | YES | BLDG | Anchorage failure. | Anchorage failure & Equipment damaged beyond repair. |  |  |  | 0.7 | 0.3 |  |  |  | By User | By User |  |  |  | User to Calculate | User to Calculate |  |  |  | User to Calculate | User to Calculate |  |  |  | By User | By User |  |  |  | NO | NO | Superior | Average | Superior | Superior | Repair anchorage and concrete pad and remount equipment. | Replace equipment including attached utilities in addition to repairing anchorage and concrete pad. Transformer tower removed, repaired offsite, and reinstalled. |  |  |  | NO | YES |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | NO |  |  |  | 0% | 0% |  |  |  | 0 | 0 |  |  |  | User to provide median demand and dispersion values. The values listed are default PACT values and do not represent the response of this component. | Not Given | By User | By User | Not Given | none | D5011.011a-DS1-1.JPG |  |  |  | No | 2016-10-25 Clarification of cost added. | YES
D5011.013e | D5011.013e | Transformer/primary service - Capacity: 100 to <350 kVA - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only | Costing is per unit and is based upon 250 kVa. | Normal - Designed for seismic loads but no special seismic certification | Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints | Each | Each | Peak Floor Acceleration | g | 1 | DS1 |  |  |  |  | Sequential |  |  |  |  | Seq(DS1) | 592 | KV 250 | YES | BLDG | Damaged, inoperative but anchorage is OK. |  |  |  |  | 1 |  |  |  |  | 3.05 |  |  |  |  | 0.6 |  |  |  |  | 0.1 |  |  |  |  | 0.5 |  |  |  |  | NO | NO | Superior | Average | Superior | Superior | Service and repair existing transformer. Transformer tower removed, repaired offsite, and reinstalled. |  |  |  |  | NO |  |  |  |  | NO |  |  |  |  | Not Applicable |  |  |  |  | 0% | 0 | [8 empty] | 0% | 0 | [8 empty] | NO |  |  |  |  | 0% |  |  |  |  | 0 |  |  |  |  | None | Not Given | By User | By User | Not Given | none |  |  |  |  | No | 2016-10-25 Clarification of cost added. | YES
D5011.013f | D5011.013f | Transformer/primary service - Capacity: 100 to <350 kVA - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | Costing is per unit and is based upon 250 kVa. | Normal - Designed for seismic loads but no special seismic certification | Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints | Each | Each | Peak Floor Acceleration | g | 3 | DS1 | DS2 | DS3 |  |  | Mutually Exclusive | Mutually Exclusive | Mutually Exclusive |  |  | MutEx(DS1,DS2,DS3) | 593 | KV 250 | YES | BLDG | Anchorage failure. | Anchorage failure & Equipment damaged beyond repair. | Damaged, Inoperative but anchorage is OK. |  |  | 0.35 | 0.15 | 0.5 |  |  | By User | By User | By User |  |  | User to Calculate | User to Calculate | User to Calculate |  |  | User to Calculate | User to Calculate | User to Calculate |  |  | By User | By User | By User |  |  | NO | NO | Superior | Average | Superior | Superior | Repair anchorage and concrete pad and remount equipment. | Replace equipment including attached utilities in addition to repairing anchorage and concrete pad. Transformer tower removed, repaired offsite, and reinstalled. | Service and repair existing transformer. Transformer tower removed, repaired offsite, and reinstalled. |  |  | NO | YES | NO |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | NO | NO |  |  | 0% | 0% | 0% |  |  | 0 | 0 | 0 |  |  | User to provide median demand and dispersion values. The values listed are default PACT values and do not represent the response of this component. | Not Given | By User | By User | Not Given | none | D5011.011a-DS1-1.JPG | none |  |  | No | 2016-10-25 Clarification of cost added. | YES
D5011.013g | D5011.013g | Transformer/primary service - Capacity: 350 to <750 kVA - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only | Costing is per unit and is based upon 500 kVa. | Normal - Designed for seismic loads but no special seismic certification | Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints | Each | Each | Peak Floor Acceleration | g | 2 | DS1 | DS2 |  |  |  | Mutually Exclusive | Mutually Exclusive |  |  |  | MutEx(DS1,DS2) | 594 | KV 500 | YES | BLDG | Anchorage failure. | Anchorage failure & Equipment damaged beyond repair. |  |  |  | 0.7 | 0.3 |  |  |  | By User | By User |  |  |  | User to Calculate | User to Calculate |  |  |  | User to Calculate | User to Calculate |  |  |  | By User | By User |  |  |  | NO | NO | Superior | Average | Superior | Superior | Repair anchorage and concrete pad and remount equipment. | Replace equipment including attached utilities in addition to repairing anchorage and concrete pad. Transformer tower removed, repaired offsite, and reinstalled. |  |  |  | NO | YES |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | NO |  |  |  | 0% | 0% |  |  |  | 0 | 0 |  |  |  | User to provide median demand and dispersion values. The values listed are default PACT values and do not represent the response of this component. | Not Given | By User | By User | Not Given | none | D5011.011a-DS1-1.JPG |  |  |  | No | 2016-10-25 Clarification of cost added. | YES
D5011.013h | D5011.013h | Transformer/primary service - Capacity: 350 to <750 kVA - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only | Costing is per unit and is based upon 500 kVa. | Normal - Designed for seismic loads but no special seismic certification | Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints | Each | Each | Peak Floor Acceleration | g | 1 | DS1 |  |  |  |  | Sequential |  |  |  |  | Seq(DS1) | 595 | KV 500 | YES | BLDG | Damaged, inoperative but anchorage is OK. |  |  |  |  | 1 |  |  |  |  | 3.05 |  |  |  |  | 0.6 |  |  |  |  | 0.1 |  |  |  |  | 0.5 |  |  |  |  | NO | NO | Superior | Average | Superior | Superior | Service and repair existing transformer. Transformer tower removed, repaired offsite, and reinstalled. |  |  |  |  | NO |  |  |  |  | NO |  |  |  |  | Not Applicable |  |  |  |  | 0% | 0 | [8 empty] | 0% | 0 | [8 empty] | NO |  |  |  |  | 0% |  |  |  |  | 0 |  |  |  |  | None | Not Given | By User | By User | Not Given | none |  |  |  |  | No | 2016-10-25 Clarification of cost added. | YES
D5011.013i | D5011.013i | Transformer/primary service - Capacity: 350 to <750 kVA - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | Costing is per unit and is based upon 500 kVa. | Normal - Designed for seismic loads but no special seismic certification | Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints | Each | Each | Peak Floor Acceleration | g | 3 | DS1 | DS2 | DS3 |  |  | Mutually Exclusive | Mutually Exclusive | Mutually Exclusive |  |  | MutEx(DS1,DS2,DS3) | 596 | KV 500 | YES | BLDG | Anchorage failure. | Anchorage failure & Equipment damaged beyond repair. | Damaged, Inoperative but anchorage is OK. |  |  | 0.35 | 0.15 | 0.5 |  |  | By User | By User | By User |  |  | User to Calculate | User to Calculate | User to Calculate |  |  | User to Calculate | User to Calculate | User to Calculate |  |  | By User | By User | By User |  |  | NO | NO | Superior | Average | Superior | Superior | Repair anchorage and concrete pad and remount equipment. | Replace equipment including attached utilities in addition to repairing anchorage and concrete pad. Transformer tower removed, repaired offsite, and reinstalled. | Service and repair existing transformer. Transformer tower removed, repaired offsite, and reinstalled. |  |  | NO | YES | NO |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | NO | NO |  |  | 0% | 0% | 0% |  |  | 0 | 0 | 0 |  |  | User to provide median demand and dispersion values. The values listed are default PACT values and do not represent the response of this component. | Not Given | By User | By User | Not Given | none | D5011.011a-DS1-1.JPG | none |  |  | No | 2016-10-25 Clarification of cost added. | YES
D5011.013j | D5011.013j | Transformer/primary service - Capacity: 750 to 1500 kVA - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only | Costing is per unit and is based upon 1000 kVa. | Normal - Designed for seismic loads but no special seismic certification | Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints | Each | Each | Peak Floor Acceleration | g | 2 | DS1 | DS2 |  |  |  | Mutually Exclusive | Mutually Exclusive |  |  |  | MutEx(DS1,DS2) | 597 | KV 1000 | YES | BLDG | Anchorage failure. | Anchorage failure & Equipment damaged beyond repair. |  |  |  | 0.7 | 0.3 |  |  |  | By User | By User |  |  |  | User to Calculate | User to Calculate |  |  |  | User to Calculate | User to Calculate |  |  |  | By User | By User |  |  |  | NO | NO | Superior | Average | Superior | Superior | Repair anchorage and concrete pad and remount equipment. | Replace equipment including attached utilities in addition to repairing anchorage and concrete pad. Transformer tower removed, repaired offsite, and reinstalled. |  |  |  | NO | YES |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | NO |  |  |  | 0% | 0% |  |  |  | 0 | 0 |  |  |  | User to provide median demand and dispersion values. The values listed are default PACT values and do not represent the response of this component. | Not Given | By User | By User | Not Given | none | D5011.011a-DS1-1.JPG |  |  |  | No | 2016-10-25 Clarification of cost added. | YES
D5011.013k | D5011.013k | Transformer/primary service - Capacity: 750 to 1500 kVA - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only | Costing is per unit and is based upon 1000 kVa. | Normal - Designed for seismic loads but no special seismic certification | Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints | Each | Each | Peak Floor Acceleration | g | 1 | DS1 |  |  |  |  | Sequential |  |  |  |  | Seq(DS1) | 598 | KV 1000 | YES | BLDG | Damaged, inoperative but anchorage is OK. |  |  |  |  | 1 |  |  |  |  | 3.05 |  |  |  |  | 0.6 |  |  |  |  | 0.1 |  |  |  |  | 0.5 |  |  |  |  | NO | NO | Superior | Average | Superior | Superior | Service and repair existing transformer. Transformer tower removed, repaired offsite, and reinstalled. |  |  |  |  | NO |  |  |  |  | NO |  |  |  |  | Not Applicable |  |  |  |  | 0% | 0 | [8 empty] | 0% | 0 | [8 empty] | NO |  |  |  |  | 0% |  |  |  |  | 0 |  |  |  |  | None | Not Given | By User | By User | Not Given | none |  |  |  |  | No | 2016-10-25 Clarification of cost added. | YES
D5011.013l | D5011.013l | Transformer/primary service - Capacity: 750 to 1500 kVA - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | Costing is per unit and is based upon 1000 kVa. | Normal - Designed for seismic loads but no special seismic certification | Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints | Each | Each | Peak Floor Acceleration | g | 3 | DS1 | DS2 | DS3 |  |  | Mutually Exclusive | Mutually Exclusive | Mutually Exclusive |  |  | MutEx(DS1,DS2,DS3) | 599 | KV 1000 | YES | BLDG | Anchorage failure. | Anchorage failure & Equipment damaged beyond repair. | Damaged, Inoperative but anchorage is OK. |  |  | 0.35 | 0.15 | 0.5 |  |  | By User | By User | By User |  |  | User to Calculate | User to Calculate | User to Calculate |  |  | User to Calculate | User to Calculate | User to Calculate |  |  | By User | By User | By User |  |  | NO | NO | Superior | Average | Superior | Superior | Repair anchorage and concrete pad and remount equipment. | Replace equipment including attached utilities in addition to repairing anchorage and concrete pad. Transformer tower removed, repaired offsite, and reinstalled. | Service and repair existing transformer. Transformer tower removed, repaired offsite, and reinstalled. |  |  | NO | YES | NO |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | NO | NO |  |  | 0% | 0% | 0% |  |  | 0 | 0 | 0 |  |  | User to provide median demand and dispersion values. The values listed are default PACT values and do not represent the response of this component. | Not Given | By User | By User | Not Given | none | D5011.011a-DS1-1.JPG | none |  |  | No | 2016-10-25 Clarification of cost added. | YES
D5012.013a | D5012.013a | Motor Control Center - Capacity: all - Unanchored equipment that is not vibration isolated - Equipment fragility only | Costing is per unit. | Normal - Not designed for seismic loads | Unanchored equipment that is not vibration isolated | Each | Each | Peak Floor Acceleration | g | 1 | DS1 |  |  |  |  | Sequential |  |  |  |  | Seq(DS1) | 600 | EA 1 | YES | BLDG | Damaged, inoperative |  |  |  |  | 1 |  |  |  |  | 0.73 |  |  |  |  | 0.45 |  |  |  |  | 0.1 |  |  |  |  | 0.45 |  |  |  |  | NO | NO | Superior | Average | Superior | Superior | Replace equipment. |  |  |  |  | NO |  |  |  |  | NO |  |  |  |  | Not Applicable |  |  |  |  | 0% | 0 | [8 empty] | 0% | 0 | [8 empty] | NO |  |  |  |  | 0% |  |  |  |  | 0 |  |  |  |  | None | Not Given | By User | By User | Not Given | none |  |  |  |  | No | None | NO
D5012.013b | D5012.013b | Motor Control Center - Capacity: all - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only | Costing is per unit. | Normal - Designed for seismic loads but no special seismic certification | Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints | Each | Each | Peak Floor Acceleration | g | 2 | DS1 | DS2 |  |  |  | Mutually Exclusive | Mutually Exclusive |  |  |  | MutEx(DS1,DS2) | 601 | EA 1 | YES | BLDG | Anchorage failure. | Anchorage failure & Equipment damaged beyond repair. |  |  |  | 0.7 | 0.3 |  |  |  | By User | By User |  |  |  | User to Calculate | User to Calculate |  |  |  | User to Calculate | User to Calculate |  |  |  | By User | By User |  |  |  | NO | NO | Superior | Average | Superior | Superior | Repair anchorage and concrete pad and remount equipment. | Replace equipment including attached utilities in addition to repairing anchorage and concrete pad. |  |  |  | NO | NO |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | NO |  |  |  | 0% | 0% |  |  |  | 0 | 0 |  |  |  | User to provide median demand and dispersion values. The values listed are default PACT values and do not represent the response of this component. | Not Given | By User | By User | Not Given | none | D5010.011a-DS1-1.JPG |  |  |  | No | None | NO
D5012.013c | D5012.013c | Motor Control Center - Capacity: all - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only | Costing is per unit. | Normal - Designed for seismic loads but no special seismic certification | Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints | Each | Each | Peak Floor Acceleration | g | 1 | DS1 |  |  |  |  | Sequential |  |  |  |  | Seq(DS1) | 602 | EA 1 | YES | BLDG | Damaged, inoperative but anchorage is OK. |  |  |  |  | 1 |  |  |  |  | 2.5 |  |  |  |  | 0.4 |  |  |  |  | 0.1 |  |  |  |  | 0.4 |  |  |  |  | NO | NO | Superior | Average | Superior | Superior | Replace equipment. |  |  |  |  | NO |  |  |  |  | NO |  |  |  |  | Not Applicable |  |  |  |  | 0% | 0 | [8 empty] | 0% | 0 | [8 empty] | NO |  |  |  |  | 0% |  |  |  |  | 0 |  |  |  |  | None | Not Given | By User | By User | Not Given | none |  |  |  |  | No | None | NO
D5012.013d | D5012.013d | Motor Control Center - Capacity: all - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | Costing is per unit. | Normal - Designed for seismic loads but no special seismic certification | Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints | Each | Each | Peak Floor Acceleration | g | 3 | DS1 | DS2 | DS3 |  |  | Mutually Exclusive | Mutually Exclusive | Mutually Exclusive |  |  | MutEx(DS1,DS2,DS3) | 603 | EA 1 | YES | BLDG | Anchorage failure. | Anchorage failure & Equipment damaged beyond repair. | Damaged, Inoperative but anchorage is OK. |  |  | 0.35 | 0.15 | 0.5 |  |  | By User | By User | By User |  |  | User to Calculate | User to Calculate | User to Calculate |  |  | User to Calculate | User to Calculate | User to Calculate |  |  | By User | By User | By User |  |  | NO | NO | Superior | Average | Superior | Superior | If anchored repair anchorage and concrete pad and remount equipment. | Replace equipment including attached utilities in addition to repairing anchorage and concrete pad if anchored. | Replace equipment. |  |  | NO | NO | NO |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | NO | NO |  |  | 0% | 0% | 0% |  |  | 0 | 0 | 0 |  |  | User to provide median demand and dispersion values. The values listed are default PACT values and do not represent the response of this component. | Not Given | By User | By User | Not Given | none | D5010.011a-DS1-1.JPG | none |  |  | No | None | NO
D5012.021a | D5012.021a | Low Voltage Switchgear - Capacity: 100 to <350 Amp - Unanchored equipment that is not vibration isolated - Equipment fragility only | Costing is per unit and is based upon 225 Amp. | Normal - Not designed for seismic loads | Unanchored equipment that is not vibration isolated | Each | Each | Peak Floor Acceleration | g | 1 | DS1 |  |  |  |  | Sequential |  |  |  |  | Seq(DS1) | 604 | AP 225 | YES | FLR | Damaged, inoperative. |  |  |  |  | 1 |  |  |  |  | 1.28 |  |  |  |  | 0.4 |  |  |  |  | 0.1 |  |  |  |  | 0.4 |  |  |  |  | NO | NO | Superior | Average | Superior | Superior | Replace insulator. |  |  |  |  | NO |  |  |  |  | NO |  |  |  |  | Not Applicable |  |  |  |  | 0% | 0 | [8 empty] | 0% | 0 | [8 empty] | NO |  |  |  |  | 0% |  |  |  |  | 0 |  |  |  |  | None | Not Given | By User | By User | Not Given | none |  |  |  |  | No | None | YES
D5012.021b | D5012.021b | Low Voltage Switchgear - Capacity: 350 to <750 Amp - Unanchored equipment that is not vibration isolated - Equipment fragility only | Costing is per unit and is based upon 400 Amp. | Normal - Not designed for seismic loads | Unanchored equipment that is not vibration isolated | Each | Each | Peak Floor Acceleration | g | 1 | DS1 |  |  |  |  | Sequential |  |  |  |  | Seq(DS1) | 605 | AP 400 | YES | FLR | Damaged, inoperative. |  |  |  |  | 1 |  |  |  |  | 1.28 |  |  |  |  | 0.4 |  |  |  |  | 0.1 |  |  |  |  | 0.4 |  |  |  |  | NO | NO | Superior | Average | Superior | Superior | Replace insulator. |  |  |  |  | NO |  |  |  |  | NO |  |  |  |  | Not Applicable |  |  |  |  | 0% | 0 | [8 empty] | 0% | 0 | [8 empty] | NO |  |  |  |  | 0% |  |  |  |  | 0 |  |  |  |  | None | Not Given | By User | By User | Not Given | none |  |  |  |  | No | None | YES
D5012.021c | D5012.021c | Low Voltage Switchgear - Capacity: 750 to <1200 Amp - Unanchored equipment that is not vibration isolated - Equipment fragility only | Costing is per unit and is based upon 800 Amp. | Normal - Not designed for seismic loads | Unanchored equipment that is not vibration isolated | Each | Each | Peak Floor Acceleration | g | 1 | DS1 |  |  |  |  | Sequential |  |  |  |  | Seq(DS1) | 606 | AP 800 | YES | FLR | Damaged, inoperative. |  |  |  |  | 1 |  |  |  |  | 1.28 |  |  |  |  | 0.4 |  |  |  |  | 0.1 |  |  |  |  | 0.4 |  |  |  |  | NO | NO | Superior | Average | Superior | Superior | Replace insulator. |  |  |  |  | NO |  |  |  |  | NO |  |  |  |  | Not Applicable |  |  |  |  | 0% | 0 | [8 empty] | 0% | 0 | [8 empty] | NO |  |  |  |  | 0% |  |  |  |  | 0 |  |  |  |  | None | Not Given | By User | By User | Not Given | none |  |  |  |  | No | None | YES
D5012.021d | D5012.021d | Low Voltage Switchgear - Capacity: 1200 to 2000 Amp - Unanchored equipment that is not vibration isolated - Equipment fragility only | Costing is per unit and is based upon 1600 Amp. | Normal - Not designed for seismic loads | Unanchored equipment that is not vibration isolated | Each | Each | Peak Floor Acceleration | g | 1 | DS1 |  |  |  |  | Sequential |  |  |  |  | Seq(DS1) | 607 | AP 1600 | YES | FLR | Damaged, inoperative. |  |  |  |  | 1 |  |  |  |  | 1.28 |  |  |  |  | 0.4 |  |  |  |  | 0.1 |  |  |  |  | 0.4 |  |  |  |  | NO | NO | Superior | Average | Superior | Superior | Replace insulator. |  |  |  |  | YES |  |  |  |  | NO |  |  |  |  | Not Applicable |  |  |  |  | 0% | 0 | [8 empty] | 0% | 0 | [8 empty] | NO |  |  |  |  | 0% |  |  |  |  | 0 |  |  |  |  | None | Not Given | By User | By User | Not Given | none |  |  |  |  | No | None | YES
D5012.023a | D5012.023a | Low Voltage Switchgear - Capacity: 100 to <350 Amp - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only | Costing is per unit and is based upon 225 Amp. | Normal - Designed for seismic loads but no special seismic certification | Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints | Each | Each | Peak Floor Acceleration | g | 2 | DS1 | DS2 |  |  |  | Mutually Exclusive | Mutually Exclusive |  |  |  | MutEx(DS1,DS2) | 608 | AP 225 | YES | FLR | Anchorage failure. | Anchorage failure & Equipment damaged beyond repair. |  |  |  | 0.7 | 0.3 |  |  |  | By User | By User |  |  |  | User to Calculate | User to Calculate |  |  |  | User to Calculate | User to Calculate |  |  |  | By User | By User |  |  |  | NO | NO | Superior | Average | Superior | Superior | Repair anchorage and concrete pad and remount equipment. | Replace equipment including attached utilities in addition to repairing anchorage and concrete pad. |  |  |  | NO | NO |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | NO |  |  |  | 0% | 0% |  |  |  | 0 | 0 |  |  |  | User to provide median demand and dispersion values. The values listed are default PACT values and do not represent the response of this component. | Not Given | By User | By User | Not Given | none | none |  |  |  | No | None | YES
D5012.023b | D5012.023b | Low Voltage Switchgear - Capacity: 100 to <350 Amp - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only | Costing is per unit and is based upon 225 Amp. | Normal - Designed for seismic loads but no special seismic certification | Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints | Each | Each | Peak Floor Acceleration | g | 1 | DS1 |  |  |  |  | Sequential |  |  |  |  | Seq(DS1) | 609 | AP 225 | YES | FLR | Damaged, inoperative but anchorage is OK. |  |  |  |  | 1 |  |  |  |  | 2.4 |  |  |  |  | 0.4 |  |  |  |  | 0.1 |  |  |  |  | 0.4 |  |  |  |  | NO | NO | Superior | Average | Superior | Superior | Replace fiberglass insulator supporting the vertical bus bars in the rear of the switchgear assembly |  |  |  |  | NO |  |  |  |  | NO |  |  |  |  | Not Applicable |  |  |  |  | 0% | 0 | [8 empty] | 0% | 0 | [8 empty] | NO |  |  |  |  | 0% |  |  |  |  | 0 |  |  |  |  | None | Not Given | By User | By User | Not Given | none |  |  |  |  | No | None | YES
D5012.023c | D5012.023c | Low Voltage Switchgear - Capacity: 100 to <350 Amp - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | Costing is per unit and is based upon 225 Amp. | Normal - Designed for seismic loads but no special seismic certification | Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints | Each | Each | Peak Floor Acceleration | g | 3 | DS1 | DS2 | DS3 |  |  | Mutually Exclusive | Mutually Exclusive | Mutually Exclusive |  |  | MutEx(DS1,DS2,DS3) | 610 | AP 225 | YES | FLR | Anchorage failure. | Anchorage failure & Equipment damaged beyond repair. | Damaged, Inoperative but anchorage is OK. |  |  | 0.35 | 0.15 | 0.5 |  |  | By User | By User | By User |  |  | User to Calculate | User to Calculate | User to Calculate |  |  | User to Calculate | User to Calculate | User to Calculate |  |  | By User | By User | By User |  |  | NO | NO | Superior | Average | Superior | Superior | Repair anchorage and concrete pad and remount equipment. | Replace equipment including attached utilities in addition to repairing anchorage and concrete pad. | Replace fiberglass insulator supporting the vertical bus bars in the rear of the switchgear assembly |  |  | NO | NO | NO |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | NO | NO |  |  | 0% | 0% | 0% |  |  | 0 | 0 | 0 |  |  | User to provide median demand and dispersion values. The values listed are default PACT values and do not represent the response of this component. | Not Given | By User | By User | Not Given | none | none | none |  |  | No | None | YES
D5012.023d | D5012.023d | Low Voltage Switchgear - Capacity: 350 to <750 Amp - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only | Costing is per unit and is based upon 400 Amp. | Normal - Designed for seismic loads but no special seismic certification | Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints | Each | Each | Peak Floor Acceleration | g | 2 | DS1 | DS2 |  |  |  | Mutually Exclusive | Mutually Exclusive |  |  |  | MutEx(DS1,DS2) | 611 | AP 400 | YES | FLR | Anchorage failure. | Anchorage failure & Equipment damaged beyond repair. |  |  |  | 0.7 | 0.3 |  |  |  | By User | By User |  |  |  | User to Calculate | User to Calculate |  |  |  | User to Calculate | User to Calculate |  |  |  | By User | By User |  |  |  | NO | NO | Superior | Average | Superior | Superior | Repair anchorage and concrete pad and remount equipment. | Replace equipment including attached utilities in addition to repairing anchorage and concrete pad. |  |  |  | NO | NO |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | NO |  |  |  | 0% | 0% |  |  |  | 0 | 0 |  |  |  | User to provide median demand and dispersion values. The values listed are default PACT values and do not represent the response of this component. | Not Given | By User | By User | Not Given | none | none |  |  |  | No | None | YES
D5012.023e | D5012.023e | Low Voltage Switchgear - Capacity: 350 to <750 Amp - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only | Costing is per unit and is based upon 400 Amp. | Normal - Designed for seismic loads but no special seismic certification | Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints | Each | Each | Peak Floor Acceleration | g | 1 | DS1 |  |  |  |  | Sequential |  |  |  |  | Seq(DS1) | 612 | AP 400 | YES | FLR | Damaged, inoperative but anchorage is OK. |  |  |  |  | 1 |  |  |  |  | 2.4 |  |  |  |  | 0.4 |  |  |  |  | 0.1 |  |  |  |  | 0.4 |  |  |  |  | NO | NO | Superior | Average | Superior | Superior | Replace fiberglass insulator supporting the vertical bus bars in the rear of the switchgear assembly |  |  |  |  | NO |  |  |  |  | NO |  |  |  |  | Not Applicable |  |  |  |  | 0% | 0 | [8 empty] | 0% | 0 | [8 empty] | NO |  |  |  |  | 0% |  |  |  |  | 0 |  |  |  |  | None | Not Given | By User | By User | Not Given | none |  |  |  |  | No | None | YES
D5012.023f | D5012.023f | Low Voltage Switchgear - Capacity: 350 to <750 Amp - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | Costing is per unit and is based upon 400 Amp. | Normal - Designed for seismic loads but no special seismic certification | Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints | Each | Each | Peak Floor Acceleration | g | 3 | DS1 | DS2 | DS3 |  |  | Mutually Exclusive | Mutually Exclusive | Mutually Exclusive |  |  | MutEx(DS1,DS2,DS3) | 613 | AP 400 | YES | FLR | Anchorage failure. | Anchorage failure & Equipment damaged beyond repair. | Damaged, Inoperative but anchorage is OK. |  |  | 0.35 | 0.15 | 0.5 |  |  | By User | By User | By User |  |  | User to Calculate | User to Calculate | User to Calculate |  |  | User to Calculate | User to Calculate | User to Calculate |  |  | By User | By User | By User |  |  | NO | NO | Superior | Average | Superior | Superior | Repair anchorage and concrete pad and remount equipment. | Replace equipment including attached utilities in addition to repairing anchorage and concrete pad. | Replace fiberglass insulator supporting the vertical bus bars in the rear of the switchgear assembly |  |  | NO | NO | NO |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | NO | NO |  |  | 0% | 0% | 0% |  |  | 0 | 0 | 0 |  |  | User to provide median demand and dispersion values. The values listed are default PACT values and do not represent the response of this component. | Not Given | By User | By User | Not Given | none | none | none |  |  | No | None | YES
D5012.023g | D5012.023g | Low Voltage Switchgear - Capacity: 750 to <1200 Amp - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only | Costing is per unit and is based upon 800 Amp. | Normal - Designed for seismic loads but no special seismic certification | Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints | Each | Each | Peak Floor Acceleration | g | 2 | DS1 | DS2 |  |  |  | Mutually Exclusive | Mutually Exclusive |  |  |  | MutEx(DS1,DS2) | 614 | AP 800 | YES | FLR | Anchorage failure. | Anchorage failure & Equipment damaged beyond repair. |  |  |  | 0.7 | 0.3 |  |  |  | By User | By User |  |  |  | User to Calculate | User to Calculate |  |  |  | User to Calculate | User to Calculate |  |  |  | By User | By User |  |  |  | NO | NO | Superior | Average | Superior | Superior | Repair anchorage and concrete pad and remount equipment. | Replace equipment including attached utilities in addition to repairing anchorage and concrete pad. |  |  |  | NO | NO |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | NO |  |  |  | 0% | 0% |  |  |  | 0 | 0 |  |  |  | User to provide median demand and dispersion values. The values listed are default PACT values and do not represent the response of this component. | Not Given | By User | By User | Not Given | none | none |  |  |  | No | None | YES
D5012.023h | D5012.023h | Low Voltage Switchgear - Capacity: 750 to <1200 Amp - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only | Costing is per unit and is based upon 800 Amp. | Normal - Designed for seismic loads but no special seismic certification | Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints | Each | Each | Peak Floor Acceleration | g | 1 | DS1 |  |  |  |  | Sequential |  |  |  |  | Seq(DS1) | 615 | AP 800 | YES | FLR | Damaged, inoperative but anchorage is OK. |  |  |  |  | 1 |  |  |  |  | 2.4 |  |  |  |  | 0.4 |  |  |  |  | 0.1 |  |  |  |  | 0.4 |  |  |  |  | NO | NO | Superior | Average | Superior | Superior | Replace fiberglass insulator supporting the vertical bus bars in the rear of the switchgear assembly |  |  |  |  | NO |  |  |  |  | NO |  |  |  |  | Not Applicable |  |  |  |  | 0% | 0 | [8 empty] | 0% | 0 | [8 empty] | NO |  |  |  |  | 0% |  |  |  |  | 0 |  |  |  |  | None | Not Given | By User | By User | Not Given | none |  |  |  |  | No | None | YES
D5012.023i | D5012.023i | Low Voltage Switchgear - Capacity: 750 to <1200 Amp - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | Costing is per unit and is based upon 800 Amp. | Normal - Designed for seismic loads but no special seismic certification | Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints | Each | Each | Peak Floor Acceleration | g | 3 | DS1 | DS2 | DS3 |  |  | Mutually Exclusive | Mutually Exclusive | Mutually Exclusive |  |  | MutEx(DS1,DS2,DS3) | 616 | AP 800 | YES | FLR | Anchorage failure. | Anchorage failure & Equipment damaged beyond repair. | Damaged, Inoperative but anchorage is OK. |  |  | 0.35 | 0.15 | 0.5 |  |  | By User | By User | By User |  |  | User to Calculate | User to Calculate | User to Calculate |  |  | User to Calculate | User to Calculate | User to Calculate |  |  | By User | By User | By User |  |  | NO | NO | Superior | Average | Superior | Superior | Repair anchorage and concrete pad and remount equipment. | Replace equipment including attached utilities in addition to repairing anchorage and concrete pad. | Replace fiberglass insulator supporting the vertical bus bars in the rear of the switchgear assembly |  |  | NO | NO | NO |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | NO | NO |  |  | 0% | 0% | 0% |  |  | 0 | 0 | 0 |  |  | User to provide median demand and dispersion values. The values listed are default PACT values and do not represent the response of this component. | Not Given | By User | By User | Not Given | none | none | none |  |  | No | None | YES
D5012.023j | D5012.023j | Low Voltage Switchgear - Capacity: 1200 to 2000 Amp - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only | Costing is per unit and is based upon 1600 Amp. | Normal - Designed for seismic loads but no special seismic certification | Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints | Each | Each | Peak Floor Acceleration | g | 2 | DS1 | DS2 |  |  |  | Mutually Exclusive | Mutually Exclusive |  |  |  | MutEx(DS1,DS2) | 617 | AP 1600 | YES | FLR | Anchorage failure. | Anchorage failure & Equipment damaged beyond repair. |  |  |  | 0.7 | 0.3 |  |  |  | By User | By User |  |  |  | User to Calculate | User to Calculate |  |  |  | User to Calculate | User to Calculate |  |  |  | By User | By User |  |  |  | NO | NO | Superior | Average | Superior | Superior | Repair anchorage and concrete pad and remount equipment. | Replace equipment including attached utilities in addition to repairing anchorage and concrete pad. |  |  |  | NO | YES |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | NO |  |  |  | 0% | 0% |  |  |  | 0 | 0 |  |  |  | User to provide median demand and dispersion values. The values listed are default PACT values and do not represent the response of this component. | Not Given | By User | By User | Not Given | none | none |  |  |  | No | None | YES
D5012.023k | D5012.023k | Low Voltage Switchgear - Capacity: 1200 to 2000 Amp - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only | Costing is per unit and is based upon 1600 Amp. | Normal - Designed for seismic loads but no special seismic certification | Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints | Each | Each | Peak Floor Acceleration | g | 1 | DS1 |  |  |  |  | Sequential |  |  |  |  | Seq(DS1) | 618 | AP 1600 | YES | FLR | Damaged, inoperative but anchorage is OK. |  |  |  |  | 1 |  |  |  |  | 2.4 |  |  |  |  | 0.4 |  |  |  |  | 0.1 |  |  |  |  | 0.4 |  |  |  |  | NO | NO | Superior | Average | Superior | Superior | Replace fiberglass insulator supporting the vertical bus bars in the rear of the switchgear assembly |  |  |  |  | YES |  |  |  |  | NO |  |  |  |  | Not Applicable |  |  |  |  | 0% | 0 | [8 empty] | 0% | 0 | [8 empty] | NO |  |  |  |  | 0% |  |  |  |  | 0 |  |  |  |  | None | Not Given | By User | By User | Not Given | none |  |  |  |  | No | None | YES
D5012.023l | D5012.023l | Low Voltage Switchgear - Capacity: 1200 to 2000 Amp - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | Costing is per unit and is based upon 1600 Amp. | Normal - Designed for seismic loads but no special seismic certification | Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints | Each | Each | Peak Floor Acceleration | g | 3 | DS1 | DS2 | DS3 |  |  | Mutually Exclusive | Mutually Exclusive | Mutually Exclusive |  |  | MutEx(DS1,DS2,DS3) | 619 | AP 1600 | YES | FLR | Anchorage failure. | Anchorage failure & Equipment damaged beyond repair. | Damaged, Inoperative but anchorage is OK. |  |  | 0.35 | 0.15 | 0.5 |  |  | By User | By User | By User |  |  | User to Calculate | User to Calculate | User to Calculate |  |  | User to Calculate | User to Calculate | User to Calculate |  |  | By User | By User | By User |  |  | NO | NO | Superior | Average | Superior | Superior | Repair anchorage and concrete pad and remount equipment. | Replace equipment including attached utilities in addition to repairing anchorage and concrete pad. | Replace fiberglass insulator supporting the vertical bus bars in the rear of the switchgear assembly |  |  | NO | YES | YES |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | NO | NO |  |  | 0% | 0% | 0% |  |  | 0 | 0 | 0 |  |  | User to provide median demand and dispersion values. The values listed are default PACT values and do not represent the response of this component. | Not Given | By User | By User | Not Given | none | none | none |  |  | No | None | YES
D5012.031a | D5012.031a | Distribution Panel - Capacity: 100 to <350 Amp - Unanchored equipment that is not vibration isolated - Equipment fragility only | Costing is per unit and is based upon 225 Amp. | Normal - Not designed for seismic loads | Unanchored equipment that is not vibration isolated | Each | Each | Peak Floor Acceleration | g | 1 | DS1 |  |  |  |  | Sequential |  |  |  |  | Seq(DS1) | 620 | AP 225 | YES | BLDG | Damaged, inoperative but anchorage is OK. |  |  |  |  | 1 |  |  |  |  | 2.16 |  |  |  |  | 0.4 |  |  |  |  | 0.25 |  |  |  |  | 0.45 |  |  |  |  | NO | NO | Superior | Average | Superior | Superior | Replace equipment |  |  |  |  | NO |  |  |  |  | NO |  |  |  |  | Not Applicable |  |  |  |  | 0% | 0 | [8 empty] | 0% | 0 | [8 empty] | NO |  |  |  |  | 0% |  |  |  |  | 0 |  |  |  |  | None | Not Given | By User | By User | Not Given | D5012.031b-DS1-1.JPG |  |  |  |  | No | None | YES
D5012.031b | D5012.031b | Distribution Panel - Capacity: 350 to <750 Amp - Unanchored equipment that is not vibration isolated - Equipment fragility only | Costing is per unit and is based upon 400 Amp. | Normal - Not designed for seismic loads | Unanchored equipment that is not vibration isolated | Each | Each | Peak Floor Acceleration | g | 1 | DS1 |  |  |  |  | Sequential |  |  |  |  | Seq(DS1) | 621 | AP 400 | YES | BLDG | Damaged, inoperative but anchorage is OK. |  |  |  |  | 1 |  |  |  |  | 2.16 |  |  |  |  | 0.4 |  |  |  |  | 0.25 |  |  |  |  | 0.45 |  |  |  |  | NO | NO | Superior | Average | Superior | Superior | Replace equipment |  |  |  |  | NO |  |  |  |  | NO |  |  |  |  | Not Applicable |  |  |  |  | 0% | 0 | [8 empty] | 0% | 0 | [8 empty] | NO |  |  |  |  | 0% |  |  |  |  | 0 |  |  |  |  | None | Not Given | By User | By User | Not Given | D5012.031b-DS1-1.JPG |  |  |  |  | No | None | YES
D5012.031c | D5012.031c | Distribution Panel - Capacity: 750 to <1200 Amp - Unanchored equipment that is not vibration isolated - Equipment fragility only | Costing is per unit and is based upon 800 Amp. | Normal - Not designed for seismic loads | Unanchored equipment that is not vibration isolated | Each | Each | Peak Floor Acceleration | g | 1 | DS1 |  |  |  |  | Sequential |  |  |  |  | Seq(DS1) | 622 | AP 800 | YES | BLDG | Damaged, inoperative but anchorage is OK. |  |  |  |  | 1 |  |  |  |  | 2.16 |  |  |  |  | 0.4 |  |  |  |  | 0.25 |  |  |  |  | 0.45 |  |  |  |  | NO | NO | Superior | Average | Superior | Superior | Replace equipment |  |  |  |  | NO |  |  |  |  | NO |  |  |  |  | Not Applicable |  |  |  |  | 0% | 0 | [8 empty] | 0% | 0 | [8 empty] | NO |  |  |  |  | 0% |  |  |  |  | 0 |  |  |  |  | None | Not Given | By User | By User | Not Given | D5012.031b-DS1-1.JPG |  |  |  |  | No | None | YES
D5012.031d | D5012.031d | Distribution Panel - Capacity: 1200 to 2000 Amp - Unanchored equipment that is not vibration isolated - Equipment fragility only | Costing is per unit and is based upon 1600 Amp. | Normal - Not designed for seismic loads | Unanchored equipment that is not vibration isolated | Each | Each | Peak Floor Acceleration | g | 1 | DS1 |  |  |  |  | Sequential |  |  |  |  | Seq(DS1) | 623 | AP 1600 | YES | BLDG | Damaged, inoperative but anchorage is OK. |  |  |  |  | 1 |  |  |  |  | 2.16 |  |  |  |  | 0.4 |  |  |  |  | 0.25 |  |  |  |  | 0.45 |  |  |  |  | NO | NO | Superior | Average | Superior | Superior | Replace equipment |  |  |  |  | YES |  |  |  |  | NO |  |  |  |  | Not Applicable |  |  |  |  | 0% | 0 | [8 empty] | 0% | 0 | [8 empty] | NO |  |  |  |  | 0% |  |  |  |  | 0 |  |  |  |  | None | Not Given | By User | By User | Not Given | D5012.031b-DS1-1.JPG |  |  |  |  | No | None | YES
D5012.033a | D5012.033a | Distribution Panel - Capacity: 100 to <350 Amp - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only | Costing is per unit and is based upon 225 Amp. | Normal - Designed for seismic loads but no special seismic certification | Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints | Each | Each | Peak Floor Acceleration | g | 2 | DS1 | DS2 |  |  |  | Mutually Exclusive | Mutually Exclusive |  |  |  | MutEx(DS1,DS2) | 624 | AP 225 | YES | BLDG | Anchorage failure. | Anchorage failure & Equipment damaged beyond repair. |  |  |  | 0.7 | 0.3 |  |  |  | By User | By User |  |  |  | User to Calculate | User to Calculate |  |  |  | User to Calculate | User to Calculate |  |  |  | By User | By User |  |  |  | NO | NO | Superior | Average | Superior | Superior | Repair anchorage and concrete pad (if floor mounted and wall if wall mounted) and remount equipment. | Replace equipment in addition to repairing anchorage and concrete pad if floor mounted or wall if wall mounted. |  |  |  | NO | NO |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | NO |  |  |  | 0% | 0% |  |  |  | 0 | 0 |  |  |  | User to provide median demand and dispersion values. The values listed are default PACT values and do not represent the response of this component. | Not Given | By User | By User | Not Given | none | none |  |  |  | No | None | YES
D5012.033b | D5012.033b | Distribution Panel - Capacity: 100 to <350 Amp - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only | Costing is per unit and is based upon 225 Amp. | Normal - Designed for seismic loads but no special seismic certification | Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints | Each | Each | Peak Floor Acceleration | g | 1 | DS1 |  |  |  |  | Sequential |  |  |  |  | Seq(DS1) | 625 | AP 225 | YES | BLDG | Damaged, inoperative but anchorage is OK. |  |  |  |  | 1 |  |  |  |  | 3.05 |  |  |  |  | 0.4 |  |  |  |  | 0.1 |  |  |  |  | 0.4 |  |  |  |  | NO | NO | Superior | Average | Superior | Superior | Replace equipment |  |  |  |  | NO |  |  |  |  | NO |  |  |  |  | Not Applicable |  |  |  |  | 0% | 0 | [8 empty] | 0% | 0 | [8 empty] | NO |  |  |  |  | 0% |  |  |  |  | 0 |  |  |  |  | None | Not Given | By User | By User | Not Given | D5012.031b-DS1-1.JPG |  |  |  |  | No | None | YES
D5012.033c | D5012.033c | Distribution Panel - Capacity: 100 to <350 Amp - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | Costing is per unit and is based upon 225 Amp. | Normal - Designed for seismic loads but no special seismic certification | Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints | Each | Each | Peak Floor Acceleration | g | 3 | DS1 | DS2 | DS3 |  |  | Mutually Exclusive | Mutually Exclusive | Mutually Exclusive |  |  | MutEx(DS1,DS2,DS3) | 626 | AP 225 | YES | BLDG | Anchorage failure. | Anchorage failure & Equipment damaged beyond repair. | Damaged, Inoperative but anchorage is OK. |  |  | 0.35 | 0.15 | 0.5 |  |  | By User | By User | By User |  |  | User to Calculate | User to Calculate | User to Calculate |  |  | User to Calculate | User to Calculate | User to Calculate |  |  | By User | By User | By User |  |  | NO | NO | Superior | Average | Superior | Superior | Repair anchorage and concrete pad (if floor mounted and wall if wall mounted) and remount equipment. | Replace equipment in addition to repairing anchorage and concrete pad if floor mounted or wall if wall mounted. | Replace equipment. |  |  | NO | NO | NO |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | NO | NO |  |  | 0% | 0% | 0% |  |  | 0 | 0 | 0 |  |  | User to provide median demand and dispersion values. The values listed are default PACT values and do not represent the response of this component. | Not Given | By User | By User | Not Given | none | none | none |  |  | No | None | YES
D5012.033d | D5012.033d | Distribution Panel - Capacity: 350 to <750 Amp - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only | Costing is per unit and is based upon 400 Amp. | Normal - Designed for seismic loads but no special seismic certification | Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints | Each | Each | Peak Floor Acceleration | g | 2 | DS1 | DS2 |  |  |  | Mutually Exclusive | Mutually Exclusive |  |  |  | MutEx(DS1,DS2) | 627 | AP 400 | YES | BLDG | Anchorage failure. | Anchorage failure & Equipment damaged beyond repair. |  |  |  | 0.7 | 0.3 |  |  |  | By User | By User |  |  |  | User to Calculate | User to Calculate |  |  |  | User to Calculate | User to Calculate |  |  |  | By User | By User |  |  |  | NO | NO | Superior | Average | Superior | Superior | Repair anchorage and concrete pad (if floor mounted and wall if wall mounted) and remount equipment. | Replace equipment in addition to repairing anchorage and concrete pad if floor mounted or wall if wall mounted. |  |  |  | NO | NO |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | NO |  |  |  | 0% | 0% |  |  |  | 0 | 0 |  |  |  | User to provide median demand and dispersion values. The values listed are default PACT values and do not represent the response of this component. | Not Given | By User | By User | Not Given | none | none |  |  |  | No | None | YES
D5012.033e | D5012.033e | Distribution Panel - Capacity: 350 to <750 Amp - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only | Costing is per unit and is based upon 400 Amp. | Normal - Designed for seismic loads but no special seismic certification | Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints | Each | Each | Peak Floor Acceleration | g | 1 | DS1 |  |  |  |  | Sequential |  |  |  |  | Seq(DS1) | 628 | AP 400 | YES | BLDG | Damaged, inoperative but anchorage is OK. |  |  |  |  | 1 |  |  |  |  | 3.05 |  |  |  |  | 0.4 |  |  |  |  | 0.1 |  |  |  |  | 0.4 |  |  |  |  | NO | NO | Superior | Average | Superior | Superior | Replace equipment |  |  |  |  | NO |  |  |  |  | NO |  |  |  |  | Not Applicable |  |  |  |  | 0% | 0 | [8 empty] | 0% | 0 | [8 empty] | NO |  |  |  |  | 0% |  |  |  |  | 0 |  |  |  |  | None | Not Given | By User | By User | Not Given | D5012.031b-DS1-1.JPG |  |  |  |  | No | None | YES
D5012.033f | D5012.033f | Distribution Panel - Capacity: 350 to <750 Amp - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | Costing is per unit and is based upon 400 Amp. | Normal - Designed for seismic loads but no special seismic certification | Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints | Each | Each | Peak Floor Acceleration | g | 3 | DS1 | DS2 | DS3 |  |  | Mutually Exclusive | Mutually Exclusive | Mutually Exclusive |  |  | MutEx(DS1,DS2,DS3) | 629 | AP 400 | YES | BLDG | Anchorage failure. | Anchorage failure & Equipment damaged beyond repair. | Damaged, Inoperative but anchorage is OK. |  |  | 0.35 | 0.15 | 0.5 |  |  | By User | By User | By User |  |  | User to Calculate | User to Calculate | User to Calculate |  |  | User to Calculate | User to Calculate | User to Calculate |  |  | By User | By User | By User |  |  | NO | NO | Superior | Average | Superior | Superior | Repair anchorage and concrete pad (if floor mounted and wall if wall mounted) and remount equipment. | Replace equipment in addition to repairing anchorage and concrete pad if floor mounted or wall if wall mounted. | Replace equipment. |  |  | NO | NO | NO |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | NO | NO |  |  | 0% | 0% | 0% |  |  | 0 | 0 | 0 |  |  | User to provide median demand and dispersion values. The values listed are default PACT values and do not represent the response of this component. | Not Given | By User | By User | Not Given | none | none | none |  |  | No | None | YES
D5012.033g | D5012.033g | Distribution Panel - Capacity: 750 to <1200 Amp - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only | Costing is per unit and is based upon 800 Amp. | Normal - Designed for seismic loads but no special seismic certification | Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints | Each | Each | Peak Floor Acceleration | g | 2 | DS1 | DS2 |  |  |  | Mutually Exclusive | Mutually Exclusive |  |  |  | MutEx(DS1,DS2) | 630 | AP 800 | YES | BLDG | Anchorage failure. | Anchorage failure & Equipment damaged beyond repair. |  |  |  | 0.7 | 0.3 |  |  |  | By User | By User |  |  |  | User to Calculate | User to Calculate |  |  |  | User to Calculate | User to Calculate |  |  |  | By User | By User |  |  |  | NO | NO | Superior | Average | Superior | Superior | Repair anchorage and concrete pad (if floor mounted and wall if wall mounted) and remount equipment. | Replace equipment in addition to repairing anchorage and concrete pad if floor mounted or wall if wall mounted. |  |  |  | NO | NO |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | NO |  |  |  | 0% | 0% |  |  |  | 0 | 0 |  |  |  | User to provide median demand and dispersion values. The values listed are default PACT values and do not represent the response of this component. | Not Given | By User | By User | Not Given | none | none |  |  |  | No | None | YES
D5012.033h | D5012.033h | Distribution Panel - Capacity: 750 to <1200 Amp - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only | Costing is per unit and is based upon 800 Amp. | Normal - Designed for seismic loads but no special seismic certification | Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints | Each | Each | Peak Floor Acceleration | g | 1 | DS1 |  |  |  |  | Sequential |  |  |  |  | Seq(DS1) | 631 | AP 800 | YES | BLDG | Damaged, inoperative but anchorage is OK. |  |  |  |  | 1 |  |  |  |  | 3.05 |  |  |  |  | 0.4 |  |  |  |  | 0.1 |  |  |  |  | 0.4 |  |  |  |  | NO | NO | Superior | Average | Superior | Superior | Replace equipment |  |  |  |  | NO |  |  |  |  | NO |  |  |  |  | Not Applicable |  |  |  |  | 0% | 0 | [8 empty] | 0% | 0 | [8 empty] | NO |  |  |  |  | 0% |  |  |  |  | 0 |  |  |  |  | None | Not Given | By User | By User | Not Given | D5012.031b-DS1-1.JPG |  |  |  |  | No | None | YES
D5012.033i | D5012.033i | Distribution Panel - Capacity: 750 to <1200 Amp - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | Costing is per unit and is based upon 800 Amp. | Normal - Designed for seismic loads but no special seismic certification | Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints | Each | Each | Peak Floor Acceleration | g | 3 | DS1 | DS2 | DS3 |  |  | Mutually Exclusive | Mutually Exclusive | Mutually Exclusive |  |  | MutEx(DS1,DS2,DS3) | 632 | AP 800 | YES | BLDG | Anchorage failure. | Anchorage failure & Equipment damaged beyond repair. | Damaged, Inoperative but anchorage is OK. |  |  | 0.35 | 0.15 | 0.5 |  |  | By User | By User | By User |  |  | User to Calculate | User to Calculate | User to Calculate |  |  | User to Calculate | User to Calculate | User to Calculate |  |  | By User | By User | By User |  |  | NO | NO | Superior | Average | Superior | Superior | Repair anchorage and concrete pad (if floor mounted and wall if wall mounted) and remount equipment. | Replace equipment in addition to repairing anchorage and concrete pad if floor mounted or wall if wall mounted. | Replace equipment. |  |  | NO | NO | NO |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | NO | NO |  |  | 0% | 0% | 0% |  |  | 0 | 0 | 0 |  |  | User to provide median demand and dispersion values. The values listed are default PACT values and do not represent the response of this component. | Not Given | By User | By User | Not Given | none | none | none |  |  | No | None | YES
D5012.033j | D5012.033j | Distribution Panel - Capacity: 1200 to 2000 Amp - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only | Costing is per unit and is based upon 1600 Amp. | Normal - Designed for seismic loads but no special seismic certification | Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints | Each | Each | Peak Floor Acceleration | g | 2 | DS1 | DS2 |  |  |  | Mutually Exclusive | Mutually Exclusive |  |  |  | MutEx(DS1,DS2) | 633 | AP 1600 | YES | BLDG | Anchorage failure. | Anchorage failure & Equipment damaged beyond repair. |  |  |  | 0.7 | 0.3 |  |  |  | By User | By User |  |  |  | User to Calculate | User to Calculate |  |  |  | User to Calculate | User to Calculate |  |  |  | By User | By User |  |  |  | NO | NO | Superior | Average | Superior | Superior | Repair anchorage and concrete pad (if floor mounted and wall if wall mounted) and remount equipment. | Replace equipment in addition to repairing anchorage and concrete pad if floor mounted or wall if wall mounted. |  |  |  | NO | YES |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | NO |  |  |  | 0% | 0% |  |  |  | 0 | 0 |  |  |  | User to provide median demand and dispersion values. The values listed are default PACT values and do not represent the response of this component. | Not Given | By User | By User | Not Given | none | none |  |  |  | No | None | YES
D5012.033k | D5012.033k | Distribution Panel - Capacity: 1200 to 2000 Amp - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only | Costing is per unit and is based upon 1600 Amp. | Normal - Designed for seismic loads but no special seismic certification | Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints | Each | Each | Peak Floor Acceleration | g | 1 | DS1 |  |  |  |  | Sequential |  |  |  |  | Seq(DS1) | 634 | AP 1600 | YES | BLDG | Damaged, inoperative but anchorage is OK. |  |  |  |  | 1 |  |  |  |  | 3.05 |  |  |  |  | 0.4 |  |  |  |  | 0.1 |  |  |  |  | 0.4 |  |  |  |  | NO | NO | Superior | Average | Superior | Superior | Replace equipment |  |  |  |  | YES |  |  |  |  | NO |  |  |  |  | Not Applicable |  |  |  |  | 0% | 0 | [8 empty] | 0% | 0 | [8 empty] | NO |  |  |  |  | 0% |  |  |  |  | 0 |  |  |  |  | None | Not Given | By User | By User | Not Given | D5012.031b-DS1-1.JPG |  |  |  |  | No | None | YES
D5012.033l | D5012.033l | Distribution Panel - Capacity: 1200 to 2000 Amp - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | Costing is per unit and is based upon 1600 Amp. | Normal - Designed for seismic loads but no special seismic certification | Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints | Each | Each | Peak Floor Acceleration | g | 3 | DS1 | DS2 | DS3 |  |  | Mutually Exclusive | Mutually Exclusive | Mutually Exclusive |  |  | MutEx(DS1,DS2,DS3) | 635 | AP 1600 | YES | BLDG | Anchorage failure. | Anchorage failure & Equipment damaged beyond repair. | Damaged, Inoperative but anchorage is OK. |  |  | 0.35 | 0.15 | 0.5 |  |  | By User | By User | By User |  |  | User to Calculate | User to Calculate | User to Calculate |  |  | User to Calculate | User to Calculate | User to Calculate |  |  | By User | By User | By User |  |  | NO | NO | Superior | Average | Superior | Superior | Repair anchorage and concrete pad (if floor mounted and wall if wall mounted) and remount equipment. | Replace equipment in addition to repairing anchorage and concrete pad if floor mounted or wall if wall mounted. | Replace equipment. |  |  | NO | YES | YES |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | NO | NO |  |  | 0% | 0% | 0% |  |  | 0 | 0 | 0 |  |  | User to provide median demand and dispersion values. The values listed are default PACT values and do not represent the response of this component. | Not Given | By User | By User | Not Given | none | none | none |  |  | No | None | YES
D5092.011a | D5092.011a | Battery Rack - Capacity: all - Unanchored equipment that is not vibration isolated - Equipment fragility only | Costing is per unit. | Normal - Not designed for seismic loads | Unanchored equipment that is not vibration isolated | Each | Each | Peak Floor Acceleration | g | 3 | DS1 | DS2 | DS3 |  |  | Simultaneous | Simultaneous | Simultaneous |  |  | Simul(DS1,DS2,DS3) | 636 | EA 1 | YES | BLDG | Damaged, inoperative. Batteries fall, crack cases, dislodge conductors, or are otherwise damaged. | Batteries spill battery acid. | Battery rack collapses. |  |  | 1 | 0.5 | 0.1 |  |  | 1.11 | 1.11 | 1.11 |  |  | 0.6 | 0.6 | 0.6 |  |  | 0.1 | 0.1 | 0.1 |  |  | 0.6 | 0.6 | 0.6 |  |  | NO | NO | Superior | Average | Superior | Superior | Replace batteries. | Clean up spilled acid. | Replace battery rack. |  |  | YES | YES | YES |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | NO | NO |  |  | 0% | 0% | 0% |  |  | 0 | 0 | 0 |  |  | None | Not Given | By User | By User | Not Given | none | none | none |  |  | No | None | YES
D5092.013a | D5092.013a | Battery Rack - Capacity: all - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only | Costing is per unit. | Normal - Designed for seismic loads but no special seismic certification | Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints | Each | Each | Peak Floor Acceleration | g | 2 | DS1 | DS2 |  |  |  | Mutually Exclusive | Mutually Exclusive |  |  |  | MutEx(DS1,DS2) | 637 | EA 1 | YES | BLDG | Anchorage failure. | Anchorage failure & Equipment damaged beyond repair. |  |  |  | 0.7 | 0.3 |  |  |  | By User | By User |  |  |  | User to Calculate | User to Calculate |  |  |  | User to Calculate | User to Calculate |  |  |  | By User | By User |  |  |  | NO | NO | Superior | Average | Superior | Superior | Repair anchorage and concrete pad and remount equipment. | Replace equipment including attached utilities in addition to repairing anchorage and concrete pad. |  |  |  | YES | YES |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | NO |  |  |  | 0% | 0% |  |  |  | 0 | 0 |  |  |  | User to provide median demand and dispersion values. The values listed are default PACT values and do not represent the response of this component. | Not Given | By User | By User | Not Given | none | none |  |  |  | No | None | YES
D5092.013b | D5092.013b | Battery Rack - Capacity: all - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only | Costing is per unit. | Normal - Designed for seismic loads but no special seismic certification | Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints | Each | Each | Peak Floor Acceleration | g | 3 | DS1 | DS2 | DS3 |  |  | Simultaneous | Simultaneous | Simultaneous |  |  | Simul(DS1,DS2,DS3) | 638 | EA 1 | YES | BLDG | Damaged, inoperative but anchorage is OK. Batteries fall, crack cases, dislodge conductors, or are otherwise damaged. | Batteries spill battery acid. | Battery rack collapses. |  |  | 1 | 0.5 | 0.1 |  |  | 2.32 | 2.32 | 2.32 |  |  | 0.2 | 0.2 | 0.2 |  |  | 0.1 | 0.1 | 0.1 |  |  | 0.2 | 0.2 | 0.2 |  |  | NO | NO | Superior | Average | Superior | Superior | Replace batteries. | Clean up spilled acid. | Replace battery rack. |  |  | YES | YES | YES |  |  | NO | NO | NO |  |  | Not Applicable | Not Applicable | Not Applicable |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | 0% | 0 | 0% | 0 | 0% | 0 |  |  |  |  | NO | NO | NO |  |  | 0% | 0% | 0% |  |  | 0 | 0 | 0 |  |  | None | Not Given | By User | By User | Not Given | none | none | none |  |  | No | None | YES
D5092.013c | D5092.013c | Battery Rack - Capacity: all - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | Costing is per unit. | Normal - Designed for seismic loads but no special seismic certification | Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints | Each | Each | Peak Floor Acceleration | g | 5 | DS1 | DS2 | DS3 | DS4 | DS5 | Mutually Exclusive | Mutually Exclusive | Mutually Exclusive | Mutually Exclusive | Mutually Exclusive | MutEx(DS1,DS2,DS3,DS4,DS5) | 639 | EA 1 | YES | BLDG | Anchorage failure. | Anchorage failure & Equipment damaged beyond repair. | Equipment is damaged and inoperative. | Equipment is damaged and inoperative. | Equipment is damaged and inoperative. | 0.35 | 0.15 | 0.15 | 0.25 | 0.1 | By User | By User | By User | By User | By User | User to Calculate | User to Calculate | User to Calculate | User to Calculate | User to Calculate | User to Calculate | User to Calculate | User to Calculate | User to Calculate | User to Calculate | By User | By User | By User | By User | By User | NO | NO | Superior | Average | Superior | Superior | Repair anchorage and concrete pad and remount equipment. | Replace equipment including attached utilities in addition to repairing anchorage and concrete pad. | Replace batteries. | Replace batteries and clean up acid. | Replace rack including batteries and clean up acid. | YES | YES | YES | YES | YES | NO | NO | NO | NO | NO | Not Applicable | Not Applicable | Not Applicable | Not Applicable | Not Applicable | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | NO | NO | NO | NO | NO | 0% | 0% | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | User to provide median demand and dispersion values. The values listed are default PACT values and do not represent the response of this component. | Not Given | By User | By User | Not Given | none | none | none | none | none | No | None | YES
D5092.021a | D5092.021a | Battery Charger - Capacity: all - Unanchored equipment that is not vibration isolated - Equipment fragility only | Costing is per unit. | Normal - Not designed for seismic loads | Unanchored equipment that is not vibration isolated | Each | Each | Peak Floor Acceleration | g | 2 | DS1 | DS2 |  |  |  | Mutually Exclusive | Mutually Exclusive |  |  |  | MutEx(DS1,DS2) | 640 | EA 1 | YES | BLDG | Damaged, inoperative but anchorage is OK. | Damaged, inoperative but anchorage is OK. Equipment damaged beyond repair. |  |  |  | 0.5 | 0.5 |  |  |  | 1.07 | 1.07 |  |  |  | 0.4 | 0.4 |  |  |  | 0.1 | 0.1 |  |  |  | 0.4 | 0.4 |  |  |  | NO | NO | Superior | Average | Superior | Superior | Service for intermittent voltage output or for blown surge suppressor. | Replace equipment. |  |  |  | NO | NO |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | NO |  |  |  | 0% | 0% |  |  |  | 0 | 0 |  |  |  | None | Not Given | By User | By User | Not Given | none | none |  |  |  | No | None | YES
D5092.023a | D5092.023a | Battery Charger - Capacity: all - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only | Costing is per unit. | Normal - Designed for seismic loads but no special seismic certification | Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints | Each | Each | Peak Floor Acceleration | g | 2 | DS1 | DS2 |  |  |  | Mutually Exclusive | Mutually Exclusive |  |  |  | MutEx(DS1,DS2) | 641 | EA 1 | YES | BLDG | Anchorage failure. | Anchorage failure & Equipment damaged beyond repair. |  |  |  | 0.7 | 0.3 |  |  |  | By User | By User |  |  |  | User to Calculate | User to Calculate |  |  |  | User to Calculate | User to Calculate |  |  |  | By User | By User |  |  |  | NO | NO | Superior | Average | Superior | Superior | Repair anchorage and concrete pad (if floor mounted and wall if wall mounted) and remount equipment. | Replace equipment including attached utilities in addition to repairing anchorage and concrete pad / wall. |  |  |  | NO | NO |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | NO |  |  |  | 0% | 0% |  |  |  | 0 | 0 |  |  |  | User to provide median demand and dispersion values. The values listed are default PACT values and do not represent the response of this component. | Not Given | By User | By User | Not Given | none | none |  |  |  | No | None | YES
D5092.023b | D5092.023b | Battery Charger - Capacity: all - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only | Costing is per unit. | Normal - Designed for seismic loads but no special seismic certification | Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints | Each | Each | Peak Floor Acceleration | g | 2 | DS1 | DS2 |  |  |  | Mutually Exclusive | Mutually Exclusive |  |  |  | MutEx(DS1,DS2) | 642 | EA 1 | YES | BLDG | Damaged, inoperative but anchorage is OK. | Damaged, inoperative but anchorage is OK. Equipment damaged beyond repair. |  |  |  | 0.5 | 0.5 |  |  |  | 2.7 | 2.7 |  |  |  | 0.6 | 0.6 |  |  |  | 0.1 | 0.1 |  |  |  | 0.6 | 0.6 |  |  |  | NO | NO | Superior | Average | Superior | Superior | Service for intermittent voltage output or for blown surge suppressor. | Replace equipment. |  |  |  | NO | NO |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | NO |  |  |  | 0% | 0% |  |  |  | 0 | 0 |  |  |  | None | Not Given | By User | By User | Not Given | none | none |  |  |  | No | None | YES
D5092.023c | D5092.023c | Battery Charger - Capacity: all - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | Costing is per unit. | Normal - Designed for seismic loads but no special seismic certification | Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints | Each | Each | Peak Floor Acceleration | g | 4 | DS1 | DS2 | DS3 | DS4 |  | Mutually Exclusive | Mutually Exclusive | Mutually Exclusive | Mutually Exclusive |  | MutEx(DS1,DS2,DS3,DS4) | 643 | EA 1 | YES | BLDG | Anchorage failure. | Anchorage failure & Equipment damaged beyond repair. | Equipment is damaged and inoperative. | Equipment is damaged and inoperative. |  | 0.35 | 0.15 | 0.25 | 0.25 |  | By User | By User | By User | By User |  | User to Calculate | User to Calculate | User to Calculate | User to Calculate |  | User to Calculate | User to Calculate | User to Calculate | User to Calculate |  | By User | By User | By User | By User |  | NO | NO | Superior | Average | Superior | Superior | Repair anchorage and concrete pad (if floor mounted and wall if wall mounted) and remount equipment. | Replace equipment including attached utilities in addition to repairing anchorage and concrete pad / wall. | Service for intermittent voltage output or for blown surge suppressor. | Replace equipment. |  | NO | NO | NO | NO |  | NO | NO | NO | NO |  | Not Applicable | Not Applicable | Not Applicable | Not Applicable |  | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 |  |  | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 |  |  | NO | NO | NO | NO |  | 0% | 0% | 0% | 0% |  | 0 | 0 | 0 | 0 |  | User to provide median demand and dispersion values. The values listed are default PACT values and do not represent the response of this component. | Not Given | By User | By User | Not Given | none | none | none | none |  | No | None | YES
D5092.031a | D5092.031a | Diesel generator - Capacity: 100 to <350 kVA - Unanchored equipment that is not vibration isolated - Equipment fragility only | Costing is per unit and is based upon 250 kVa. | Normal - Not designed for seismic loads | Unanchored equipment that is not vibration isolated | Each | Each | Peak Floor Acceleration | g | 4 | DS1 | DS2 | DS3 | DS4 |  | Mutually Exclusive | Mutually Exclusive | Mutually Exclusive | Mutually Exclusive |  | MutEx(DS1,DS2,DS3,DS4) | 644 | KV 250 | YES | BLDG | Damaged, inoperative. Pipes and nozzles damaged. | Damaged, inoperative. Drive shaft misalignment. | Damaged, inoperative. Minor electrical damage, e.g., failed relay. | Damaged, inoperative. Exhaust line disconnected at expansion bellows. |  | 0.7 | 0.1 | 0.1 | 0.1 |  | 0.9 | 0.9 | 0.9 | 0.9 |  | 0.4 | 0.6 | 0.6 | 0.6 |  | 0.1 | 0.1 | 0.1 | 0.1 |  | 0.4 | 0.4 | 0.4 | 0.4 |  | NO | NO | Average | Average | Superior | Superior | Repair fracture pipes and damaged nozzles. | Overhaul because of drive shaft misalignment. | Minor electrical repair e.g., replace relay. | Reconnect exhaust line. |  | NO | NO | NO | NO |  | NO | NO | NO | NO |  | Not Applicable | Not Applicable | Not Applicable | Not Applicable |  | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 |  |  | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 |  |  | NO | NO | NO | NO |  | 0% | 0% | 0% | 0% |  | 0 | 0 | 0 | 0 |  | None | Not Given | By User | By User | Not Given | D5092.031b-DS1-1.JPG | none | none | none |  | No | 2011-08-24 DS2, DS3, DS4 median changed from 0.3 to 0.9 and beta changed from 0.6 to 0.4 in order to match D5092.031b,c,d. | YES
D5092.031b | D5092.031b | Diesel generator - Capacity: 350 to <750 kVA - Unanchored equipment that is not vibration isolated - Equipment fragility only | Costing is per unit and is based upon 500 kVa. | Normal - Not designed for seismic loads | Unanchored equipment that is not vibration isolated | Each | Each | Peak Floor Acceleration | g | 4 | DS1 | DS2 | DS3 | DS4 |  | Mutually Exclusive | Mutually Exclusive | Mutually Exclusive | Mutually Exclusive |  | MutEx(DS1,DS2,DS3,DS4) | 645 | KV 500 | YES | BLDG | Damaged, inoperative. Pipes and nozzles damaged. | Damaged, inoperative. Drive shaft misalignment. | Damaged, inoperative. Minor electrical damage, e.g., failed relay. | Damaged, inoperative. Exhaust line disconnected at expansion bellows. |  | 0.7 | 0.1 | 0.1 | 0.1 |  | 0.9 | 0.9 | 0.9 | 0.9 |  | 0.4 | 0.4 | 0.4 | 0.4 |  | 0.1 | 0.1 | 0.1 | 0.1 |  | 0.4 | 0.4 | 0.4 | 0.4 |  | NO | NO | Average | Average | Superior | Superior | Repair fracture pipes and damaged nozzles. | Overhaul because of drive shaft misalignment. | Minor electrical repair e.g., replace relay. | Reconnect exhaust line. |  | YES | YES | YES | YES |  | NO | NO | NO | NO |  | Not Applicable | Not Applicable | Not Applicable | Not Applicable |  | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 |  |  | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 |  |  | NO | NO | NO | NO |  | 0% | 0% | 0% | 0% |  | 0 | 0 | 0 | 0 |  | None | Not Given | By User | By User | Not Given | D5092.031b-DS1-1.JPG | none | none | none |  | No | None | YES
D5092.031c | D5092.031c | Diesel generator - Capacity: 750 to 1200 kVA - Unanchored equipment that is not vibration isolated - Equipment fragility only | Costing is per unit and is based upon 1000 kVa. | Normal - Not designed for seismic loads | Unanchored equipment that is not vibration isolated | Each | Each | Peak Floor Acceleration | g | 4 | DS1 | DS2 | DS3 | DS4 |  | Mutually Exclusive | Mutually Exclusive | Mutually Exclusive | Mutually Exclusive |  | MutEx(DS1,DS2,DS3,DS4) | 646 | KV 1000 | YES | BLDG | Damaged, inoperative. Pipes and nozzles damaged. | Damaged, inoperative. Drive shaft misalignment. | Damaged, inoperative. Minor electrical damage, e.g., failed relay. | Damaged, inoperative. Exhaust line disconnected at expansion bellows. |  | 0.7 | 0.1 | 0.1 | 0.1 |  | 0.9 | 0.9 | 0.9 | 0.9 |  | 0.4 | 0.4 | 0.4 | 0.4 |  | 0.1 | 0.1 | 0.1 | 0.1 |  | 0.4 | 0.4 | 0.4 | 0.4 |  | NO | NO | Average | Average | Superior | Superior | Repair fracture pipes and damaged nozzles. | Overhaul because of drive shaft misalignment. | Minor electrical repair e.g., replace relay. | Reconnect exhaust line. |  | YES | YES | YES | YES |  | NO | NO | NO | NO |  | Not Applicable | Not Applicable | Not Applicable | Not Applicable |  | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 |  |  | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 |  |  | NO | NO | NO | NO |  | 0% | 0% | 0% | 0% |  | 0 | 0 | 0 | 0 |  | None | Not Given | By User | By User | Not Given | D5092.031b-DS1-1.JPG | none | none | none |  | No | None | YES
D5092.031d | D5092.031d | Diesel generator - Capacity: 1200 to 2000 kVa - Unanchored equipment that is not vibration isolated - Equipment fragility only | Costing is per unit and is based upon 1500 kVa. | Normal - Not designed for seismic loads | Unanchored equipment that is not vibration isolated | Each | Each | Peak Floor Acceleration | g | 4 | DS1 | DS2 | DS3 | DS4 |  | Mutually Exclusive | Mutually Exclusive | Mutually Exclusive | Mutually Exclusive |  | MutEx(DS1,DS2,DS3,DS4) | 647 | KV 1500 | YES | BLDG | Damaged, inoperative. Pipes and nozzles damaged. | Damaged, inoperative. Drive shaft misalignment. | Damaged, inoperative. Minor electrical damage, e.g., failed relay. | Damaged, inoperative. Exhaust line disconnected at expansion bellows. |  | 0.7 | 0.1 | 0.1 | 0.1 |  | 0.9 | 0.9 | 0.9 | 0.9 |  | 0.4 | 0.4 | 0.4 | 0.4 |  | 0.1 | 0.1 | 0.1 | 0.1 |  | 0.4 | 0.4 | 0.4 | 0.4 |  | NO | NO | Average | Average | Superior | Superior | Repair fracture pipes and damaged nozzles. | Overhaul because of drive shaft misalignment. | Minor electrical repair e.g., replace relay. | Reconnect exhaust line. |  | YES | YES | YES | YES |  | NO | NO | NO | NO |  | Not Applicable | Not Applicable | Not Applicable | Not Applicable |  | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 |  |  | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 |  |  | NO | NO | NO | NO |  | 0% | 0% | 0% | 0% |  | 0 | 0 | 0 | 0 |  | None | Not Given | By User | By User | Not Given | D5092.031b-DS1-1.JPG | none | none | none |  | No | None | YES
D5092.032a | D5092.032a | Diesel generator - Capacity: 100 to <350 kVA - Vibration isolated equipment that is not snubbed or restrained - Anchorage fragility only | Costing is per unit and is based upon 250 kVa. | Normal - Not designed for seismic loads | Vibration isolated equipment that is not snubbed or restrained | Each | Each | Peak Floor Acceleration | g | 2 | DS1 | DS2 |  |  |  | Mutually Exclusive | Mutually Exclusive |  |  |  | MutEx(DS1,DS2) | 648 | KV 250 | YES | BLDG | Anchorage failure. | Anchorage failure & Equipment damaged beyond repair. |  |  |  | 0.7 | 0.3 |  |  |  | By User | By User |  |  |  | User to Calculate | User to Calculate |  |  |  | User to Calculate | User to Calculate |  |  |  | By User | By User |  |  |  | NO | NO | Average | Average | Superior | Superior | Repair anchorage and concrete pad and remount equipment. | Replace equipment including attached utilities in addition to repairing anchorage and concrete pad. |  |  |  | NO | NO |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | NO |  |  |  | 0% | 0% |  |  |  | 0 | 0 |  |  |  | User to provide median demand and dispersion values. The values listed are default PACT values and do not represent the response of this component. | Not Given | By User | By User | Not Given | D5092.031a-DS1-1.JPG | none |  |  |  | No | None | YES
D5092.032b | D5092.032b | Diesel generator - Capacity: 100 to <350 kVA - Vibration isolated equipment that is not snubbed or restrained - Equipment fragility only | Costing is per unit and is based upon 250 kVa. | Normal - Not designed for seismic loads | Vibration isolated equipment that is not snubbed or restrained | Each | Each | Peak Floor Acceleration | g | 4 | DS1 | DS2 | DS3 | DS4 |  | Mutually Exclusive | Mutually Exclusive | Mutually Exclusive | Mutually Exclusive |  | MutEx(DS1,DS2,DS3,DS4) | 649 | KV 250 | YES | BLDG | Damaged, inoperative but anchorage is OK. Pipes and nozzles damaged. | Damaged, inoperative but anchorage is OK. Drive shaft misalignment. | Damaged, inoperative but anchorage is OK. Minor electrical damage, e.g., failed relay. | Damaged, inoperative but anchorage is OK. Exhaust line disconnected at expansion bellows. |  | 0.7 | 0.1 | 0.1 | 0.1 |  | 1.07 | 1.07 | 1.07 | 1.07 |  | 0.4 | 0.4 | 0.4 | 0.4 |  | 0.1 | 0.1 | 0.1 | 0.1 |  | 0.4 | 0.4 | 0.4 | 0.4 |  | NO | NO | Average | Average | Superior | Superior | Repair fracture pipes and damaged nozzles. | Overhaul because of drive shaft misalignment. | Minor electrical repair e.g., replace relay. | Reconnect exhaust line. |  | NO | NO | NO | NO |  | NO | NO | NO | NO |  | Not Applicable | Not Applicable | Not Applicable | Not Applicable |  | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 |  |  | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 |  |  | NO | NO | NO | NO |  | 0% | 0% | 0% | 0% |  | 0 | 0 | 0 | 0 |  | None | Not Given | By User | By User | Not Given | D5092.031b-DS1-1.JPG | none | none | none |  | No | None | YES
D5092.032c | D5092.032c | Diesel generator - Capacity: 100 to <350 kVA - Vibration isolated equipment that is not snubbed or restrained - Combined anchorage/isolator & equipment fragility | Costing is per unit and is based upon 250 kVa. | Normal - Not designed for seismic loads | Vibration isolated equipment that is not snubbed or restrained | Each | Each | Peak Floor Acceleration | g | 5 | DS1 | DS2 | DS3 | DS4 | DS5 | Mutually Exclusive | Mutually Exclusive | Mutually Exclusive | Mutually Exclusive | Mutually Exclusive | MutEx(DS1,DS2,DS3,DS4,DS5) | 650 | KV 250 | YES | BLDG | Anchorage failure. | Anchorage failure & Equipment damaged beyond repair. | Damaged, Inoperative but anchorage is OK | Equipment is damaged and inoperative but anchorage is OK. | Equipment is damaged and inoperative but anchorage is OK. | 0.35 | 0.15 | 0.4 | 0.05 | 0.05 | By User | By User | By User | By User | By User | User to Calculate | User to Calculate | User to Calculate | User to Calculate | User to Calculate | User to Calculate | User to Calculate | User to Calculate | User to Calculate | User to Calculate | By User | By User | By User | By User | By User | NO | NO | Average | Average | Superior | Superior | Repair anchorage and concrete pad and remount equipment. | Replace equipment including attached utilities in addition to repairing anchorage and concrete pad. | Repair fracture pipes & damaged nozzles, and or reconnect exhaust line. | Overhaul because of drive shaft misalignment. | minor electrical repair e.g., replace relays. | NO | NO | NO | NO | NO | NO | NO | NO | NO | NO | Not Applicable | Not Applicable | Not Applicable | Not Applicable | Not Applicable | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | NO | NO | NO | NO | NO | 0% | 0% | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | User to provide median demand and dispersion values. The values listed are default PACT values and do not represent the response of this component. | Not Given | By User | By User | Not Given | D5092.031a-DS1-1.JPG | none | none | none | none | No | None | YES
D5092.032d | D5092.032d | Diesel generator - Capacity: 350 to <750 kVA - Vibration isolated equipment that is not snubbed or restrained - Anchorage fragility only | Costing is per unit and is based upon 500 kVa. | Normal - Not designed for seismic loads | Vibration isolated equipment that is not snubbed or restrained | Each | Each | Peak Floor Acceleration | g | 2 | DS1 | DS2 |  |  |  | Mutually Exclusive | Mutually Exclusive |  |  |  | MutEx(DS1,DS2) | 651 | KV 500 | YES | BLDG | Anchorage failure. | Anchorage failure & Equipment damaged beyond repair. |  |  |  | 0.7 | 0.3 |  |  |  | By User | By User |  |  |  | User to Calculate | User to Calculate |  |  |  | User to Calculate | User to Calculate |  |  |  | By User | By User |  |  |  | NO | NO | Average | Average | Superior | Superior | Repair anchorage and concrete pad and remount equipment. | Replace equipment including attached utilities in addition to repairing anchorage and concrete pad. |  |  |  | YES | YES |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | NO |  |  |  | 0% | 0% |  |  |  | 0 | 0 |  |  |  | User to provide median demand and dispersion values. The values listed are default PACT values and do not represent the response of this component. | Not Given | By User | By User | Not Given | D5092.031a-DS1-1.JPG | none |  |  |  | No | None | YES
D5092.032e | D5092.032e | Diesel generator - Capacity: 350 to <750 kVA - Vibration isolated equipment that is not snubbed or restrained - Equipment fragility only | Costing is per unit and is based upon 500 kVa. | Normal - Not designed for seismic loads | Vibration isolated equipment that is not snubbed or restrained | Each | Each | Peak Floor Acceleration | g | 4 | DS1 | DS2 | DS3 | DS4 |  | Mutually Exclusive | Mutually Exclusive | Mutually Exclusive | Mutually Exclusive |  | MutEx(DS1,DS2,DS3,DS4) | 652 | KV 500 | YES | BLDG | Damaged, inoperative but anchorage is OK. Pipes and nozzles damaged. | Damaged, inoperative but anchorage is OK. Drive shaft misalignment. | Damaged, inoperative but anchorage is OK. Minor electrical damage, e.g., failed relay. | Damaged, inoperative but anchorage is OK. Exhaust line disconnected at expansion bellows. |  | 0.7 | 0.1 | 0.1 | 0.1 |  | 1.07 | 1.07 | 1.07 | 1.07 |  | 0.4 | 0.4 | 0.4 | 0.4 |  | 0.1 | 0.1 | 0.1 | 0.1 |  | 0.4 | 0.4 | 0.4 | 0.4 |  | NO | NO | Average | Average | Superior | Superior | Repair fracture pipes and damaged nozzles. | Overhaul because of drive shaft misalignment. | Minor electrical repair e.g., replace relay. | Reconnect exhaust line. |  | YES | YES | YES | YES |  | NO | NO | NO | NO |  | Not Applicable | Not Applicable | Not Applicable | Not Applicable |  | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 |  |  | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 |  |  | NO | NO | NO | NO |  | 0% | 0% | 0% | 0% |  | 0 | 0 | 0 | 0 |  | None | Not Given | By User | By User | Not Given | D5092.031b-DS1-1.JPG | none | none | none |  | No | None | YES
D5092.032f | D5092.032f | Diesel generator - Capacity: 350 to <750 kVA - Vibration isolated equipment that is not snubbed or restrained - Combined anchorage/isolator & equipment fragility | Costing is per unit and is based upon 500 kVa. | Normal - Not designed for seismic loads | Vibration isolated equipment that is not snubbed or restrained | Each | Each | Peak Floor Acceleration | g | 5 | DS1 | DS2 | DS3 | DS4 | DS5 | Mutually Exclusive | Mutually Exclusive | Mutually Exclusive | Mutually Exclusive | Mutually Exclusive | MutEx(DS1,DS2,DS3,DS4,DS5) | 653 | KV 500 | YES | BLDG | Anchorage failure. | Anchorage failure & Equipment damaged beyond repair. | Damaged, Inoperative but anchorage is OK | Equipment is damaged and inoperative but anchorage is OK. | Equipment is damaged and inoperative but anchorage is OK. | 0.35 | 0.15 | 0.4 | 0.05 | 0.05 | By User | By User | By User | By User | By User | User to Calculate | User to Calculate | User to Calculate | User to Calculate | User to Calculate | User to Calculate | User to Calculate | User to Calculate | User to Calculate | User to Calculate | By User | By User | By User | By User | By User | NO | NO | Average | Average | Superior | Superior | Repair anchorage and concrete pad and remount equipment. | Replace equipment including attached utilities in addition to repairing anchorage and concrete pad. | Repair fracture pipes & damaged nozzles, and or reconnect exhaust line. | Overhaul because of drive shaft misalignment. | minor electrical repair e.g., replace relays. | YES | YES | YES | YES | YES | NO | NO | NO | NO | NO | Not Applicable | Not Applicable | Not Applicable | Not Applicable | Not Applicable | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | NO | NO | NO | NO | NO | 0% | 0% | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | User to provide median demand and dispersion values. The values listed are default PACT values and do not represent the response of this component. | Not Given | By User | By User | Not Given | D5092.031a-DS1-1.JPG | none | none | none | none | No | None | YES
D5092.032g | D5092.032g | Diesel generator - Capacity: 750 to 1200 kVA - Vibration isolated equipment that is not snubbed or restrained - Anchorage fragility only | Costing is per unit and is based upon 1000 kVa. | Normal - Not designed for seismic loads | Vibration isolated equipment that is not snubbed or restrained | Each | Each | Peak Floor Acceleration | g | 2 | DS1 | DS2 |  |  |  | Mutually Exclusive | Mutually Exclusive |  |  |  | MutEx(DS1,DS2) | 654 | KV 1000 | YES | BLDG | Anchorage failure. | Anchorage failure & Equipment damaged beyond repair. |  |  |  | 0.7 | 0.3 |  |  |  | By User | By User |  |  |  | User to Calculate | User to Calculate |  |  |  | User to Calculate | User to Calculate |  |  |  | By User | By User |  |  |  | NO | NO | Average | Average | Superior | Superior | Repair anchorage and concrete pad and remount equipment. | Replace equipment including attached utilities in addition to repairing anchorage and concrete pad. |  |  |  | YES | YES |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | NO |  |  |  | 0% | 0% |  |  |  | 0 | 0 |  |  |  | User to provide median demand and dispersion values. The values listed are default PACT values and do not represent the response of this component. | Not Given | By User | By User | Not Given | D5092.031a-DS1-1.JPG | none |  |  |  | No | None | YES
D5092.032h | D5092.032h | Diesel generator - Capacity: 750 to 1200 kVA - Vibration isolated equipment that is not snubbed or restrained - Equipment fragility only | Costing is per unit and is based upon 1000 kVa. | Normal - Not designed for seismic loads | Vibration isolated equipment that is not snubbed or restrained | Each | Each | Peak Floor Acceleration | g | 4 | DS1 | DS2 | DS3 | DS4 |  | Mutually Exclusive | Mutually Exclusive | Mutually Exclusive | Mutually Exclusive |  | MutEx(DS1,DS2,DS3,DS4) | 655 | KV 1000 | YES | BLDG | Damaged, inoperative but anchorage is OK. Pipes and nozzles damaged. | Damaged, inoperative but anchorage is OK. Drive shaft misalignment. | Damaged, inoperative but anchorage is OK. Minor electrical damage, e.g., failed relay. | Damaged, inoperative but anchorage is OK. Exhaust line disconnected at expansion bellows. |  | 0.7 | 0.1 | 0.1 | 0.1 |  | 1.07 | 1.07 | 1.07 | 1.07 |  | 0.4 | 0.4 | 0.4 | 0.4 |  | 0.1 | 0.1 | 0.1 | 0.1 |  | 0.4 | 0.4 | 0.4 | 0.4 |  | NO | NO | Average | Average | Superior | Superior | Repair fracture pipes and damaged nozzles. | Overhaul because of drive shaft misalignment. | Minor electrical repair e.g., replace relay. | Reconnect exhaust line. |  | YES | YES | YES | YES |  | NO | NO | NO | NO |  | Not Applicable | Not Applicable | Not Applicable | Not Applicable |  | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 |  |  | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 |  |  | NO | NO | NO | NO |  | 0% | 0% | 0% | 0% |  | 0 | 0 | 0 | 0 |  | None | Not Given | By User | By User | Not Given | D5092.031b-DS1-1.JPG | none | none | none |  | No | None | YES
D5092.032i | D5092.032i | Diesel generator - Capacity: 750 to 1200 kVA - Vibration isolated equipment that is not snubbed or restrained - Combined anchorage/isolator & equipment fragility | Costing is per unit and is based upon 1000 kVa. | Normal - Not designed for seismic loads | Vibration isolated equipment that is not snubbed or restrained | Each | Each | Peak Floor Acceleration | g | 5 | DS1 | DS2 | DS3 | DS4 | DS5 | Mutually Exclusive | Mutually Exclusive | Mutually Exclusive | Mutually Exclusive | Mutually Exclusive | MutEx(DS1,DS2,DS3,DS4,DS5) | 656 | KV 1000 | YES | BLDG | Anchorage failure. | Anchorage failure & Equipment damaged beyond repair. | Damaged, Inoperative but anchorage is OK | Equipment is damaged and inoperative but anchorage is OK. | Equipment is damaged and inoperative but anchorage is OK. | 0.35 | 0.15 | 0.4 | 0.05 | 0.05 | By User | By User | By User | By User | By User | User to Calculate | User to Calculate | User to Calculate | User to Calculate | User to Calculate | User to Calculate | User to Calculate | User to Calculate | User to Calculate | User to Calculate | By User | By User | By User | By User | By User | NO | NO | Average | Average | Superior | Superior | Repair anchorage and concrete pad and remount equipment. | Replace equipment including attached utilities in addition to repairing anchorage and concrete pad. | Repair fracture pipes & damaged nozzles, and or reconnect exhaust line. | Overhaul because of drive shaft misalignment. | minor electrical repair e.g., replace relays. | YES | YES | YES | YES | YES | NO | NO | NO | NO | NO | Not Applicable | Not Applicable | Not Applicable | Not Applicable | Not Applicable | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | NO | NO | NO | NO | NO | 0% | 0% | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | User to provide median demand and dispersion values. The values listed are default PACT values and do not represent the response of this component. | Not Given | By User | By User | Not Given | D5092.031a-DS1-1.JPG | none | none | none | none | No | None | YES
D5092.032j | D5092.032j | Diesel generator - Capacity: 1200 to 2000 kVa - Vibration isolated equipment that is not snubbed or restrained - Anchorage fragility only | Costing is per unit and is based upon 1500 kVa. | Normal - Not designed for seismic loads | Vibration isolated equipment that is not snubbed or restrained | Each | Each | Peak Floor Acceleration | g | 2 | DS1 | DS2 |  |  |  | Mutually Exclusive | Mutually Exclusive |  |  |  | MutEx(DS1,DS2) | 657 | KV 1500 | YES | BLDG | Anchorage failure. | Anchorage failure & Equipment damaged beyond repair. |  |  |  | 0.7 | 0.3 |  |  |  | By User | By User |  |  |  | User to Calculate | User to Calculate |  |  |  | User to Calculate | User to Calculate |  |  |  | By User | By User |  |  |  | NO | NO | Average | Average | Superior | Superior | Repair anchorage and concrete pad and remount equipment. | Replace equipment including attached utilities in addition to repairing anchorage and concrete pad. |  |  |  | YES | YES |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | NO |  |  |  | 0% | 0% |  |  |  | 0 | 0 |  |  |  | User to provide median demand and dispersion values. The values listed are default PACT values and do not represent the response of this component. | Not Given | By User | By User | Not Given | D5092.031a-DS1-1.JPG | none |  |  |  | No | None | YES
D5092.032k | D5092.032k | Diesel generator - Capacity: 1200 to 2000 kVa - Vibration isolated equipment that is not snubbed or restrained - Equipment fragility only | Costing is per unit and is based upon 1500 kVa. | Normal - Not designed for seismic loads | Vibration isolated equipment that is not snubbed or restrained | Each | Each | Peak Floor Acceleration | g | 4 | DS1 | DS2 | DS3 | DS4 |  | Mutually Exclusive | Mutually Exclusive | Mutually Exclusive | Mutually Exclusive |  | MutEx(DS1,DS2,DS3,DS4) | 658 | KV 1500 | YES | BLDG | Damaged, inoperative but anchorage is OK. Pipes and nozzles damaged. | Damaged, inoperative but anchorage is OK. Drive shaft misalignment. | Damaged, inoperative but anchorage is OK. Minor electrical damage, e.g., failed relay. | Damaged, inoperative but anchorage is OK. Exhaust line disconnected at expansion bellows. |  | 0.7 | 0.1 | 0.1 | 0.1 |  | 1.07 | 1.07 | 1.07 | 1.07 |  | 0.4 | 0.4 | 0.4 | 0.4 |  | 0.1 | 0.1 | 0.1 | 0.1 |  | 0.4 | 0.4 | 0.4 | 0.4 |  | NO | NO | Average | Average | Superior | Superior | Repair fracture pipes and damaged nozzles. | Overhaul because of drive shaft misalignment. | Minor electrical repair e.g., replace relay. | Reconnect exhaust line. |  | YES | YES | YES | YES |  | NO | NO | NO | NO |  | Not Applicable | Not Applicable | Not Applicable | Not Applicable |  | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 |  |  | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 |  |  | NO | NO | NO | NO |  | 0% | 0% | 0% | 0% |  | 0 | 0 | 0 | 0 |  | None | Not Given | By User | By User | Not Given | D5092.031b-DS1-1.JPG | none | none | none |  | No | None | YES
D5092.032l | D5092.032l | Diesel generator - Capacity: 1200 to 2000 kVa - Vibration isolated equipment that is not snubbed or restrained - Combined anchorage/isolator & equipment fragility | Costing is per unit and is based upon 1500 kVa. | Normal - Not designed for seismic loads | Vibration isolated equipment that is not snubbed or restrained | Each | Each | Peak Floor Acceleration | g | 5 | DS1 | DS2 | DS3 | DS4 | DS5 | Mutually Exclusive | Mutually Exclusive | Mutually Exclusive | Mutually Exclusive | Mutually Exclusive | MutEx(DS1,DS2,DS3,DS4,DS5) | 659 | KV 1500 | YES | BLDG | Anchorage failure. | Anchorage failure & Equipment damaged beyond repair. | Damaged, Inoperative but anchorage is OK | Equipment is damaged and inoperative but anchorage is OK. | Equipment is damaged and inoperative but anchorage is OK. | 0.35 | 0.15 | 0.4 | 0.05 | 0.05 | By User | By User | By User | By User | By User | User to Calculate | User to Calculate | User to Calculate | User to Calculate | User to Calculate | User to Calculate | User to Calculate | User to Calculate | User to Calculate | User to Calculate | By User | By User | By User | By User | By User | NO | NO | Average | Average | Superior | Superior | Repair anchorage and concrete pad and remount equipment. | Replace equipment including attached utilities in addition to repairing anchorage and concrete pad. | Repair fracture pipes & damaged nozzles, and or reconnect exhaust line. | Overhaul because of drive shaft misalignment. | minor electrical repair e.g., replace relays. | YES | YES | YES | YES | YES | NO | NO | NO | NO | NO | Not Applicable | Not Applicable | Not Applicable | Not Applicable | Not Applicable | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | NO | NO | NO | NO | NO | 0% | 0% | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | User to provide median demand and dispersion values. The values listed are default PACT values and do not represent the response of this component. | Not Given | By User | By User | Not Given | D5092.031a-DS1-1.JPG | none | none | none | none | No | None | YES
D5092.033a | D5092.033a | Diesel generator - Capacity: 100 to <350 kVA - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only | Costing is per unit and is based upon 250 kVa. | Normal - Designed for seismic loads but no special seismic certification | Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints | Each | Each | Peak Floor Acceleration | g | 2 | DS1 | DS2 |  |  |  | Mutually Exclusive | Mutually Exclusive |  |  |  | MutEx(DS1,DS2) | 660 | KV 250 | YES | BLDG | Anchorage failure. | Anchorage failure & Equipment damaged beyond repair. |  |  |  | 0.7 | 0.3 |  |  |  | By User | By User |  |  |  | User to Calculate | User to Calculate |  |  |  | User to Calculate | User to Calculate |  |  |  | By User | By User |  |  |  | NO | NO | Average | Average | Superior | Superior | Repair anchorage and concrete pad and remount equipment. | Replace equipment including attached utilities in addition to repairing anchorage and concrete pad. |  |  |  | NO | NO |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | NO |  |  |  | 0% | 0% |  |  |  | 0 | 0 |  |  |  | User to provide median demand and dispersion values. The values listed are default PACT values and do not represent the response of this component. | Not Given | By User | By User | Not Given | D5092.031a-DS1-1.JPG | none |  |  |  | No | None | YES
D5092.033b | D5092.033b | Diesel generator - Capacity: 100 to <350 kVA - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only | Costing is per unit and is based upon 250 kVa. | Normal - Designed for seismic loads but no special seismic certification | Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints | Each | Each | Peak Floor Acceleration | g | 4 | DS1 | DS2 | DS3 | DS4 |  | Mutually Exclusive | Mutually Exclusive | Mutually Exclusive | Mutually Exclusive |  | MutEx(DS1,DS2,DS3,DS4) | 661 | KV 250 | YES | BLDG | Damaged, inoperative but anchorage is OK. Pipes and nozzles damaged. | Damaged, inoperative but anchorage is OK. Drive shaft misalignment. | Damaged, inoperative but anchorage is OK. Minor electrical damage, e.g., failed relay. | Damaged, inoperative but anchorage is OK. Exhaust line disconnected at expansion bellows. |  | 0.7 | 0.1 | 0.1 | 0.1 |  | 2 | 2 | 2 | 2 |  | 0.2 | 0.2 | 0.2 | 0.2 |  | 0.1 | 0.1 | 0.1 | 0.1 |  | 0.2 | 0.2 | 0.2 | 0.2 |  | NO | NO | Average | Average | Superior | Superior | Repair fracture pipes and damaged nozzles. | Overhaul because of drive shaft misalignment. | Minor electrical repair e.g., replace relay. | Reconnect exhaust line. |  | NO | NO | NO | NO |  | NO | NO | NO | NO |  | Not Applicable | Not Applicable | Not Applicable | Not Applicable |  | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 |  |  | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 |  |  | NO | NO | NO | NO |  | 0% | 0% | 0% | 0% |  | 0 | 0 | 0 | 0 |  | None | Not Given | By User | By User | Not Given | D5092.031b-DS1-1.JPG | none | none | none |  | No | None | YES
D5092.033c | D5092.033c | Diesel generator - Capacity: 100 to <350 kVA - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | Costing is per unit and is based upon 250 kVa. | Normal - Designed for seismic loads but no special seismic certification | Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints | Each | Each | Peak Floor Acceleration | g | 5 | DS1 | DS2 | DS3 | DS4 | DS5 | Mutually Exclusive | Mutually Exclusive | Mutually Exclusive | Mutually Exclusive | Mutually Exclusive | MutEx(DS1,DS2,DS3,DS4,DS5) | 662 | KV 250 | YES | BLDG | Anchorage failure. | Anchorage failure & Equipment damaged beyond repair. | Damaged, Inoperative but anchorage is OK | Equipment is damaged and inoperative but anchorage is OK. | Equipment is damaged and inoperative but anchorage is OK. | 0.35 | 0.15 | 0.4 | 0.05 | 0.05 | By User | By User | By User | By User | By User | User to Calculate | User to Calculate | User to Calculate | User to Calculate | User to Calculate | User to Calculate | User to Calculate | User to Calculate | User to Calculate | User to Calculate | By User | By User | By User | By User | By User | NO | NO | Average | Average | Superior | Superior | Repair anchorage and concrete pad and remount equipment. | Replace equipment including attached utilities in addition to repairing anchorage and concrete pad. | Repair fracture pipes & damaged nozzles, and or reconnect exhaust line. | Overhaul because of drive shaft misalignment. | minor electrical repair e.g., replace relays. | NO | NO | NO | NO | NO | NO | NO | NO | NO | NO | Not Applicable | Not Applicable | Not Applicable | Not Applicable | Not Applicable | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | NO | NO | NO | NO | NO | 0% | 0% | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | User to provide median demand and dispersion values. The values listed are default PACT values and do not represent the response of this component. | Not Given | By User | By User | Not Given | D5092.031a-DS1-1.JPG | none | none | none | none | No | None | YES
D5092.033d | D5092.033d | Diesel generator - Capacity: 350 to <750 kVA - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only | Costing is per unit and is based upon 500 kVa. | Normal - Designed for seismic loads but no special seismic certification | Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints | Each | Each | Peak Floor Acceleration | g | 2 | DS1 | DS2 |  |  |  | Mutually Exclusive | Mutually Exclusive |  |  |  | MutEx(DS1,DS2) | 663 | KV 500 | YES | BLDG | Anchorage failure. | Anchorage failure & Equipment damaged beyond repair. |  |  |  | 0.7 | 0.3 |  |  |  | By User | By User |  |  |  | User to Calculate | User to Calculate |  |  |  | User to Calculate | User to Calculate |  |  |  | By User | By User |  |  |  | NO | NO | Average | Average | Superior | Superior | Repair anchorage and concrete pad and remount equipment. | Replace equipment including attached utilities in addition to repairing anchorage and concrete pad. |  |  |  | YES | YES |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | NO |  |  |  | 0% | 0% |  |  |  | 0 | 0 |  |  |  | User to provide median demand and dispersion values. The values listed are default PACT values and do not represent the response of this component. | Not Given | By User | By User | Not Given | D5092.031a-DS1-1.JPG | none |  |  |  | No | None | YES
D5092.033e | D5092.033e | Diesel generator - Capacity: 350 to <750 kVA - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only | Costing is per unit and is based upon 500 kVa. | Normal - Designed for seismic loads but no special seismic certification | Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints | Each | Each | Peak Floor Acceleration | g | 4 | DS1 | DS2 | DS3 | DS4 |  | Mutually Exclusive | Mutually Exclusive | Mutually Exclusive | Mutually Exclusive |  | MutEx(DS1,DS2,DS3,DS4) | 664 | KV 500 | YES | BLDG | Damaged, inoperative but anchorage is OK. Pipes and nozzles damaged. | Damaged, inoperative but anchorage is OK. Drive shaft misalignment. | Damaged, inoperative but anchorage is OK. Minor electrical damage, e.g., failed relay. | Damaged, inoperative but anchorage is OK. Exhaust line disconnected at expansion bellows. |  | 0.7 | 0.1 | 0.1 | 0.1 |  | 2 | 2 | 2 | 2 |  | 0.2 | 0.2 | 0.2 | 0.2 |  | 0.1 | 0.1 | 0.1 | 0.1 |  | 0.2 | 0.2 | 0.2 | 0.2 |  | NO | NO | Average | Average | Superior | Superior | Repair fracture pipes and damaged nozzles. | Overhaul because of drive shaft misalignment. | Minor electrical repair e.g., replace relay. | Reconnect exhaust line. |  | YES | YES | YES | YES |  | NO | NO | NO | NO |  | Not Applicable | Not Applicable | Not Applicable | Not Applicable |  | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 |  |  | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 |  |  | NO | NO | NO | NO |  | 0% | 0% | 0% | 0% |  | 0 | 0 | 0 | 0 |  | None | Not Given | By User | By User | Not Given | D5092.031b-DS1-1.JPG | none | none | none |  | No | None | YES
D5092.033f | D5092.033f | Diesel generator - Capacity: 350 to <750 kVA - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | Costing is per unit and is based upon 500 kVa. | Normal - Designed for seismic loads but no special seismic certification | Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints | Each | Each | Peak Floor Acceleration | g | 5 | DS1 | DS2 | DS3 | DS4 | DS5 | Mutually Exclusive | Mutually Exclusive | Mutually Exclusive | Mutually Exclusive | Mutually Exclusive | MutEx(DS1,DS2,DS3,DS4,DS5) | 665 | KV 500 | YES | BLDG | Anchorage failure. | Anchorage failure & Equipment damaged beyond repair. | Damaged, Inoperative but anchorage is OK | Equipment is damaged and inoperative but anchorage is OK. | Equipment is damaged and inoperative but anchorage is OK. | 0.35 | 0.15 | 0.4 | 0.05 | 0.05 | By User | By User | By User | By User | By User | User to Calculate | User to Calculate | User to Calculate | User to Calculate | User to Calculate | User to Calculate | User to Calculate | User to Calculate | User to Calculate | User to Calculate | By User | By User | By User | By User | By User | NO | NO | Average | Average | Superior | Superior | Repair anchorage and concrete pad and remount equipment. | Replace equipment including attached utilities in addition to repairing anchorage and concrete pad. | Repair fracture pipes & damaged nozzles, and or reconnect exhaust line. | Overhaul because of drive shaft misalignment. | minor electrical repair e.g., replace relays. | YES | YES | YES | YES | YES | NO | NO | NO | NO | NO | Not Applicable | Not Applicable | Not Applicable | Not Applicable | Not Applicable | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | NO | NO | NO | NO | NO | 0% | 0% | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | User to provide median demand and dispersion values. The values listed are default PACT values and do not represent the response of this component. | Not Given | By User | By User | Not Given | D5092.031a-DS1-1.JPG | none | none | none | none | No | None | YES
D5092.033g | D5092.033g | Diesel generator - Capacity: 750 to 1200 kVA - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only | Costing is per unit and is based upon 1000 kVa. | Normal - Designed for seismic loads but no special seismic certification | Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints | Each | Each | Peak Floor Acceleration | g | 2 | DS1 | DS2 |  |  |  | Mutually Exclusive | Mutually Exclusive |  |  |  | MutEx(DS1,DS2) | 666 | KV 1000 | YES | BLDG | Anchorage failure. | Anchorage failure & Equipment damaged beyond repair. |  |  |  | 0.7 | 0.3 |  |  |  | By User | By User |  |  |  | User to Calculate | User to Calculate |  |  |  | User to Calculate | User to Calculate |  |  |  | By User | By User |  |  |  | NO | NO | Average | Average | Superior | Superior | Repair anchorage and concrete pad and remount equipment. | Replace equipment including attached utilities in addition to repairing anchorage and concrete pad. |  |  |  | YES | YES |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | NO |  |  |  | 0% | 0% |  |  |  | 0 | 0 |  |  |  | User to provide median demand and dispersion values. The values listed are default PACT values and do not represent the response of this component. | Not Given | By User | By User | Not Given | D5092.031a-DS1-1.JPG | none |  |  |  | No | None | YES
D5092.033h | D5092.033h | Diesel generator - Capacity: 750 to 1200 kVA - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only | Costing is per unit and is based upon 1000 kVa. | Normal - Designed for seismic loads but no special seismic certification | Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints | Each | Each | Peak Floor Acceleration | g | 4 | DS1 | DS2 | DS3 | DS4 |  | Mutually Exclusive | Mutually Exclusive | Mutually Exclusive | Mutually Exclusive |  | MutEx(DS1,DS2,DS3,DS4) | 667 | KV 1000 | YES | BLDG | Damaged, inoperative but anchorage is OK. Pipes and nozzles damaged. | Damaged, inoperative but anchorage is OK. Drive shaft misalignment. | Damaged, inoperative but anchorage is OK. Minor electrical damage, e.g., failed relay. | Damaged, inoperative but anchorage is OK. Exhaust line disconnected at expansion bellows. |  | 0.7 | 0.1 | 0.1 | 0.1 |  | 2 | 2 | 2 | 2 |  | 0.2 | 0.2 | 0.2 | 0.2 |  | 0.1 | 0.1 | 0.1 | 0.1 |  | 0.2 | 0.2 | 0.2 | 0.2 |  | NO | NO | Average | Average | Superior | Superior | Repair fracture pipes and damaged nozzles. | Overhaul because of drive shaft misalignment. | Minor electrical repair e.g., replace relay. | Reconnect exhaust line. |  | YES | YES | YES | YES |  | NO | NO | NO | NO |  | Not Applicable | Not Applicable | Not Applicable | Not Applicable |  | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 |  |  | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 |  |  | NO | NO | NO | NO |  | 0% | 0% | 0% | 0% |  | 0 | 0 | 0 | 0 |  | None | Not Given | By User | By User | Not Given | D5092.031b-DS1-1.JPG | none | none | none |  | No | None | YES
D5092.033i | D5092.033i | Diesel generator - Capacity: 750 to 1200 kVA - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | Costing is per unit and is based upon 1000 kVa. | Normal - Designed for seismic loads but no special seismic certification | Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints | Each | Each | Peak Floor Acceleration | g | 5 | DS1 | DS2 | DS3 | DS4 | DS5 | Mutually Exclusive | Mutually Exclusive | Mutually Exclusive | Mutually Exclusive | Mutually Exclusive | MutEx(DS1,DS2,DS3,DS4,DS5) | 668 | KV 1000 | YES | BLDG | Anchorage failure. | Anchorage failure & Equipment damaged beyond repair. | Damaged, Inoperative but anchorage is OK | Equipment is damaged and inoperative but anchorage is OK. | Equipment is damaged and inoperative but anchorage is OK. | 0.35 | 0.15 | 0.4 | 0.05 | 0.05 | By User | By User | By User | By User | By User | User to Calculate | User to Calculate | User to Calculate | User to Calculate | User to Calculate | User to Calculate | User to Calculate | User to Calculate | User to Calculate | User to Calculate | By User | By User | By User | By User | By User | NO | NO | Average | Average | Superior | Superior | Repair anchorage and concrete pad and remount equipment. | Replace equipment including attached utilities in addition to repairing anchorage and concrete pad. | Repair fracture pipes & damaged nozzles, and or reconnect exhaust line. | Overhaul because of drive shaft misalignment. | minor electrical repair e.g., replace relays. | YES | YES | YES | YES | YES | NO | NO | NO | NO | NO | Not Applicable | Not Applicable | Not Applicable | Not Applicable | Not Applicable | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | NO | NO | NO | NO | NO | 0% | 0% | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | User to provide median demand and dispersion values. The values listed are default PACT values and do not represent the response of this component. | Not Given | By User | By User | Not Given | D5092.031a-DS1-1.JPG | none | none | none | none | No | None | YES
D5092.033j | D5092.033j | Diesel generator - Capacity: 1200 to 2000 kVa - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only | Costing is per unit and is based upon 1500 kVa. | Normal - Designed for seismic loads but no special seismic certification | Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints | Each | Each | Peak Floor Acceleration | g | 2 | DS1 | DS2 |  |  |  | Mutually Exclusive | Mutually Exclusive |  |  |  | MutEx(DS1,DS2) | 669 | KV 1500 | YES | BLDG | Anchorage failure. | Anchorage failure & Equipment damaged beyond repair. |  |  |  | 0.7 | 0.3 |  |  |  | By User | By User |  |  |  | User to Calculate | User to Calculate |  |  |  | User to Calculate | User to Calculate |  |  |  | By User | By User |  |  |  | NO | NO | Average | Average | Superior | Superior | Repair anchorage and concrete pad and remount equipment. | Replace equipment including attached utilities in addition to repairing anchorage and concrete pad. |  |  |  | YES | YES |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | NO |  |  |  | 0% | 0% |  |  |  | 0 | 0 |  |  |  | User to provide median demand and dispersion values. The values listed are default PACT values and do not represent the response of this component. | Not Given | By User | By User | Not Given | D5092.031a-DS1-1.JPG | none |  |  |  | No | None | YES
D5092.033k | D5092.033k | Diesel generator - Capacity: 1200 to 2000 kVa - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only | Costing is per unit and is based upon 1500 kVa. | Normal - Designed for seismic loads but no special seismic certification | Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints | Each | Each | Peak Floor Acceleration | g | 4 | DS1 | DS2 | DS3 | DS4 |  | Mutually Exclusive | Mutually Exclusive | Mutually Exclusive | Mutually Exclusive |  | MutEx(DS1,DS2,DS3,DS4) | 670 | KV 1500 | YES | BLDG | Damaged, inoperative but anchorage is OK. Pipes and nozzles damaged. | Damaged, inoperative but anchorage is OK. Drive shaft misalignment. | Damaged, inoperative but anchorage is OK. Minor electrical damage, e.g., failed relay. | Damaged, inoperative but anchorage is OK. Exhaust line disconnected at expansion bellows. |  | 0.7 | 0.1 | 0.1 | 0.1 |  | 2 | 2 | 2 | 2 |  | 0.2 | 0.2 | 0.2 | 0.2 |  | 0.1 | 0.1 | 0.1 | 0.1 |  | 0.2 | 0.2 | 0.2 | 0.2 |  | NO | NO | Average | Average | Superior | Superior | Repair fracture pipes and damaged nozzles. | Overhaul because of drive shaft misalignment. | Minor electrical repair e.g., replace relay. | Reconnect exhaust line. |  | YES | YES | YES | YES |  | NO | NO | NO | NO |  | Not Applicable | Not Applicable | Not Applicable | Not Applicable |  | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 |  |  | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 |  |  | NO | NO | NO | NO |  | 0% | 0% | 0% | 0% |  | 0 | 0 | 0 | 0 |  | None | Not Given | By User | By User | Not Given | D5092.031b-DS1-1.JPG | none | none | none |  | No | None | YES
D5092.033l | D5092.033l | Diesel generator - Capacity: 1200 to 2000 kVa - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | Costing is per unit and is based upon 1500 kVa. | Normal - Designed for seismic loads but no special seismic certification | Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints | Each | Each | Peak Floor Acceleration | g | 5 | DS1 | DS2 | DS3 | DS4 | DS5 | Mutually Exclusive | Mutually Exclusive | Mutually Exclusive | Mutually Exclusive | Mutually Exclusive | MutEx(DS1,DS2,DS3,DS4,DS5) | 671 | KV 1500 | YES | BLDG | Anchorage failure. | Anchorage failure & Equipment damaged beyond repair. | Damaged, Inoperative but anchorage is OK | Equipment is damaged and inoperative but anchorage is OK. | Equipment is damaged and inoperative but anchorage is OK. | 0.35 | 0.15 | 0.4 | 0.05 | 0.05 | By User | By User | By User | By User | By User | User to Calculate | User to Calculate | User to Calculate | User to Calculate | User to Calculate | User to Calculate | User to Calculate | User to Calculate | User to Calculate | User to Calculate | By User | By User | By User | By User | By User | NO | NO | Average | Average | Superior | Superior | Repair anchorage and concrete pad and remount equipment. | Replace equipment including attached utilities in addition to repairing anchorage and concrete pad. | Repair fracture pipes & damaged nozzles, and or reconnect exhaust line. | Overhaul because of drive shaft misalignment. | minor electrical repair e.g., replace relays. | YES | YES | YES | YES | YES | NO | NO | NO | NO | NO | Not Applicable | Not Applicable | Not Applicable | Not Applicable | Not Applicable | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | NO | NO | NO | NO | NO | 0% | 0% | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | User to provide median demand and dispersion values. The values listed are default PACT values and do not represent the response of this component. | Not Given | By User | By User | Not Given | D5092.031a-DS1-1.JPG | none | none | none | none | No | None | YES
E2022.001 | E2022.001 | Modular office work stations. | Unanchored and installed per manufacturer's recommendations on a carpeted floor. | Any | Unsecured | Each | Each | Peak Floor Acceleration | g | 1 | DS1 |  |  |  |  | Sequential |  |  |  |  | Seq(DS1) | 672 | EA 1 | NO | NO | Wall units need to be adjusted and straightened. Some elements are bent / damaged and need to be replaced. |  |  |  |  | 1 |  |  |  |  | 1 |  |  |  |  | Not Specified |  |  |  |  | Not Specified |  |  |  |  | 0.4 |  |  |  |  | NO | NO | Not Rated | Not Rated | Not Rated | Not Rated | Adjust and or straightened wall units. Replace damaged units. Assume a repair cost of 5% of the replacement value. |  |  |  |  | NO |  |  |  |  | NO |  |  |  |  | Not Applicable |  |  |  |  | 0% | 0 | [8 empty] | 0% | 0 | [8 empty] | NO |  |  |  |  | 0% |  |  |  |  | 0 |  |  |  |  | This component requires user specified cost and time consequence data. Values within PACT are defaults (equal to zero) and do not represent actual consequence. | Not Given | By User | By User | Not Given | none |  |  |  |  | No | None | NO
E2022.010 | E2022.010 | Unsecured fragile objects on shelves, unknown restraint | Costing to be furnished by user. Consequence data assumes 16 SF of damage area. | Any | Unknown conditions: some objects may have museum putty. Some cabinets may have latches. Some cabinets may be secured to the wall. | Each | Each | Peak Floor Acceleration | g | 1 | DS1 |  |  |  |  | Sequential |  |  |  |  | Seq(DS1) | 673 | EA 1 | NO | NO | Object falls off shelf or shelf overturns and object breaks or object breaks within cabinet. |  |  |  |  | 1 |  |  |  |  | 0.4 |  |  |  |  | 0.4 |  |  |  |  | 0.3 |  |  |  |  | 0.6 |  |  |  |  | NO | NO | Not Rated | Not Rated | Not Rated | Not Rated | Replace object. Note: user must supply cost of replacement. |  |  |  |  | NO |  |  |  |  | YES |  |  |  |  | 16 SF |  |  |  |  | 10% | 0.5 | [8 empty] | 0% | 0 | [8 empty] | NO |  |  |  |  | 0% |  |  |  |  | 0 |  |  |  |  | This component requires user specified cost and time consequence data. Values within PACT are defaults (equal to zero) and do not represent actual consequence. | Not Given | By User | By User | Not Given | E2022.010-DS1-1.JPG |  |  |  |  | No | None | NO
E2022.011 | E2022.011 | Fragile contents secured by museum putty, Velcro or other weak but sticky stuff | Costing to be furnished by user. Consequence data assumes 16 SF of damage area. | Any | High adhesion surface (e.g., museum putty) and secured in cabinets (e.g., with latches & cabinet is secured to wall) | Each | Each | Peak Floor Acceleration | g | 1 | DS1 |  |  |  |  | Sequential |  |  |  |  | Seq(DS1) | 674 | EA 1 | NO | NO | Object falls off shelf or shelf overturns and object breaks or object breaks within cabinet. |  |  |  |  | 1 |  |  |  |  | 1 |  |  |  |  | 0.4 |  |  |  |  | 0.3 |  |  |  |  | 0.5 |  |  |  |  | NO | NO | Not Rated | Not Rated | Not Rated | Not Rated | Replace object. Note: user must supply cost of replacement. |  |  |  |  | NO |  |  |  |  | YES |  |  |  |  | 16 SF |  |  |  |  | 10% | 0.5 | [8 empty] | 0% | 0 | [8 empty] | NO |  |  |  |  | 0% |  |  |  |  | 0 |  |  |  |  | This component requires user specified cost and time consequence data. Values within PACT are defaults (equal to zero) and do not represent actual consequence. | Not Given | By User | By User | Not Given | E2022.010-DS1-1.JPG |  |  |  |  | No | None | NO
E2022.012 | E2022.012 | Fragile contents on shelves in storage cabinets with latches | Costing to be furnished by user. Consequence data assumes 16 SF of damage area. | Any | In secured cabinets (e.g., with latches) | Each | Each | Peak Floor Acceleration | g | 1 | DS1 |  |  |  |  | Sequential |  |  |  |  | Seq(DS1) | 675 | EA 1 | NO | NO | Object falls off shelf or shelf overturns and object breaks or object breaks within cabinet. |  |  |  |  | 1 |  |  |  |  | 0.6 |  |  |  |  | 0.5 |  |  |  |  | 0.3 |  |  |  |  | 0.6 |  |  |  |  | NO | NO | Not Rated | Not Rated | Not Rated | Not Rated | Replace object. Note: user must supply cost of replacement. |  |  |  |  | NO |  |  |  |  | YES |  |  |  |  | 16 SF |  |  |  |  | 5% | 0.5 | [8 empty] | 0% | 0 | [8 empty] | NO |  |  |  |  | 0% |  |  |  |  | 0 |  |  |  |  | This component requires user specified cost and time consequence data. Values within PACT are defaults (equal to zero) and do not represent actual consequence. | Not Given | By User | By User | Not Given | E2022.010-DS1-1.JPG |  |  |  |  | No | None | NO
E2022.013 | E2022.013 | Unsecured fragile objects on shelves, low friction surface | Costing to be furnished by user. Consequence data assumes 16 SF of damage area. | Any | Low friction coefficient (e.g., glass or metal on wood), in unsecured cabinets (e.g., no latches) | Each | Each | Peak Floor Acceleration | g | 1 | DS1 |  |  |  |  | Sequential |  |  |  |  | Seq(DS1) | 676 | EA 1 | NO | NO | Object falls off shelf or shelf overturns and object breaks or object breaks within cabinet. |  |  |  |  | 1 |  |  |  |  | 0.25 |  |  |  |  | 0.4 |  |  |  |  | 0.3 |  |  |  |  | 0.5 |  |  |  |  | NO | NO | Not Rated | Not Rated | Not Rated | Not Rated | Replace object. Note: user must supply cost of replacement. |  |  |  |  | NO |  |  |  |  | YES |  |  |  |  | 16 SF |  |  |  |  | 10% | 0.5 | [8 empty] | 0% | 0 | [8 empty] | NO |  |  |  |  | 0% |  |  |  |  | 0 |  |  |  |  | This component requires user specified cost and time consequence data. Values within PACT are defaults (equal to zero) and do not represent actual consequence. | Not Given | By User | By User | Not Given | E2022.010-DS1-1.JPG |  |  |  |  | No | None | NO
E2022.020 | E2022.020 | Home entertainment equipment, unknown installation | Costing to be furnished by user. Consequence data assumes 16 SF of damage area. | Any | Unknown | Each | Each | Peak Floor Acceleration | g | 1 | DS1 |  |  |  |  | Sequential |  |  |  |  | Seq(DS1) | 677 | EA 1 | NO | NO | Falls, does not function. |  |  |  |  | 1 |  |  |  |  | 0.8 |  |  |  |  | 0.4 |  |  |  |  | 0.25 |  |  |  |  | 0.45 |  |  |  |  | NO | NO | Not Rated | Not Rated | Not Rated | Not Rated | Replace equipment. User must supply replacement cost. |  |  |  |  | NO |  |  |  |  | YES |  |  |  |  | 16 SF |  |  |  |  | 10% | 0.5 | [8 empty] | 5% | 0.5 | [8 empty] | NO |  |  |  |  | 0% |  |  |  |  | 0 |  |  |  |  | This component requires user specified cost and time consequence data. Values within PACT are defaults (equal to zero) and do not represent actual consequence. | Not Given | By User | By User | Not Given | E2022.020-DS1-1.JPG |  |  |  |  | No | None | NO
E2022.021 | E2022.021 | Electronic equipment on wall mount brackets | Costing to be furnished by user. Consequence data assumes 16 SF of damage area. | Any | Unsecured | Each | Each | Peak Floor Acceleration | g | 1 | DS1 |  |  |  |  | Sequential |  |  |  |  | Seq(DS1) | 678 | EA 1 | NO | NO | Falls, does not function. |  |  |  |  | 1 |  |  |  |  | 2.5 |  |  |  |  | 0.4 |  |  |  |  | 0.3 |  |  |  |  | 0.5 |  |  |  |  | NO | NO | Not Rated | Not Rated | Not Rated | Not Rated | Replace equipment. User must supply replacement cost. |  |  |  |  | NO |  |  |  |  | YES |  |  |  |  | 16 SF |  |  |  |  | 20% | 0.5 | [8 empty] | 10% | 0.5 | [8 empty] | NO |  |  |  |  | 0% |  |  |  |  | 0 |  |  |  |  | This component requires user specified cost and time consequence data. Values within PACT are defaults (equal to zero) and do not represent actual consequence. | Not Given | By User | By User | Not Given | E2022.020-DS1-1.JPG |  |  |  |  | No | None | NO
E2022.022 | E2022.022 | Desktop electronics including computers, monitors, stereos, etc on a slip resistant surface | Costing to be furnished by user. Consequence data assumes 16 SF of damage area. | Any | Unsecured | Each | Each | Peak Floor Acceleration | g | 1 | DS1 |  |  |  |  | Sequential |  |  |  |  | Seq(DS1) | 679 | EA 1 | NO | NO | Falls, does not function. |  |  |  |  | 1 |  |  |  |  | 1 |  |  |  |  | 0.4 |  |  |  |  | 0.3 |  |  |  |  | 0.5 |  |  |  |  | NO | NO | Not Rated | Not Rated | Not Rated | Not Rated | Replace equipment. User must supply replacement cost. |  |  |  |  | NO |  |  |  |  | YES |  |  |  |  | 16 SF |  |  |  |  | 10% | 0.5 | [8 empty] | 0% | 0 | [8 empty] | NO |  |  |  |  | 0% |  |  |  |  | 0 |  |  |  |  | This component requires user specified cost and time consequence data. Values within PACT are defaults (equal to zero) and do not represent actual consequence. | Not Given | By User | By User | Not Given | E2022.020-DS1-1.JPG |  |  |  |  | No | None | NO
E2022.023 | E2022.023 | Desktop electronics including computers, monitors, stereos, etc, smooth surface | Costing to be furnished by user. Consequence data assumes 16 SF of damage area. | Any | Unsecured | Each | Each | Peak Floor Acceleration | g | 1 | DS1 |  |  |  |  | Sequential |  |  |  |  | Seq(DS1) | 680 | EA 1 | NO | NO | Falls, does not function. |  |  |  |  | 1 |  |  |  |  | 0.4 |  |  |  |  | 0.4 |  |  |  |  | 0.3 |  |  |  |  | 0.5 |  |  |  |  | NO | NO | Not Rated | Not Rated | Not Rated | Not Rated | Replace equipment. User must supply replacement cost. |  |  |  |  | NO |  |  |  |  | YES |  |  |  |  | 16 SF |  |  |  |  | 10% | 0.5 | [8 empty] | 0% | 0 | [8 empty] | NO |  |  |  |  | 0% |  |  |  |  | 0 |  |  |  |  | This component requires user specified cost and time consequence data. Values within PACT are defaults (equal to zero) and do not represent actual consequence. | Not Given | By User | By User | Not Given | E2022.020-DS1-1.JPG |  |  |  |  | No | None | NO
E2022.102a | E2022.102a | Bookcase, 2 shelves, unanchored laterally | Standard bookcase, unanchored laterally. Bookcase is 12-5/8" deep x 29" tall | Normal | Unsecured | Each | Each | Peak Floor Velocity | meter/sec | 1 | DS1 |  |  |  |  | Sequential |  |  |  |  | Seq(DS1) | 681 | EA 1 | NO | NO | Book case falls over and contents are scattered. Likely damage to bookcase. |  |  |  |  | 1 |  |  |  |  | 0.724 |  |  |  |  | User to Calculate |  |  |  |  | User to Calculate |  |  |  |  | 0.5 |  |  |  |  | NO | NO | Not Rated | Not Rated | Not Rated | Not Rated | Replace bookcase and restack / replace contents. |  |  |  |  | NO |  |  |  |  | NO |  |  |  |  | Not Applicable |  |  |  |  | 0% | 0 | [8 empty] | 0% | 0 | [8 empty] | NO |  |  |  |  | 0% |  |  |  |  | 0 |  |  |  |  | Peak floor velocity limit is calculated as a function of the aspect ratio of the filing cabinet and the building period, T. At the ground floor the fragility will be based upon the ground motion only. This component requires user specified cost and time consequence data. Values within PACT are defaults (equal to zero) and do not represent actual consequence. | Not Given | By User | By User | Not Given | none |  |  |  |  | No | None | YES
E2022.102b | E2022.102b | Bookcase, 2 shelves, anchored laterally | Standard bookcase, anchored laterally. Bookcase is 12-5/8" deep x 29" tall. | Normal | Secured | Each | Each | Peak Floor Acceleration | g | 1 | DS1 |  |  |  |  | Sequential |  |  |  |  | Seq(DS1) | 682 | EA 1 | NO | NO | Book case falls over and contents are scattered. Likely damage to bookcase. |  |  |  |  | 1 |  |  |  |  | By User |  |  |  |  | User to Calculate |  |  |  |  | User to Calculate |  |  |  |  | By User |  |  |  |  | NO | NO | Not Rated | Not Rated | Not Rated | Not Rated | Replace bookcase and restack / replace contents. |  |  |  |  | NO |  |  |  |  | NO |  |  |  |  | Not Applicable |  |  |  |  | 0% | 0 | [8 empty] | 0% | 0 | [8 empty] | NO |  |  |  |  | 0% |  |  |  |  | 0 |  |  |  |  | User to provide median demand and dispersion values. The values listed are default PACT values and do not represent the response of this component. This component requires user specified cost and time consequence data. Values within PACT are defaults (equal to zero) and do not represent actual consequence. | Not Given | By User | By User | Not Given | none |  |  |  |  | No | None | YES
E2022.103a | E2022.103a | Bookcase, 3 shelves, unanchored laterally | Standard bookcase, unanchored laterally. Bookcase is 12-5/8" deep x 41" tall | Normal | Unsecured | Each | Each | Peak Floor Velocity | meter/sec | 1 | DS1 |  |  |  |  | Sequential |  |  |  |  | Seq(DS1) | 683 | EA 1 | NO | NO | Book case falls over and contents are scattered. Likely damage to bookcase. |  |  |  |  | 1 |  |  |  |  | 0.493 |  |  |  |  | User to Calculate |  |  |  |  | User to Calculate |  |  |  |  | 0.5 |  |  |  |  | NO | NO | Not Rated | Not Rated | Not Rated | Not Rated | Replace bookcase and restack / replace contents. |  |  |  |  | NO |  |  |  |  | NO |  |  |  |  | Not Applicable |  |  |  |  | 0% | 0 | [8 empty] | 0% | 0 | [8 empty] | NO |  |  |  |  | 0% |  |  |  |  | 0 |  |  |  |  | Peak floor velocity limit is calculated as a function of the aspect ratio of the filing cabinet and the building period, T. At the ground floor the fragility will be based upon the ground motion only. This component requires user specified cost and time consequence data. Values within PACT are defaults (equal to zero) and do not represent actual consequence. | Not Given | By User | By User | Not Given | none |  |  |  |  | No | None | YES
E2022.103b | E2022.103b | Bookcase, 3 shelves, anchored laterally | Standard bookcase, anchored laterally. Bookcase is 12-5/8" deep x 41" tall. | Normal | Secured | Each | Each | Peak Floor Acceleration | g | 1 | DS1 |  |  |  |  | Sequential |  |  |  |  | Seq(DS1) | 684 | EA 1 | NO | NO | Book case falls over and contents are scattered. Likely damage to bookcase. |  |  |  |  | 1 |  |  |  |  | By User |  |  |  |  | User to Calculate |  |  |  |  | User to Calculate |  |  |  |  | By User |  |  |  |  | NO | NO | Not Rated | Not Rated | Not Rated | Not Rated | Replace bookcase and restack / replace contents. |  |  |  |  | NO |  |  |  |  | NO |  |  |  |  | Not Applicable |  |  |  |  | 0% | 0 | [8 empty] | 0% | 0 | [8 empty] | NO |  |  |  |  | 0% |  |  |  |  | 0 |  |  |  |  | User to provide median demand and dispersion values. The values listed are default PACT values and do not represent the response of this component. This component requires user specified cost and time consequence data. Values within PACT are defaults (equal to zero) and do not represent actual consequence. | Not Given | By User | By User | Not Given | none |  |  |  |  | No | None | YES
E2022.104a | E2022.104a | Bookcase, 4 shelves, unanchored laterally | Standard bookcase, unanchored laterally. Bookcase is 12-5/8" deep x 56" tall | Normal | Unsecured | Each | Each | Peak Floor Velocity | meter/sec | 1 | DS1 |  |  |  |  | Sequential |  |  |  |  | Seq(DS1) | 685 | EA 1 | NO | NO | Book case falls over and contents are scattered. Likely damage to bookcase. |  |  |  |  | 1 |  |  |  |  | 0.361 |  |  |  |  | User to Calculate |  |  |  |  | User to Calculate |  |  |  |  | 0.5 |  |  |  |  | NO | NO | Not Rated | Not Rated | Not Rated | Not Rated | Replace bookcase and restack / replace contents. |  |  |  |  | NO |  |  |  |  | NO |  |  |  |  | Not Applicable |  |  |  |  | 0% | 0 | [8 empty] | 0% | 0 | [8 empty] | NO |  |  |  |  | 0% |  |  |  |  | 0 |  |  |  |  | Peak floor velocity limit is calculated as a function of the aspect ratio of the filing cabinet and the building period, T. At the ground floor the fragility will be based upon the ground motion only. This component requires user specified cost and time consequence data. Values within PACT are defaults (equal to zero) and do not represent actual consequence. | Not Given | By User | By User | Not Given | none |  |  |  |  | No | None | YES
E2022.104b | E2022.104b | Bookcase, 4 shelves, anchored laterally | Standard bookcase, anchored laterally. Bookcase is 12-5/8" deep x 56" tall. | Normal | Secured | Each | Each | Peak Floor Acceleration | g | 1 | DS1 |  |  |  |  | Sequential |  |  |  |  | Seq(DS1) | 686 | EA 1 | NO | NO | Book case falls over and contents are scattered. Likely damage to bookcase. |  |  |  |  | 1 |  |  |  |  | By User |  |  |  |  | User to Calculate |  |  |  |  | User to Calculate |  |  |  |  | By User |  |  |  |  | NO | NO | Not Rated | Not Rated | Not Rated | Not Rated | Replace bookcase and restack / replace contents. |  |  |  |  | NO |  |  |  |  | NO |  |  |  |  | Not Applicable |  |  |  |  | 0% | 0 | [8 empty] | 0% | 0 | [8 empty] | NO |  |  |  |  | 0% |  |  |  |  | 0 |  |  |  |  | User to provide median demand and dispersion values. The values listed are default PACT values and do not represent the response of this component. This component requires user specified cost and time consequence data. Values within PACT are defaults (equal to zero) and do not represent actual consequence. | Not Given | By User | By User | Not Given | none |  |  |  |  | No | None | YES
E2022.105a | E2022.105a | Bookcase, 5 shelves, unanchored laterally | Standard bookcase, unanchored laterally. Bookcase is 12-5/8" deep x 71" tall | Normal | Unsecured | Each | Each | Peak Floor Velocity | meter/sec | 1 | DS1 |  |  |  |  | Sequential |  |  |  |  | Seq(DS1) | 687 | EA 1 | NO | NO | Book case falls over and contents are scattered. Likely damage to bookcase. |  |  |  |  | 1 |  |  |  |  | 0.29 |  |  |  |  | User to Calculate |  |  |  |  | User to Calculate |  |  |  |  | 0.5 |  |  |  |  | NO | NO | Not Rated | Not Rated | Not Rated | Not Rated | Replace bookcase and restack / replace contents. |  |  |  |  | NO |  |  |  |  | YES |  |  |  |  | 10 SF |  |  |  |  | By User | 0.5 | [8 empty] | 0% | 0 | [8 empty] | NO |  |  |  |  | 0% |  |  |  |  | 0 |  |  |  |  | Peak floor velocity limit is calculated as a function of the aspect ratio of the filing cabinet and the building period, T. At the ground floor the fragility will be based upon the ground motion only. This component requires user specified cost and time consequence data. Values within PACT are defaults (equal to zero) and do not represent actual consequence. | Not Given | By User | By User | Not Given | none |  |  |  |  | No | None | YES
E2022.105b | E2022.105b | Bookcase, 5 shelves, anchored laterally | Standard bookcase, anchored laterally. Bookcase is 12-5/8" deep x 71" tall. | Normal | Secured | Each | Each | Peak Floor Acceleration | g | 1 | DS1 |  |  |  |  | Sequential |  |  |  |  | Seq(DS1) | 688 | EA 1 | NO | NO | Book case falls over and contents are scattered. Likely damage to bookcase. |  |  |  |  | 1 |  |  |  |  | By User |  |  |  |  | User to Calculate |  |  |  |  | User to Calculate |  |  |  |  | By User |  |  |  |  | NO | NO | Not Rated | Not Rated | Not Rated | Not Rated | Replace bookcase and restack / replace contents. |  |  |  |  | NO |  |  |  |  | YES |  |  |  |  | 10 SF |  |  |  |  | By User | 0.5 | [8 empty] | 0% | 0 | [8 empty] | NO |  |  |  |  | 0% |  |  |  |  | 0 |  |  |  |  | User to provide median demand and dispersion values. The values listed are default PACT values and do not represent the response of this component. This component requires user specified cost and time consequence data. Values within PACT are defaults (equal to zero) and do not represent actual consequence. | Not Given | By User | By User | Not Given | none |  |  |  |  | No | None | YES
E2022.106a | E2022.106a | Bookcase, 6 shelves, unanchored laterally | Standard bookcase, unanchored laterally. Bookcase is 12-5/8" deep x 81-1/4" tall | Normal | Unsecured | Each | Each | Peak Floor Velocity | meter/sec | 1 | DS1 |  |  |  |  | Sequential |  |  |  |  | Seq(DS1) | 689 | EA 1 | NO | NO | Book case falls over and contents are scattered. Likely damage to bookcase. |  |  |  |  | 1 |  |  |  |  | 0.251 |  |  |  |  | User to Calculate |  |  |  |  | User to Calculate |  |  |  |  | 0.5 |  |  |  |  | NO | NO | Not Rated | Not Rated | Not Rated | Not Rated | Replace bookcase and restack / replace contents. |  |  |  |  | NO |  |  |  |  | YES |  |  |  |  | 20 SF |  |  |  |  | By User | 0.5 | [8 empty] | 0% | 0 | [8 empty] | NO |  |  |  |  | 0% |  |  |  |  | 0 |  |  |  |  | Peak floor velocity limit is calculated as a function of the aspect ratio of the filing cabinet and the building period, T. At the ground floor the fragility will be based upon the ground motion only. This component requires user specified cost and time consequence data. Values within PACT are defaults (equal to zero) and do not represent actual consequence. | Not Given | By User | By User | Not Given | none |  |  |  |  | No | None | YES
E2022.106b | E2022.106b | Bookcase, 6 shelves, anchored laterally | Standard bookcase, anchored laterally. Bookcase is 12-5/8" deep x 81-1/4" tall. | Normal | Secured | Each | Each | Peak Floor Acceleration | g | 1 | DS1 |  |  |  |  | Sequential |  |  |  |  | Seq(DS1) | 690 | EA 1 | NO | NO | Book case falls over and contents are scattered. Likely damage to bookcase. |  |  |  |  | 1 |  |  |  |  | By User |  |  |  |  | User to Calculate |  |  |  |  | User to Calculate |  |  |  |  | By User |  |  |  |  | NO | NO | Not Rated | Not Rated | Not Rated | Not Rated | Replace bookcase and restack / replace contents. |  |  |  |  | NO |  |  |  |  | YES |  |  |  |  | 20 SF |  |  |  |  | By User | 0.5 | [8 empty] | 0% | 0 | [8 empty] | NO |  |  |  |  | 0% |  |  |  |  | 0 |  |  |  |  | User to provide median demand and dispersion values. The values listed are default PACT values and do not represent the response of this component. This component requires user specified cost and time consequence data. Values within PACT are defaults (equal to zero) and do not represent actual consequence. | Not Given | By User | By User | Not Given | none |  |  |  |  | No | None | YES
E2022.112a | E2022.112a | Vertical Filing Cabinet, 2 drawer, unanchored laterally | Filing cabinet, unanchored laterally. Cabinet has 2 drawers and is 15" deep x 24" tall | Normal | Unsecured | Each | Each | Peak Floor Velocity | meter/sec | 1 | DS1 |  |  |  |  | Sequential |  |  |  |  | Seq(DS1) | 691 | EA 1 | NO | NO | Filing cabinet falls over and contents are scattered. Likely damage to file cabinet. |  |  |  |  | 1 |  |  |  |  | 1.229 |  |  |  |  | User to Calculate |  |  |  |  | User to Calculate |  |  |  |  | 0.5 |  |  |  |  | NO | NO | Not Rated | Not Rated | Not Rated | Not Rated | Replace filing cabinet and refile / replace contents. |  |  |  |  | NO |  |  |  |  | NO |  |  |  |  | Not Applicable |  |  |  |  | 0% | 0 | [8 empty] | 0% | 0 | [8 empty] | NO |  |  |  |  | 0% |  |  |  |  | 0 |  |  |  |  | Peak floor velocity limit is calculated as a function of the aspect ratio of the filing cabinet and the building period, T. At the ground floor the fragility will be based upon the ground motion only. This component requires user specified cost and time consequence data. Values within PACT are defaults (equal to zero) and do not represent actual consequence. | Not Given | By User | By User | Not Given | none |  |  |  |  | No | None | YES
E2022.112b | E2022.112b | Vertical Filing Cabinet, 2 drawer, anchored laterally | Filing cabinet, anchored laterally. Cabinet has 2 drawers and is 15" deep x 24" tall | Normal | Secured | Each | Each | Peak Floor Velocity | meter/sec | 1 | DS1 |  |  |  |  | Sequential |  |  |  |  | Seq(DS1) | 692 | EA 1 | NO | NO | Filing cabinet falls over and contents are scattered. Likely damage to file cabinet. |  |  |  |  | 1 |  |  |  |  | By User |  |  |  |  | User to Calculate |  |  |  |  | User to Calculate |  |  |  |  | By User |  |  |  |  | NO | NO | Not Rated | Not Rated | Not Rated | Not Rated | Replace filing cabinet and refile / replace contents. |  |  |  |  | NO |  |  |  |  | NO |  |  |  |  | Not Applicable |  |  |  |  | 0% | 0 | [8 empty] | 0% | 0 | [8 empty] | NO |  |  |  |  | 0% |  |  |  |  | 0 |  |  |  |  | User to provide median demand and dispersion values. The values listed are default PACT values and do not represent the response of this component. This component requires user specified cost and time consequence data. Values within PACT are defaults (equal to zero) and do not represent actual consequence. | Not Given | By User | By User | Not Given | none |  |  |  |  | No | None | YES
E2022.114a | E2022.114a | Vertical Filing Cabinet, 4 drawer, unanchored laterally | Filing cabinet, unanchored laterally. Cabinet has 4 drawers and is 15" deep x 52" tall | Normal | Unsecured | Each | Each | Peak Floor Velocity | meter/sec | 1 | DS1 |  |  |  |  | Sequential |  |  |  |  | Seq(DS1) | 693 | EA 1 | NO | NO | Filing cabinet falls over and contents are scattered. Likely damage to file cabinet. |  |  |  |  | 1 |  |  |  |  | 0.498 |  |  |  |  | User to Calculate |  |  |  |  | User to Calculate |  |  |  |  | 0.5 |  |  |  |  | NO | NO | Not Rated | Not Rated | Not Rated | Not Rated | Replace filing cabinet and refile / replace contents. |  |  |  |  | NO |  |  |  |  | YES |  |  |  |  | 10 SF |  |  |  |  | By User | 0.5 | [8 empty] | 0% | 0 | [8 empty] | NO |  |  |  |  | 0% |  |  |  |  | 0 |  |  |  |  | Peak floor velocity limit is calculated as a function of the aspect ratio of the filing cabinet and the building period, T. At the ground floor the fragility will be based upon the ground motion only. This component requires user specified cost and time consequence data. Values within PACT are defaults (equal to zero) and do not represent actual consequence. | Not Given | By User | By User | Not Given | none |  |  |  |  | No | None | YES
E2022.114b | E2022.114b | Vertical Filing Cabinet, 4 drawer, anchored laterally | Filing cabinet, anchored laterally. Cabinet has 4 drawers and is 15" deep x 52" tall | Normal | Secured | Each | Each | Peak Floor Velocity | meter/sec | 1 | DS1 |  |  |  |  | Sequential |  |  |  |  | Seq(DS1) | 694 | EA 1 | NO | NO | Filing cabinet falls over and contents are scattered. Likely damage to file cabinet. |  |  |  |  | 1 |  |  |  |  | By User |  |  |  |  | User to Calculate |  |  |  |  | User to Calculate |  |  |  |  | By User |  |  |  |  | NO | NO | Not Rated | Not Rated | Not Rated | Not Rated | Replace filing cabinet and refile / replace contents. |  |  |  |  | NO |  |  |  |  | YES |  |  |  |  | 10 SF |  |  |  |  | By User | 0.5 | [8 empty] | 0% | 0 | [8 empty] | NO |  |  |  |  | 0% |  |  |  |  | 0 |  |  |  |  | User to provide median demand and dispersion values. The values listed are default PACT values and do not represent the response of this component. This component requires user specified cost and time consequence data. Values within PACT are defaults (equal to zero) and do not represent actual consequence. | Not Given | By User | By User | Not Given | none |  |  |  |  | No | None | YES
E2022.124a | E2022.124a | Lateral Filing Cabinet, 2 drawer, unanchored laterally | Filing cabinet, unanchored laterally. Cabinet has 4 drawers and is 18.6" deep x 52.5" tall | Normal | Unsecured | Each | Each | Peak Floor Velocity | meter/sec | 1 | DS1 |  |  |  |  | Sequential |  |  |  |  | Seq(DS1) | 695 | EA 1 | NO | NO | Filing cabinet falls over and contents are scattered. Likely damage to file cabinet. |  |  |  |  | 1 |  |  |  |  | 0.688 |  |  |  |  | User to Calculate |  |  |  |  | User to Calculate |  |  |  |  | 0.5 |  |  |  |  | NO | NO | Not Rated | Not Rated | Not Rated | Not Rated | Replace filing cabinet and refile / replace contents. |  |  |  |  | NO |  |  |  |  | YES |  |  |  |  | 10 SF |  |  |  |  | By User | 0.5 | [8 empty] | 0% | 0 | [8 empty] | NO |  |  |  |  | 0% |  |  |  |  | 0 |  |  |  |  | Peak floor velocity limit is calculated as a function of the aspect ratio of the filing cabinet and the building period, T. At the ground floor the fragility will be based upon the ground motion only. This component requires user specified cost and time consequence data. Values within PACT are defaults (equal to zero) and do not represent actual consequence. | Not Given | By User | By User | Not Given | none |  |  |  |  | No | None | YES
E2022.124b | E2022.124b | Lateral Filing Cabinet, 2 drawer, anchored laterally | Filing cabinet, anchored laterally. Cabinet has 4 drawers and is 18.6" deep x 52.5" tall | Normal | Secured | Each | Each | Peak Floor Acceleration | g | 1 | DS1 |  |  |  |  | Sequential |  |  |  |  | Seq(DS1) | 696 | EA 1 | NO | NO | Filing cabinet falls over and contents are scattered. Likely damage to file cabinet. |  |  |  |  | 1 |  |  |  |  | By User |  |  |  |  | User to Calculate |  |  |  |  | User to Calculate |  |  |  |  | By User |  |  |  |  | NO | NO | Not Rated | Not Rated | Not Rated | Not Rated | Replace filing cabinet and refile / replace contents. |  |  |  |  | NO |  |  |  |  | YES |  |  |  |  | 10 SF |  |  |  |  | By User | 0.5 | [8 empty] | 0% | 0 | [8 empty] | NO |  |  |  |  | 0% |  |  |  |  | 0 |  |  |  |  | User to provide median demand and dispersion values. The values listed are default PACT values and do not represent the response of this component. This component requires user specified cost and time consequence data. Values within PACT are defaults (equal to zero) and do not represent actual consequence. | Not Given | By User | By User | Not Given | none |  |  |  |  | No | None | YES
E2022.125a | E2022.125a | Lateral Filing Cabinet, 4 drawer, unanchored laterally | Filing cabinet, unanchored laterally. Cabinet has 5 drawers and is 18.6" deep x 67.75" tall | Normal | Unsecured | Each | Each | Peak Floor Velocity | meter/sec | 1 | DS1 |  |  |  |  | Sequential |  |  |  |  | Seq(DS1) | 697 | EA 1 | NO | NO | Filing cabinet falls over and contents are scattered. Likely damage to file cabinet. |  |  |  |  | 1 |  |  |  |  | 0.526 |  |  |  |  | User to Calculate |  |  |  |  | User to Calculate |  |  |  |  | 0.5 |  |  |  |  | NO | NO | Not Rated | Not Rated | Not Rated | Not Rated | Replace filing cabinet and refile / replace contents. |  |  |  |  | NO |  |  |  |  | YES |  |  |  |  | 20 SF |  |  |  |  | By User | 0.5 | [8 empty] | 0% | 0 | [8 empty] | NO |  |  |  |  | 0% |  |  |  |  | 0 |  |  |  |  | Peak floor velocity limit is calculated as a function of the aspect ratio of the filing cabinet and the building period, T. At the ground floor the fragility will be based upon the ground motion only. This component requires user specified cost and time consequence data. Values within PACT are defaults (equal to zero) and do not represent actual consequence. | Not Given | By User | By User | Not Given | none |  |  |  |  | No | None | YES
E2022.125b | E2022.125b | Lateral Filing Cabinet, 4 drawer, anchored laterally | Filing cabinet, anchored laterally. Cabinet has 5 drawers and is 18.6" deep x 67.75" tall | Normal | Secured | Each | Each | Peak Floor Acceleration | g | 1 | DS1 |  |  |  |  | Sequential |  |  |  |  | Seq(DS1) | 698 | EA 1 | NO | NO | Filing cabinet falls over and contents are scattered. Likely damage to file cabinet. |  |  |  |  | 1 |  |  |  |  | By User |  |  |  |  | User to Calculate |  |  |  |  | User to Calculate |  |  |  |  | By User |  |  |  |  | NO | NO | Not Rated | Not Rated | Not Rated | Not Rated | Replace filing cabinet and refile / replace contents. |  |  |  |  | NO |  |  |  |  | YES |  |  |  |  | 20 SF |  |  |  |  | By User | 0.5 | [8 empty] | 0% | 0 | [8 empty] | NO |  |  |  |  | 0% |  |  |  |  | 0 |  |  |  |  | User to provide median demand and dispersion values. The values listed are default PACT values and do not represent the response of this component. This component requires user specified cost and time consequence data. Values within PACT are defaults (equal to zero) and do not represent actual consequence. | Not Given | By User | By User | Not Given | none |  |  |  |  | No | None | YES
F1012.001 | F1012.001 | Storage racks designed and installed before 2007, big box retail (12' to 15' tall) | Standard pallet back to back storage rack. Three to five levels tall with total height from 15 to 20 ft. Costing assumes one single side access rack. Costing of rack and restocking based upon 50 LF of rack. Costing of rack contents to be furnished by user. | Normal | Varies | Each | Each | Peak Floor Acceleration | g | 2 | DS1 | DS2 |  |  |  | Mutually Exclusive | Mutually Exclusive |  |  |  | MutEx(DS1,DS2) | 699 | LF 50 | NO | NO | Significant merchandise shedding from rack shelves. | Significant structural damage to rack structure. |  |  |  | 0.6 | 0.4 |  |  |  | 0.42 | 0.42 |  |  |  | User to Calculate | User to Calculate |  |  |  | User to Calculate | User to Calculate |  |  |  | 0.4 | 0.4 |  |  |  | NO | NO | Average | Average | Average | Average | Minor repair to storage rack. Resort and restock shelves. Clean up debris. | Remove and replace storage rack system. Make minor repair to adjacent finishes. Resort and restock shelves. Clean up debris. |  |  |  | NO | NO |  |  |  | YES | YES |  |  |  | By User | By User |  |  |  | By User | By User | By User | By User | [6 empty] | By User | By User | By User | By User | [6 empty] | By User | By User |  |  |  | By User | By User |  |  |  | By User | By User |  |  |  | None | Not Given | By User | By User | Not Given | F1012.001-DS1-1.JPG | F1012.001-DS2-1.JPG |  |  |  | No | None | YES
D2021.011a | D2021.011a | Cold or Hot Potable - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC A or B, PIPING FRAGILITY | Potable water. Costing based upon 1000 ft segments. | Normal | SDC A or B | Each | Each | Peak Floor Acceleration | g | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 700 | LF 1000 | NO | NO | Minor leakage at flange connections - 1 leak per 1000 feet of pipe. | Pipe Break - 1 break per 1000 feet of pipe. |  |  |  | 1 | 1 |  |  |  | 1.5 | 2.6 |  |  |  | Not Specified | Not Specified |  |  |  | Not Specified | Not Specified |  |  |  | 0.4 | 0.4 |  |  |  | NO | NO | Not Rated | Not Rated | Not Rated | Not Rated | Retighten flange bolts at leaking joints. One joint per 1000 LF. | Replace 20 foot sections of pipe where breaks occur. One repair per 1000 LF. |  |  |  | NO | NO |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | NO |  |  |  | 0% | 0% |  |  |  | 0 | 0 |  |  |  | Consequence is for piping only. Enter floor wetting consequence seperately. Cost includes allowance for MEP relocation to perform work. | Not Given | By User | By User | Not Given | none | none |  |  |  | Yes | 2016-10-26 - Corrected consequence descriptions. | YES
D2021.011b | D2021.011b | Cold or Hot Potable - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC A or B, BRACING FRAGILITY | Potable water. Costing based upon 1000 ft segments. | Normal | SDC A or B | Each | Each | Peak Floor Acceleration | g | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 701 | LF 1000 | NO | NO | Lateral Brace Failure - 1 failure per 1000 feet of pipe. | Vertical Brace Failure - 1 failure per 1000 feet of pipe. |  |  |  | 1 | 1 |  |  |  | 1.5 | 2.6 |  |  |  | Not Specified | Not Specified |  |  |  | Not Specified | Not Specified |  |  |  | 0.4 | 0.4 |  |  |  | NO | NO | Not Rated | Not Rated | Not Rated | Not Rated | Retighten flange bolts at leaking joints. One joint per 1000 LF. | Replace 20 foot sections of pipe where breaks occur. One repair per 1000 LF. |  |  |  | NO | NO |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0% | 0% | 0% | [6 empty] | 0% | 0% | 0% | 0% | [6 empty] | NO | NO |  |  |  | 0% | 0% |  |  |  | 0 | 0 |  |  |  | Consequence is for piping only. Enter floor wetting consequence seperately. Cost includes allowance for MEP relocation to perform work. | Not Given | By User | By User | Not Given | none | none |  |  |  | Yes | 2016-10-26 - Corrected consequence descriptions. | YES
D2021.012a | D2021.012a | Cold or Hot Potable - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC C, PIPING FRAGILITY | Potable water. Costing based upon 1000 ft segments. | Normal | SDC C | Each | Each | Peak Floor Acceleration | g | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 702 | LF 1000 | NO | NO | Minor leakage at flange connections - 1 leak per 1000 feet of pipe. | Pipe Break - 1 break per 1000 feet of pipe. |  |  |  | 1 | 1 |  |  |  | 1.5 | 2.6 |  |  |  | Not Specified | Not Specified |  |  |  | Not Specified | Not Specified |  |  |  | 0.4 | 0.4 |  |  |  | NO | NO | Not Rated | Not Rated | Not Rated | Not Rated | Replace failed lateral braces. One repair per 1000 LF. | Replace failed vertical braces. One repair per 1000 LF. |  |  |  | NO | NO |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | NO |  |  |  | 0% | 0% |  |  |  | 0 | 0 |  |  |  | Consequence is for piping only. Enter floor wetting consequence seperately. Cost includes allowance for MEP relocation to perform work. | Not Given | By User | By User | Not Given | none | none |  |  |  | Yes | 2016-10-26 - Corrected consequence descriptions. | YES
D2021.012b | D2021.012b | Cold or Hot Potable - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC C, BRACING FRAGILITY | Potable water. Costing based upon 1000 ft segments. | Normal | SDC C | Each | Each | Peak Floor Acceleration | g | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 703 | LF 1000 | NO | NO | Lateral Brace Failure - 1 failure per 1000 feet of pipe. | Vertical Brace Failure - 1 failure per 1000 feet of pipe. |  |  |  | 1 | 1 |  |  |  | 1.5 | 2.6 |  |  |  | Not Specified | Not Specified |  |  |  | Not Specified | Not Specified |  |  |  | 0.4 | 0.4 |  |  |  | NO | NO | Not Rated | Not Rated | Not Rated | Not Rated | Retighten flange bolts at leaking joints. One joint per 1000 LF. | Replace 20 foot sections of pipe where breaks occur. One repair per 1000 LF.. |  |  |  | NO | NO |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | NO |  |  |  | 0% | 0% |  |  |  | 0 | 0 |  |  |  | Consequence is for piping only. Enter floor wetting consequence seperately. Cost includes allowance for MEP relocation to perform work. | Not Given | By User | By User | Not Given | none | none |  |  |  | Yes | 2016-10-26 - Corrected consequence descriptions. | YES
D2021.013a | D2021.013a | Cold or Hot Potable - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC D, E, or F, PIPING FRAGILITY | Potable water. Costing based upon 1000 ft segments. | Normal | SDC D, E or F (high seismic design) | Each | Each | Peak Floor Acceleration | g | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 704 | LF 1000 | NO | NO | Minor leakage at flange connections - 1 leak per 1000 feet of pipe. | Pipe Break - 1 break per 1000 feet of pipe. |  |  |  | 1 | 1 |  |  |  | 2.25 | 4.1 |  |  |  | Not Specified | Not Specified |  |  |  | Not Specified | Not Specified |  |  |  | 0.4 | 0.4 |  |  |  | NO | NO | Not Rated | Not Rated | Not Rated | Not Rated | Replace failed lateral braces. One repair per 1000 LF. | Replace failed vertical braces. One repair per 1000 LF. |  |  |  | NO | NO |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | NO |  |  |  | 0% | 0% |  |  |  | 0 | 0 |  |  |  | Consequence is for piping only. Enter floor wetting consequence seperately. Cost includes allowance for MEP relocation to perform work. | Not Given | By User | By User | Not Given | none | none |  |  |  | Yes | 2016-10-26 - Corrected consequence descriptions. | YES
D2021.013b | D2021.013b | Cold or Hot Potable - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC D, E, or F, BRACING FRAGILITY | Potable water. Costing based upon 1000 ft segments. | Normal | SDC D, E or F (high seismic design) | Each | Each | Peak Floor Acceleration | g | 1 | DS1 |  |  |  |  | Sequential |  |  |  |  | Seq(DS1) | 705 | LF 1000 | NO | NO | Lateral Brace Failure - 1 failure per 1000 feet of pipe. |  |  |  |  | 1 |  |  |  |  | 1.5 |  |  |  |  | Not Specified |  |  |  |  | Not Specified |  |  |  |  | 0.4 |  |  |  |  | NO | NO | Not Rated | Not Rated | Not Rated | Not Rated | Retighten leaking joints. One joint per 1000 LF. | Replace 20 ft section of pipe at leaking joints. One repair per 1000 LF. |  |  |  | NO |  |  |  |  | NO |  |  |  |  | Not Applicable |  |  |  |  | 0% | 0 | [8 empty] | 0% | 0 | [8 empty] | NO |  |  |  |  | 0% |  |  |  |  | 0 |  |  |  |  | Consequence is for piping only. Enter floor wetting consequence seperately. Cost includes allowance for MEP relocation to perform work. | Not Given | By User | By User | Not Given | none |  |  |  |  | Yes | 2016-10-26 - Corrected consequence descriptions. | YES
D2021.014a | D2021.014a | Cold or Hot Potable - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC D, E, or F (OSHPD or sim), PIPING FRAGILITY | Potable water. Costing based upon 1000 ft segments. | Special Regulation (e.g. OSHPD) for piping installations | SDC D, E or F (high seismic design) | Each | Each | Peak Floor Acceleration | g | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 706 | LF 1000 | NO | NO | Minor leakage at flange connections - 1 leak per 1000 feet of pipe. | Pipe Break - 1 break per 1000 feet of pipe. |  |  |  | 1 | 1 |  |  |  | 2.25 | 4.1 |  |  |  | Not Specified | Not Specified |  |  |  | Not Specified | Not Specified |  |  |  | 0.4 | 0.4 |  |  |  | NO | NO | Not Rated | Not Rated | Not Rated | Not Rated | Replace failed supports. One repair per 1000 LF. | Replace failed supports. One repair per 1000 LF. |  |  |  | NO | NO |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | NO |  |  |  | 0% | 0% |  |  |  | 0 | 0 |  |  |  | Consequence is for piping only. Enter floor wetting consequence seperately. Cost includes allowance for MEP relocation to perform work. | Not Given | By User | By User | Not Given | none | none |  |  |  | Yes | 2016-10-26 - Corrected consequence descriptions. | YES
D2021.014b | D2021.014b | Cold or Hot Potable - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC D, E, or F (OSHPD or sim), BRACING FRAGILITY | Potable water. Costing based upon 1000 ft segments. | Special Regulation (e.g. OSHPD) for piping installations | SDC D, E or F (high seismic design) | Each | Each | Peak Floor Acceleration | g | 1 | DS1 |  |  |  |  | Sequential |  |  |  |  | Seq(DS1) | 707 | LF 1000 | NO | NO | Lateral Brace Failure - 1 failure per 1000 feet of pipe. |  |  |  |  | 1 |  |  |  |  | 1.5 |  |  |  |  | Not Specified |  |  |  |  | Not Specified |  |  |  |  | 0.4 |  |  |  |  | NO | NO | Not Rated | Not Rated | Not Rated | Not Rated | Retighten leaking joints. One joint per 1000 LF. | Replace 20 ft section of pipe at leaking joints. One repair per 1000 LF. |  |  |  | NO |  |  |  |  | NO |  |  |  |  | Not Applicable |  |  |  |  | 0% | 0 | [8 empty] | 0% | 0 | [8 empty] | NO |  |  |  |  | 0% |  |  |  |  | 0 |  |  |  |  | Consequence is for piping only. Enter floor wetting consequence seperately. Cost includes allowance for MEP relocation to perform work. | Not Given | By User | By User | Not Given | none |  |  |  |  | Yes | 2016-10-26 - Corrected consequence descriptions. | YES
D2021.021a | D2021.021a | Cold or Hot Potable Water Piping (dia > 2.5 inches), SDC A or B, PIPING FRAGILITY | Potable water. Costing based upon 1000 ft segments. | Normal | SDC A or B | Each | Each | Peak Floor Acceleration | g | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 708 | LF 1000 | NO | NO | Minor leakage at flange connections - 1 leak per 1000 feet of pipe. | Pipe Break - 1 break per 1000 feet of pipe. |  |  |  | 1 | 1 |  |  |  | 1.5 | 2.6 |  |  |  | Not Specified | Not Specified |  |  |  | Not Specified | Not Specified |  |  |  | 0.4 | 0.4 |  |  |  | NO | NO | Not Rated | Not Rated | Not Rated | Not Rated | Replace failed supports. One repair per 1000 LF. | Replace failed 60 ft pipe sections including supports. One repair per 1000 LF. |  |  |  | NO | NO |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | NO |  |  |  | 0% | 0% |  |  |  | 0 | 0 |  |  |  | Consequence is for piping only. Enter floor wetting consequence seperately. Cost includes allowance for MEP relocation to perform work. | Not Given | By User | By User | Not Given | none | none |  |  |  | Yes | 2016-10-26 - Corrected consequence descriptions. | YES
D2021.022a | D2021.022a | Cold or Hot Potable Water Piping (dia > 2.5 inches), SDC C, PIPING FRAGILITY | Potable water. Costing based upon 1000 ft segments. | Normal | SDC C | Each | Each | Peak Floor Acceleration | g | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 709 | LF 1000 | NO | NO | Minor leakage at flange connections - 1 leak per 1000 feet of pipe. | Pipe Break - 1 break per 1000 feet of pipe. |  |  |  | 1 | 1 |  |  |  | 1.5 | 2.6 |  |  |  | 0.4 | 0.4 |  |  |  | Not Specified | Not Specified |  |  |  | 0.4 | 0.4 |  |  |  | NO | NO | Not Rated | Not Rated | Not Rated | Not Rated | Retighten leaking joints. One joint per 1000 LF. | Replace 20 ft section of pipe at leaking joints. One repair per 1000 LF. |  |  |  | NO | NO |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | NO |  |  |  | 0% | 0% |  |  |  | 0 | 0 |  |  |  | Consequence is for piping only. Enter floor wetting consequence seperately. Cost includes allowance for MEP relocation to perform work. | Not Given | By User | By User | Not Given | none | none |  |  |  | Yes | 2016-10-26 - Corrected consequence descriptions. | YES
D2021.023a | D2021.023a | Cold or Hot Potable Water Piping (dia > 2.5 inches), SDC D,E,F, PIPING FRAGILITY | Potable water. Costing based upon 1000 ft segments. | Normal | SDC D, E or F (high seismic design) | Each | Each | Peak Floor Acceleration | g | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 710 | LF 1000 | NO | NO | Minor leakage at flange connections - 1 leak per 1000 feet of pipe. | Pipe Break - 1 break per 1000 feet of pipe. |  |  |  | 1 | 1 |  |  |  | 2.25 | 4.1 |  |  |  | 0.4 | 0.4 |  |  |  | Not Specified | Not Specified |  |  |  | 0.4 | 0.4 |  |  |  | NO | NO | Not Rated | Not Rated | Not Rated | Not Rated | Replace failed supports. One repair per 1000 LF. |  |  |  |  | NO | NO |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | NO |  |  |  | 0% | 0% |  |  |  | 0 | 0 |  |  |  | Consequence is for piping only. Enter floor wetting consequence seperately. Cost includes allowance for MEP relocation to perform work. | Not Given | By User | By User | Not Given | none | none |  |  |  | Yes | 2016-10-26 - Corrected consequence descriptions. | YES
D2021.023b | D2021.023b | Cold or Hot Potable Water Piping (dia > 2.5 inches), SDC D,E,F, BRACING FRAGILITY | Potable water. Costing based upon 1000 ft segments. | Normal | SDC D, E or F (high seismic design) | Each | Each | Peak Floor Acceleration | g | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 711 | LF 1000 | NO | NO | Lateral Brace Failure - 1 failure per 1000 feet of pipe. | Vertical Brace Failure - 1 failure per 1000 feet of pipe. |  |  |  | 1 | 1 |  |  |  | 1.5 | 2.25 |  |  |  | 0.4 | 0.4 |  |  |  | Not Specified | Not Specified |  |  |  | 0.4 | 0.4 |  |  |  | NO | NO | Not Rated | Not Rated | Not Rated | Not Rated | Retighten leaking joints. One joint per 1000 LF. | Replace 20 ft section of pipe at leaking joints. One repair per 1000 LF. |  |  |  | NO | NO |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | NO |  |  |  | 0% | 0% |  |  |  | 0 | 0 |  |  |  | Consequence is for piping only. Enter floor wetting consequence seperately. Cost includes allowance for MEP relocation to perform work. | Not Given | By User | By User | Not Given | none | none |  |  |  | Yes | 2016-10-26 - Corrected consequence descriptions. | YES
D2021.024a | D2021.024a | Cold or Hot Potable Water Piping (dia > 2.5 inches), SDC D,E,F (OSPHD or sim), PIPING FRAGILITY | Potable water. Costing based upon 1000 ft segments. | Special Regulation (e.g. OSHPD) for piping installations | SDC D, E or F (high seismic design) | Each | Each | Peak Floor Acceleration | g | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 712 | LF 1000 | NO | NO | Minor leakage at flange connections - 1 leak per 1000 feet of pipe. | Pipe Break - 1 break per 1000 feet of pipe. |  |  |  | 1 | 1 |  |  |  | 2.25 | 4.1 |  |  |  | 0.4 | 0.4 |  |  |  | Not Specified | Not Specified |  |  |  | 0.4 | 0.4 |  |  |  | NO | NO | Not Rated | Not Rated | Not Rated | Not Rated | Replace failed supports. One repair per 1000 LF. |  |  |  |  | NO | NO |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | NO |  |  |  | 0% | 0% |  |  |  | 0 | 0 |  |  |  | Consequence is for piping only. Enter floor wetting consequence seperately. Cost includes allowance for MEP relocation to perform work. | Not Given | By User | By User | Not Given | none | none |  |  |  | Yes | 2016-10-26 - Corrected consequence descriptions. | YES
D2021.024b | D2021.024b | Cold or Hot Potable Water Piping (dia > 2.5 inches), SDC D,E,F (OSPHD or sim), BRACING FRAGILITY | Potable water. Costing based upon 1000 ft segments. | Special Regulation (e.g. OSHPD) for piping installations | SDC D, E or F (high seismic design) | Each | Each | Peak Floor Acceleration | g | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 713 | LF 1000 | NO | NO | Lateral Brace Failure - 1 failure per 1000 feet of pipe. | Vertical Brace Failure - 1 failure per 1000 feet of pipe. |  |  |  | 1 | 1 |  |  |  | 1.5 | 2.25 |  |  |  | 0.4 | 0.4 |  |  |  | Not Specified | Not Specified |  |  |  | 0.4 | 0.4 |  |  |  | NO | NO | Not Rated | Not Rated | Not Rated | Not Rated | Retighten flange bolts at leaking joints. One joint per 1000 LF. | Replace 20 foot sections of pipe where breaks occur. One repair per 1000 LF. |  |  |  | NO | NO |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | NO |  |  |  | 0% | 0% |  |  |  | 0 | 0 |  |  |  | Consequence is for piping only. Enter floor wetting consequence seperately. Cost includes allowance for MEP relocation to perform work. | Not Given | By User | By User | Not Given | none | none |  |  |  | Yes | 2016-10-26 - Corrected consequence descriptions. | YES
D2022.011a | D2022.011a | Heating hot Water Piping - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC A or B, PIPING FRAGILITY | Heating water. Costing based upon 1000 ft segments of pipe, pipe 2.5 inches in diameter or less | Normal | SDC A or B (no seismic design) | Each | Each | Peak Floor Acceleration | g | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 714 | LF 1000 | NO | NO | Small Leakage at joints - 1 leak per 1000 feet of pipe. | Large Leakage w/ major repair - 1 leak per 1000 feet of pipe. |  |  |  | 1 | 1 |  |  |  | 0.55 | 1.1 |  |  |  | 0.4 | 0.4 |  |  |  | Not Specified | Not Specified |  |  |  | By User | By User |  |  |  | NO | NO | Not Rated | Not Rated | Not Rated | Not Rated | Retighten flange bolts at leaking joints. One repair per 1000 LF. | Replace 20 foot sections of pipe where breaks occur. One repair per 1000 LF. |  |  |  | NO | NO |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | NO |  |  |  | 0% | 0% |  |  |  | 0 | 0 |  |  |  | Consequence is for piping only. Enter floor wetting consequence seperately. Cost includes allowance for MEP relocation to perform work. | None | By User | By User | Not Given | none | none |  |  |  | Yes | 2016-10-26 - Corrected consequence descriptions. | YES
D2022.011b | D2022.011b | Heating hot Water Piping - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC A or B, BRACING FRAGILITY | Heating water. Costing based upon 1000 ft segments of pipe, pipe 2.5 inches in diameter or less | Normal | SDC A or B (no seismic design) | Each | Each | Peak Floor Acceleration | g | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 715 | LF 1000 | NO | NO | Isolated support failure w/o leakage - 0.5 supports fail per 1000 feet of pipe (assuming supports every 20 feet). | Multiple supports failure and 60 feet of pipe fail per 1000 feet of pipe (assuming supports every 20 feet). |  |  |  | 1 | 1 |  |  |  | 1.2 | 2.4 |  |  |  | 0.5 | 0.5 |  |  |  | Not Specified | Not Specified |  |  |  | By User | By User |  |  |  | NO | NO | Not Rated | Not Rated | Not Rated | Not Rated | Retighten flange bolts at leaking joints. One repair per 1000 LF. | Replace 20 foot sections of pipe where breaks occur. One repair per 1000 LF. |  |  |  | NO | NO |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | NO |  |  |  | 0% | 0% |  |  |  | 0 | 0 |  |  |  | Consequence is for piping only. Enter floor wetting consequence seperately. Cost includes allowance for MEP relocation to perform work. | None | By User | By User | Not Given | none | none |  |  |  | Yes | 2016-10-26 - Corrected consequence descriptions. | YES
D2022.012a | D2022.012a | Heating hot Water Piping - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC C, PIPING FRAGILITY | Heating water. Costing based upon 1000 ft segments of pipe, pipe 2.5 inches in diameter or less | Normal | SDC C (low seismic design) | Each | Each | Peak Floor Acceleration | g | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 716 | LF 1000 | NO | NO | Small Leakage at joints - 1 leak per 1000 feet of pipe. | Large Leakage w/ major repair - 1 leak per 1000 feet of pipe. |  |  |  | 1 | 1 |  |  |  | 0.55 | 1.1 |  |  |  | 0.4 | 0.4 |  |  |  | Not Specified | Not Specified |  |  |  | By User | By User |  |  |  | NO | NO | Not Rated | Not Rated | Not Rated | Not Rated | Replace failed lateral braces. One repair per 1000 LF. | Replace failed vertical braces. One repair per 1000 LF. |  |  |  | NO | NO |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | NO |  |  |  | 0% | 0% |  |  |  | 0 | 0 |  |  |  | Consequence is for piping only. Enter floor wetting consequence seperately. Cost includes allowance for MEP relocation to perform work. | None | By User | By User | Not Given | none | none |  |  |  | Yes | 2016-10-26 - Corrected consequence descriptions. | YES
D2022.012b | D2022.012b | Heating hot Water Piping - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC C, BRACING FRAGILITY | Heating water. Costing based upon 1000 ft segments of pipe, pipe 2.5 inches in diameter or less | Normal | SDC C (low seismic design) | Each | Each | Peak Floor Acceleration | g | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 717 | LF 1000 | NO | NO | Isolated support failure w/o leakage - 0.5 supports fail per 1000 feet of pipe (assuming supports every 20 feet). | Multiple supports failure and 60 feet of pipe fail per 1000 feet of pipe (assuming supports every 20 feet). |  |  |  | 1 | 1 |  |  |  | 1.2 | 2.4 |  |  |  | 0.5 | 0.5 |  |  |  | Not Specified | Not Specified |  |  |  | By User | By User |  |  |  | NO | NO | Not Rated | Not Rated | Not Rated | Not Rated | Retighten flange bolts at leaking joints. One repair per 1000 LF. | Replace 20 foot sections of pipe where breaks occur. One repair per 1000 LF. |  |  |  | NO | NO |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | NO |  |  |  | 0% | 0% |  |  |  | 0 | 0 |  |  |  | Consequence is for piping only. Enter floor wetting consequence seperately. Cost includes allowance for MEP relocation to perform work. | None | By User | By User | Not Given | none | none |  |  |  | Yes | 2016-10-26 - Corrected consequence descriptions. | YES
D2022.013a | D2022.013a | Heating hot Water Piping - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC D, E, or F, PIPING FRAGILITY | Heating water. Costing based upon 1000 ft segments of pipe, pipe 2.5 inches in diameter or less | Normal | SDC D, E, F (high seismic design) | Each | Each | Peak Floor Acceleration | g | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 718 | LF 1000 | NO | NO | Small Leakage at joints - 1 leak per 1000 feet of pipe. | Large Leakage w/ major repair - 1 leak per 1000 feet of pipe. |  |  |  | 1 | 1 |  |  |  | 0.55 | 1.1 |  |  |  | 0.4 | 0.4 |  |  |  | Not Specified | Not Specified |  |  |  | By User | By User |  |  |  | NO | NO | Not Rated | Not Rated | Not Rated | Not Rated | Replace failed lateral braces. One repair per 1000 LF. | Replace failed vertical braces. One repair per 1000 LF. |  |  |  | NO | NO |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | NO |  |  |  | 0% | 0% |  |  |  | 0 | 0 |  |  |  | Consequence is for piping only. Enter floor wetting consequence seperately. Cost includes allowance for MEP relocation to perform work. | None | By User | By User | Not Given | none | none |  |  |  | Yes | 2016-10-26 - Corrected consequence descriptions. | YES
D2022.013b | D2022.013b | Heating hot Water Piping - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC D, E, or F, BRACING FRAGILITY | Heating water. Costing based upon 1000 ft segments of pipe, pipe 2.5 inches in diameter or less | Normal | SDC D, E, F (high seismic design) | Each | Each | Peak Floor Acceleration | g | 1 | DS1 |  |  |  |  | Sequential |  |  |  |  | Seq(DS1) | 719 | LF 1000 | NO | NO | Isolated support failure w/o leakage - 0.5 supports fail per 1000 feet of pipe (assuming supports every 20 feet). |  |  |  |  | 1 |  |  |  |  | 2.25 |  |  |  |  | 0.4 |  |  |  |  | Not Specified |  |  |  |  | By User |  |  |  |  | NO | NO | Not Rated | Not Rated | Not Rated | Not Rated | Replace failed supports. One repair per 1000 LF. | Replace failed 60 ft pipe sections including supports. One repair per 1000 LF. |  |  |  | NO |  |  |  |  | NO |  |  |  |  | Not Applicable |  |  |  |  | 0% | 0 | [8 empty] | 0% | 0 | [8 empty] | NO |  |  |  |  | 0% |  |  |  |  | 0 |  |  |  |  | Consequence is for piping only. Enter floor wetting consequence seperately. Cost includes allowance for MEP relocation to perform work. | None | By User | By User | Not Given | none |  |  |  |  | Yes | 2016-10-26 - Corrected consequence descriptions. | YES
D2022.014a | D2022.014a | Heating hot Water Piping - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC D, E, or F (OSHPD or sim), PIPING FRAGILITY | Heating water. Costing based upon 1000 ft segments of pipe, pipe 2.5 inches in diameter or less | Special Regulations (e.g. OSHPD) for Piping Installations | SDC D, E, F (high seismic design) | Each | Each | Peak Floor Acceleration | g | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 720 | LF 1000 | NO | NO | Small Leakage at joints - 1 leak per 1000 feet of pipe. | Large Leakage w/ major repair - 1 leak per 1000 feet of pipe. |  |  |  | 1 | 1 |  |  |  | 0.55 | 1.1 |  |  |  | 0.4 | 0.4 |  |  |  | Not Specified | Not Specified |  |  |  | By User | By User |  |  |  | NO | NO | Not Rated | Not Rated | Not Rated | Not Rated | Replace failed supports. One repair per 1000 LF. | Replace failed 60 ft pipe sections including supports. One repair per 1000 LF. |  |  |  | NO | NO |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | NO |  |  |  | 0% | 0% |  |  |  | 0 | 0 |  |  |  | Consequence is for piping only. Enter floor wetting consequence seperately. Cost includes allowance for MEP relocation to perform work. | None | By User | By User | Not Given | none | none |  |  |  | Yes | 2016-10-26 - Corrected consequence descriptions. | YES
D2022.014b | D2022.014b | Heating hot Water Piping - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC D, E, or F (OSHPD or sim), BRACING FRAGILITY | Heating water. Costing based upon 1000 ft segments of pipe, pipe 2.5 inches in diameter or less | Special Regulations (e.g. OSHPD) for Piping Installations | SDC D, E, F (high seismic design) | Each | Each | Peak Floor Acceleration | g | 1 | DS1 |  |  |  |  | Sequential |  |  |  |  | Seq(DS1) | 721 | LF 1000 | NO | NO | Isolated support failure w/o leakage - 0.5 supports fail per 1000 feet of pipe (assuming supports every 20 feet). |  |  |  |  | 1 |  |  |  |  | 3 |  |  |  |  | 0.4 |  |  |  |  | Not Specified |  |  |  |  | By User |  |  |  |  | NO | NO | Not Rated | Not Rated | Not Rated | Not Rated | Replace failed supports. One repair per 1000 LF. |  |  |  |  | NO |  |  |  |  | NO |  |  |  |  | Not Applicable |  |  |  |  | 0% | 0 | [8 empty] | 0% | 0 | [8 empty] | NO |  |  |  |  | 0% |  |  |  |  | 0 |  |  |  |  | Consequence is for piping only. Enter floor wetting consequence seperately. Cost includes allowance for MEP relocation to perform work. | None | By User | By User | Not Given | none |  |  |  |  | Yes | 2016-10-26 - Corrected consequence descriptions. | YES
D2022.021a | D2022.021a | Heating hot Water Piping - Large Diameter Welded Steel - (greater than 2.5 inches in diameter), SDC A or B, PIPING FRAGILITY | Heating water. Costing based upon 1000 ft segments of pipe, pipe 2.5 inches in diameter or less | Normal | SDC A or B (no seismic design) | Each | Each | Peak Floor Acceleration | g | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 722 | LF 1000 | NO | NO | Minor leakage at flange connections - 1 leak per 1000 feet of pipe. | Pipe Break - 1 break per 1000 feet of pipe. |  |  |  | 1 | 1 |  |  |  | 1.5 | 2.6 |  |  |  | 0.4 | 0.4 |  |  |  | Not Specified | Not Specified |  |  |  | By User | By User |  |  |  | NO | NO | Not Rated | Not Rated | Not Rated | Not Rated | Replace failed supports. One repair per 1000 LF. |  |  |  |  | NO | NO |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | NO |  |  |  | 0% | 0% |  |  |  | 0 | 0 |  |  |  | Consequence is for piping only. Enter floor wetting consequence seperately. Cost includes allowance for MEP relocation to perform work. | None | By User | By User | Not Given | none | none |  |  |  | Yes | 2016-10-26 - Corrected consequence descriptions. | YES
D2022.022a | D2022.022a | Heating hot Water Piping - Large Diameter Welded Steel - (greater than 2.5 inches in diameter), SDC C, PIPING FRAGILITY | Heating water. Costing based upon 1000 ft segments of pipe, pipe 2.5 inches in diameter or less | Normal | SDC C (low seismic design) | Each | Each | Peak Floor Acceleration | g | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 723 | LF 1000 | NO | NO | Minor leakage at flange connections - 1 leak per 1000 feet of pipe. | Pipe Break - 1 break per 1000 feet of pipe. |  |  |  | 1 | 1 |  |  |  | 1.5 | 2.6 |  |  |  | 0.4 | 0.4 |  |  |  | Not Specified | Not Specified |  |  |  | By User | By User |  |  |  | NO | NO | Not Rated | Not Rated | Not Rated | Not Rated | Replace failed supports. One repair per 1000 LF. |  |  |  |  | NO | NO |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0 | 0 | [6 empty] | NO | NO |  |  |  | 0% | 0 |  |  |  | 0 | 0 |  |  |  | Consequence is for piping only. Enter floor wetting consequence seperately. Cost includes allowance for MEP relocation to perform work. | None | By User | By User | Not Given | none | none |  |  |  | Yes | 2016-10-26 - Corrected consequence descriptions. | YES
D2022.023a | D2022.023a | Heating hot Water Piping - Large Diameter Welded Steel - (greater than 2.5 inches in diameter), SDC D, E, or F, PIPING FRAGILITY | Heating water. Costing based upon 1000 ft segments of pipe, pipe 2.5 inches in diameter or less | Normal | SDC D, E, F (high seismic design | Each | Each | Peak Floor Acceleration | g | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 724 | LF 1000 | NO | NO | Minor leakage at flange connections - 1 leak per 1000 feet of pipe. | Pipe Break - 1 break per 1000 feet of pipe. |  |  |  | 1 | 1 |  |  |  | 2.25 | 4.1 |  |  |  | 0.4 | 0.4 |  |  |  | Not Specified | Not Specified |  |  |  | By User | By User |  |  |  | NO | NO | Not Rated | Not Rated | Not Rated | Not Rated | Replace failed supports. One repair per 1000 LF. | Replace failed 60 ft pipe sections including supports. One repair per 1000 LF. |  |  |  | NO | NO |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | NO |  |  |  | 0% | 0% |  |  |  | 0 | 0 |  |  |  | Consequence is for piping only. Enter floor wetting consequence seperately. Cost includes allowance for MEP relocation to perform work. | None | By User | By User | Not Given | none | none |  |  |  | Yes | 2016-10-26 - Corrected consequence descriptions. | YES
D2022.023b | D2022.023b | Heating hot Water Piping - Large Diameter Welded Steel - (greater than 2.5 inches in diameter), SDC D, E, or F, BRACING FRAGILITY | Heating water. Costing based upon 1000 ft segments of pipe, pipe 2.5 inches in diameter or less | Normal | SDC D, E, F (high seismic design | Each | Each | Peak Floor Acceleration | g | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 725 | LF 1000 | NO | NO | Lateral Brace Failure - 1 failure per 1000 foot of pipe. | Vertical Brace Failure - 1 failure per 1000 feet of pipe. |  |  |  | 1 | 1 |  |  |  | 1.5 | 2.25 |  |  |  | 0.4 | 0.4 |  |  |  | Not Specified | Not Specified |  |  |  | By User | By User |  |  |  | NO | NO | Not Rated | Not Rated | Not Rated | Not Rated | Replace failed supports. One repair per 1000 LF. |  |  |  |  | NO | NO |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | NO |  |  |  | 0% | 0% |  |  |  | 0 | 0 |  |  |  | Consequence is for piping only. Enter floor wetting consequence seperately. Cost includes allowance for MEP relocation to perform work. | None | By User | By User | Not Given | none | none |  |  |  | Yes | 2016-10-26 - Corrected consequence descriptions. | YES
D2022.024a | D2022.024a | Heating hot Water Piping - Large Diameter Welded Steel - (greater than 2.5 inches in diameter), SDC D, E, or F (OSHPD or sim), PIPING FRAGILITY | Heating water. Costing based upon 1000 ft segments of pipe, pipe 2.5 inches in diameter or less | Special Regulation (e.g. OSHPD) for Piping Installations | SDC D, E, F (high seismic design) | Each | Each | Peak Floor Acceleration | g | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 726 | LF 1000 | NO | NO | Minor leakage at flange connections - 1 leak per 1000 feet of pipe. | Pipe Break - 1 break per 1000 feet of pipe. |  |  |  | 1 | 1 |  |  |  | 2.25 | 4.1 |  |  |  | 0.4 | 0.4 |  |  |  | Not Specified | Not Specified |  |  |  | By User | By User |  |  |  | NO | NO | Not Rated | Not Rated | Not Rated | Not Rated | Replace failed supports. One repair per 1000 LF. | Replace failed 60 ft pipe sections including supports. One repair per 1000 LF. |  |  |  | NO | NO |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | NO |  |  |  | 0% | 0% |  |  |  | 0 | 0 |  |  |  | Consequence is for piping only. Enter floor wetting consequence seperately. Cost includes allowance for MEP relocation to perform work. | None | By User | By User | Not Given | none | none |  |  |  | Yes | 2016-10-26 - Corrected consequence descriptions. | YES
D2022.024b | D2022.024b | Heating hot Water Piping - Large Diameter Welded Steel - (greater than 2.5 inches in diameter), SDC D, E, or F (OSHPD or sim), BRACING FRAGILITY | Heating water. Costing based upon 1000 ft segments of pipe, pipe 2.5 inches in diameter or less | Special Regulation (e.g. OSHPD) for Piping Installations | SDC D, E, F (high seismic design) | Each | Each | Peak Floor Acceleration | g | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 727 | LF 1000 | NO | NO | Lateral Brace Failure - 1 failure per 1000 foot of pipe. | Vertical Brace Failure - 1 failure per 1000 feet of pipe. |  |  |  | 1 | 1 |  |  |  | 1.5 | 2.25 |  |  |  | 0.4 | 0.4 |  |  |  | Not Specified | Not Specified |  |  |  | By User | By User |  |  |  | NO | NO | Not Rated | Not Rated | Not Rated | Not Rated | Replace failed supports. One repair per 1000 LF. |  |  |  |  | NO | NO |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | NO |  |  |  | 0% | 0% |  |  |  | 0 | 0 |  |  |  | Consequence is for piping only. Enter floor wetting consequence seperately. Cost includes allowance for MEP relocation to perform work. | None | By User | By User | Not Given | none | none |  |  |  | Yes | 2016-10-26 - Corrected consequence descriptions. | YES
D2031.011b | D2031.011b | Sanitary Waste Piping - Cast Iron w/flexible couplings, SDC A,B, BRACING FRAGILITY | Costing based upon 1000 ft segments of pipe | Normal | SDC A or B | Each | Each | Peak Floor Acceleration | g | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 728 | LF 1000 | NO | NO | Isolated support failure w/o leakage - 0.5 supports fail per 1000 feet of pipe (assuming supports every 20 feet). | Multiple supports failure and 60 feet of pipe fail per 1000 feet of pipe (assuming supports every 20 feet). |  |  |  | 1 | 1 |  |  |  | 1.2 | 2.4 |  |  |  | 0.5 | 0.5 |  |  |  | Not Specified | Not Specified |  |  |  | By User | By User |  |  |  | NO | NO | Not Rated | Not Rated | Not Rated | Not Rated | Replace failed supports - 0.5 per 1000 LF. | Replace failed supports and 60 ft pipe per 1000 LF. |  |  |  | NO | NO |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | NO |  |  |  | 0% | 0% |  |  |  | 0 | 0 |  |  |  | Consequence is for piping only. Enter floor wetting consequence seperately. Cost includes allowance for MEP relocation to perform work. | None | By User | By User | Not Given | none | none |  |  |  | Yes | 2016-10-26 - Corrected consequence descriptions. | YES
D2031.012b | D2031.012b | Sanitary Waste Piping - Cast Iron w/flexible couplings, SDC C, BRACING FRAGILITY | Costing based upon 1000 ft segments of pipe | Normal | SDC C | Each | Each | Peak Floor Acceleration | g | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 729 | LF 1000 | NO | NO | Isolated support failure w/o leakage - 0.5 supports fail per 1000 feet of pipe (assuming supports every 20 feet). | Multiple supports failure and 60 feet of pipe fail per 1000 feet of pipe (assuming supports every 20 feet). |  |  |  | 1 | 1 |  |  |  | 1.2 | 2.4 |  |  |  | 0.5 | 0.5 |  |  |  | Not Specified | Not Specified |  |  |  | By User | By User |  |  |  | NO | NO | Not Rated | Not Rated | Not Rated | Not Rated | Replace failed supports - 0.5 per 1000 LF. | Replace failed supports and 60 ft pipe per 1000 LF. |  |  |  | NO | NO |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | NO |  |  |  | 0% | 0% |  |  |  | 0 | 0 |  |  |  | Consequence is for piping only. Enter floor wetting consequence seperately. Cost includes allowance for MEP relocation to perform work. | None | By User | By User | Not Given | none | none |  |  |  | Yes | 2016-10-26 - Corrected consequence descriptions. | YES
D2031.013b | D2031.013b | Sanitary Waste Piping - Cast Iron w/flexible couplings, SDC D,E,F, BRACING FRAGILITY | Costing based upon 1000 ft segments of pipe | Normal | SDC D, E or F (high seismic design) | Each | Each | Peak Floor Acceleration | g | 1 | DS1 |  |  |  |  | Sequential |  |  |  |  | Seq(DS1) | 730 | LF 1000 | NO | NO | Isolated support failure w/o leakage - 0.5 supports fail per 1000 feet of pipe (assuming supports every 20 feet). |  |  |  |  | 1 |  |  |  |  | 2.25 |  |  |  |  | 0.4 |  |  |  |  | Not Specified |  |  |  |  | By User |  |  |  |  | NO | NO | Not Rated | Not Rated | Not Rated | Not Rated | Replace failed supports - 0.5 per 1000 LF. |  |  |  |  | NO |  |  |  |  | NO |  |  |  |  | Not Applicable |  |  |  |  | 0% | 0 | [8 empty] | 0% | 0 | [8 empty] | NO |  |  |  |  | 0% |  |  |  |  | 0 |  |  |  |  | Consequence is for piping only. Enter floor wetting consequence seperately. Cost includes allowance for MEP relocation to perform work. | None | By User | By User | Not Given | none |  |  |  |  | Yes | 2016-10-26 - Corrected consequence descriptions. | YES
D2031.014b | D2031.014b | Sanitary Waste Piping - Cast Iron w/flexible couplings, SDC D,E,F (OSHPD or sim), BRACING FRAGILITY | Costing based upon 1000 ft segments of pipe | Special Regulation (e.g. OSHPD) for piping installations | SDC D, E or F (high seismic design) | Each | Each | Peak Floor Acceleration | g | 1 | DS1 |  |  |  |  | Sequential |  |  |  |  | Seq(DS1) | 731 | LF 1000 | NO | NO | Isolated support failure w/o leakage - 0.5 supports fail per 1000 feet of pipe (assuming supports every 20 feet). |  |  |  |  | 1 |  |  |  |  | 3 |  |  |  |  | 0.4 |  |  |  |  | Not Specified |  |  |  |  | By User |  |  |  |  | NO | NO | Not Rated | Not Rated | Not Rated | Not Rated | Replace failed supports - 0.5 per 1000 LF. |  |  |  |  | NO |  |  |  |  | NO |  |  |  |  | Not Applicable |  |  |  |  | 0% | 0 | [8 empty] | 0% | 0 | [8 empty] | NO |  |  |  |  | 0% |  |  |  |  | 0 |  |  |  |  | Consequence is for piping only. Enter floor wetting consequence seperately. Cost includes allowance for MEP relocation to perform work. | None | By User | By User | Not Given | none |  |  |  |  | Yes | 2016-10-26 - Corrected consequence descriptions. | YES
D2031.021a | D2031.021a | Sanitary Waste Piping - Cast Iron w/bell and spigot couplings, SDC A,B, PIPING FRAGILITY | Costing based upon 1000 ft segments of pipe | Normal | SDC A or B | Each | Each | Peak Floor Acceleration | g | 1 | DS1 |  |  |  |  | Sequential |  |  |  |  | Seq(DS1) | 732 | LF 1000 | NO | NO | Joints break - 1 break per 1000 feet of pipe. |  |  |  |  | 1 |  |  |  |  | 2.25 |  |  |  |  | 0.4 |  |  |  |  | Not Specified |  |  |  |  | By User |  |  |  |  | NO | NO | Not Rated | Not Rated | Not Rated | Not Rated | Replace failed 20 ft pipe sections including supports - one per 1000 LF. |  |  |  |  | NO |  |  |  |  | NO |  |  |  |  | Not Applicable |  |  |  |  | 0% | 0 | [8 empty] | 0% | 0 | [8 empty] | NO |  |  |  |  | 0% |  |  |  |  | 0 |  |  |  |  | Consequence is for piping only. Enter floor wetting consequence seperately. Cost includes allowance for MEP relocation to perform work. | None | By User | By User | Not Given | none |  |  |  |  | Yes | 2016-10-26 - Corrected consequence descriptions. | YES
D2031.021b | D2031.021b | Sanitary Waste Piping - Cast Iron w/bell and spigot couplings, SDC A,B, BRACING FRAGILITY | Costing based upon 1000 ft segments of pipe | Normal | SDC A or B | Each | Each | Peak Floor Acceleration | g | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 733 | LF 1000 | NO | NO | Isolated support failure w/o leakage - 0.5 supports fail per 1000 feet of pipe (assuming supports every 20 feet). | Multiple supports failure and 60 feet of pipe fail per 1000 feet of pipe (assuming supports every 20 feet) |  |  |  | 1 | 1 |  |  |  | 1.2 | 2.4 |  |  |  | 0.5 | 0.5 |  |  |  | Not Specified | Not Specified |  |  |  | By User | By User |  |  |  | NO | NO | Not Rated | Not Rated | Not Rated | Not Rated | Replace failed supports - 0.5 per 1000 LF. | Replace failed supports and 60 ft pipe per 1000 LF. |  |  |  | NO | NO |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0 | 0 | [6 empty] | NO | NO |  |  |  | 0% | 0 |  |  |  | 0 | 0 |  |  |  | Consequence is for piping only. Enter floor wetting consequence seperately. Cost includes allowance for MEP relocation to perform work. | None | By User | By User | Not Given | none | none |  |  |  | Yes | 2016-10-26 - Corrected consequence descriptions. | YES
D2031.022a | D2031.022a | Sanitary Waste Piping - Cast Iron w/bell and spigot couplings, SDC C, PIPING FRAGILITY | Costing based upon 1000 ft segments of pipe | Normal | SDC C | Each | Each | Peak Floor Acceleration | g | 1 | DS1 |  |  |  |  | Sequential |  |  |  |  | Seq(DS1) | 734 | LF 1000 | NO | NO | Isolated support failure w/o leakage - 0.5 supports fail per 1000 feet of pipe (assuming supports every 20 feet). |  |  |  |  | 1 |  |  |  |  | 1.2 |  |  |  |  | 0.5 |  |  |  |  | Not Specified |  |  |  |  | By User |  |  |  |  | NO | NO | Not Rated | Not Rated | Not Rated | Not Rated | Replace failed 20 ft pipe sections including supports - one per 1000 LF. |  |  |  |  | NO |  |  |  |  | NO |  |  |  |  | Not Applicable |  |  |  |  | 0% | 0 | [8 empty] | 0% | 0 | [8 empty] | NO |  |  |  |  | 0% |  |  |  |  | 0 |  |  |  |  | Consequence is for piping only. Enter floor wetting consequence seperately. Cost includes allowance for MEP relocation to perform work. | None | By User | By User | Not Given | none |  |  |  |  | Yes | 2016-10-26 - Corrected consequence descriptions. | YES
D2031.022b | D2031.022b | Sanitary Waste Piping - Cast Iron w/bell and spigot couplings, SDC C, BRACING FRAGILITY | Costing based upon 1000 ft segments of pipe | Normal | SDC C | Each | Each | Peak Floor Acceleration | g | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 735 | LF 1000 | NO | NO | Isolated support failure w/o leakage - 0.5 supports fail per 1000 feet of pipe (assuming supports every 20 feet). | Multiple supports failure and 60 feet of pipe fail per 1000 feet of pipe (assuming supports every 20 feet) |  |  |  | 1 | 1 |  |  |  | 1.2 | 2.4 |  |  |  | 0.5 | 0.5 |  |  |  | Not Specified | Not Specified |  |  |  | By User | By User |  |  |  | NO | NO | Not Rated | Not Rated | Not Rated | Not Rated | Replace failed supports - 0.5 per 1000 LF. | Replace failed supports and 60 ft pipe per 1000 LF. |  |  |  | NO | NO |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | NO |  |  |  | 0% | 0% |  |  |  | 0 | 0 |  |  |  | Consequence is for piping only. Enter floor wetting consequence seperately. Cost includes allowance for MEP relocation to perform work. | None | By User | By User | Not Given | none | none |  |  |  | Yes | 2016-10-26 - Corrected consequence descriptions. | YES
D2031.023a | D2031.023a | Sanitary Waste Piping - Cast Iron w/bell and spigot couplings, SDC D,E,F, PIPING FRAGILITY | Costing based upon 1000 ft segments of pipe | Normal | SDC D, E or F (high seismic design) | Each | Each | Peak Floor Acceleration | g | 1 | DS1 |  |  |  |  | Sequential |  |  |  |  | Seq(DS1) | 736 | LF 1000 | NO | NO | Joints break - 1 break per 1000 feet of pipe. |  |  |  |  | 1 |  |  |  |  | 3 |  |  |  |  | 0.4 |  |  |  |  | Not Specified |  |  |  |  | By User |  |  |  |  | NO | NO | Not Rated | Not Rated | Not Rated | Not Rated | Replace failed 20 ft pipe sections including supports - one per 1000 LF. |  |  |  |  | NO |  |  |  |  | NO |  |  |  |  | Not Applicable |  |  |  |  | 0% | 0 | [8 empty] | 0% | 0 | [8 empty] | NO |  |  |  |  | 0% |  |  |  |  | 0 |  |  |  |  | Consequence is for piping only. Enter floor wetting consequence seperately. Cost includes allowance for MEP relocation to perform work. | None | By User | By User | Not Given | none |  |  |  |  | Yes | 2016-10-26 - Corrected consequence descriptions. | YES
D2031.023b | D2031.023b | Sanitary Waste Piping - Cast Iron w/bell and spigot couplings, SDC D,E,F, BRACING FRAGILITY | Costing based upon 1000 ft segments of pipe | Normal | SDC D, E or F (high seismic design) | Each | Each | Peak Floor Acceleration | g | 1 | DS1 |  |  |  |  | Sequential |  |  |  |  | Seq(DS1) | 737 | LF 1000 | NO | NO | Isolated support failure w/o leakage - 0.5 supports fail per 1000 feet of pipe (assuming supports every 20 feet). |  |  |  |  | 1 |  |  |  |  | 2.25 |  |  |  |  | 0.4 |  |  |  |  | Not Specified |  |  |  |  | By User |  |  |  |  | NO | NO | Not Rated | Not Rated | Not Rated | Not Rated | Replace failed supports - 0.5 per 1000 LF. |  |  |  |  | NO |  |  |  |  | NO |  |  |  |  | Not Applicable |  |  |  |  | 0% | 0 | [8 empty] | 0% | 0 | [8 empty] | NO |  |  |  |  | 0% |  |  |  |  | 0 |  |  |  |  | Consequence is for piping only. Enter floor wetting consequence seperately. Cost includes allowance for MEP relocation to perform work. | None | By User | By User | Not Given | none |  |  |  |  | Yes | 2016-10-26 - Corrected consequence descriptions. | YES
D2031.024a | D2031.024a | Sanitary Waste Piping - Cast Iron w/bell and spigot couplings, SDC D,E,F (OSHPD or sim), PIPING FRAGILITY | Costing based upon 1000 ft segments of pipe | Special Regulation (e.g. OSHPD) for piping installations | SDC D, E or F (high seismic design) | Each | Each | Peak Floor Acceleration | g | 1 | DS1 |  |  |  |  | Sequential |  |  |  |  | Seq(DS1) | 738 | LF 1000 | NO | NO | Joints break - 1 break per 1000 feet of pipe. |  |  |  |  | 1 |  |  |  |  | 3 |  |  |  |  | 0.4 |  |  |  |  | Not Specified |  |  |  |  | By User |  |  |  |  | NO | NO | Not Rated | Not Rated | Not Rated | Not Rated | Replace failed 20 ft pipe sections including supports - one per 1000 LF. |  |  |  |  | NO |  |  |  |  | NO |  |  |  |  | Not Applicable |  |  |  |  | 0% | 0 | [8 empty] | 0% | 0 | [8 empty] | NO |  |  |  |  | 0% |  |  |  |  | 0 |  |  |  |  | Consequence is for piping only. Enter floor wetting consequence seperately. Cost includes allowance for MEP relocation to perform work. | None | By User | By User | Not Given | none |  |  |  |  | Yes | 2016-10-26 - Corrected consequence descriptions. | YES
D2031.024b | D2031.024b | Sanitary Waste Piping - Cast Iron w/bell and spigot couplings, SDC D,E,F (OSHPD or sim), BRACING FRAGILITY | Costing based upon 1000 ft segments of pipe | Special Regulation (e.g. OSHPD) for piping installations | SDC D, E or F (high seismic design) | Each | Each | Peak Floor Acceleration | g | 1 | DS1 |  |  |  |  | Sequential |  |  |  |  | Seq(DS1) | 739 | LF 1000 | NO | NO | Isolated support failure w/o leakage - 0.5 supports fail per 1000 feet of pipe (assuming supports every 20 feet). |  |  |  |  | 1 |  |  |  |  | 2.25 |  |  |  |  | 0.4 |  |  |  |  | Not Specified |  |  |  |  | By User |  |  |  |  | NO | NO | Not Rated | Not Rated | Not Rated | Not Rated | Retighten flange bolts at leaking joints. |  |  |  |  | NO |  |  |  |  | NO |  |  |  |  | Not Applicable |  |  |  |  | 0% | 0 | [8 empty] | 0% | 0 | [8 empty] | NO |  |  |  |  | 0% |  |  |  |  | 0 |  |  |  |  | Consequence is for piping only. Enter floor wetting consequence seperately. Cost includes allowance for MEP relocation to perform work. | None | By User | By User | Not Given | none |  |  |  |  | Yes | 2016-10-26 - Corrected consequence descriptions. | YES
D2051.011a | D2051.011a | Chilled Water Piping - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC A or B, PIPING FRAGILITY | Costing based upon 1000 ft segments of pipe, pipe 2.5 inches in diameter or less | Normal | SDC A or B (no seismic design) | Each | Each | Peak Floor Acceleration | g | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 740 | LF 1000 | NO | NO | Small Leakage at joints - 1 leak per 1000 feet of pipe. | Large Leakage w/ major repair - 1 leak per 1000 feet of pipe. |  |  |  | 1 | 1 |  |  |  | 0.55 | 1.1 |  |  |  | 0.4 | 0.4 |  |  |  | Not Specified | Not Specified |  |  |  | By User | By User |  |  |  | NO | NO | Not Rated | Not Rated | Not Rated | Not Rated | Replace failed vertical braces. One repair per 1000 LF. |  |  |  |  | NO | NO |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0 | 0 | [6 empty] | NO | NO |  |  |  | 0% | 0 |  |  |  | 0 | 0 |  |  |  | Consequence is for piping only. Enter floor wetting consequence seperately. Cost includes allowance for MEP relocation to perform work. | None | By User | By User | Not Given | none | none |  |  |  | Yes | 2016-10-26 - Corrected consequence descriptions. | YES
D2051.011b | D2051.011b | Chilled Water Piping - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC A or B, BRACING FRAGILITY | Costing based upon 1000 ft segments of pipe, pipe 2.5 inches in diameter or less | Normal | SDC A or B (no seismic design) | Each | Each | Peak Floor Acceleration | g | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 741 | LF 1000 | NO | NO | Isolated support failure w/o leakage - 0.5 supports fail per 1000 feet of pipe (assuming supports every 20 feet). | Multiple supports failure and 60 feet of pipe fail per 1000 feet of pipe (assuming supports every 20 feet). |  |  |  | 1 | 1 |  |  |  | 1.2 | 2.4 |  |  |  | 0.5 | 0.5 |  |  |  | Not Specified | Not Specified |  |  |  | By User | By User |  |  |  | NO | NO | Not Rated | Not Rated | Not Rated | Not Rated | Retighten flange bolts at leaking joints. One repair per 1000 LF. | Replace 20 foot sections of pipe where breaks occur. One repair per 1000 LF. |  |  |  | NO | NO |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0 | 0 | [6 empty] | NO | NO |  |  |  | 0% | 0 |  |  |  | 0 | 0 |  |  |  | Consequence is for piping only. Enter floor wetting consequence seperately. Cost includes allowance for MEP relocation to perform work. | None | By User | By User | Not Given | none | none |  |  |  | Yes | 2016-10-26 - Corrected consequence descriptions. | YES
D2051.012a | D2051.012a | Chilled Water Piping - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC C, PIPING FRAGILITY | Costing based upon 1000 ft segments of pipe, pipe 2.5 inches in diameter or less | Normal | SDC C (low seismic design) | Each | Each | Peak Floor Acceleration | g | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 742 | LF 1000 | NO | NO | Small Leakage at joints - 1 leak per 1000 feet of pipe. | Large Leakage w/ major repair - 1 leak per 1000 feet of pipe. |  |  |  | 1 | 1 |  |  |  | 0.55 | 1.1 |  |  |  | 0.4 | 0.4 |  |  |  | Not Specified | Not Specified |  |  |  | By User | By User |  |  |  | NO | NO | Not Rated | Not Rated | Not Rated | Not Rated | Retighten flange bolts at leaking joints. One repair per 1000 LF. | Replace 20 foot sections of pipe where breaks occur. One repair per 1000 LF. |  |  |  | NO | NO |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | NO |  |  |  | 0% | 0% |  |  |  | 0 | 0 |  |  |  | Consequence is for piping only. Enter floor wetting consequence seperately. Cost includes allowance for MEP relocation to perform work. | None | By User | By User | Not Given | none | none |  |  |  | Yes | 2016-10-26 - Corrected consequence descriptions. | YES
D2051.012b | D2051.012b | Chilled Water Piping - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC C, BRACING FRAGILITY | Costing based upon 1000 ft segments of pipe, pipe 2.5 inches in diameter or less | Normal | SDC C (low seismic design) | Each | Each | Peak Floor Acceleration | g | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 743 | LF 1000 | NO | NO | Isolated support failure w/o leakage - 0.5 supports fail per 1000 feet of pipe (assuming supports every 20 feet). | Multiple supports failure and 60 feet of pipe fail per 1000 feet of pipe (assuming supports every 20 feet). |  |  |  | 1 | 1 |  |  |  | 1.2 | 2.4 |  |  |  | 0.5 | 0.5 |  |  |  | Not Specified | Not Specified |  |  |  | By User | By User |  |  |  | NO | NO | Not Rated | Not Rated | Not Rated | Not Rated | Replace failed lateral braces. One repair per 1000 LF. | Replace failed vertical braces. One repair per 1000 LF. |  |  |  | NO | NO |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | NO |  |  |  | 0% | 0% |  |  |  | 0 | 0 |  |  |  | Consequence is for piping only. Enter floor wetting consequence seperately. Cost includes allowance for MEP relocation to perform work. | None | By User | By User | Not Given | none | none |  |  |  | Yes | 2016-10-26 - Corrected consequence descriptions. | YES
D2051.013a | D2051.013a | Chilled Water Piping - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC D, E, or F, PIPING FRAGILITY | Costing based upon 1000 ft segments of pipe, pipe 2.5 inches in diameter or less | Normal | SDC D, E, F (high seismic design) | Each | Each | Peak Floor Acceleration | g | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 744 | LF 1000 | NO | NO | Small Leakage at joints - 1 leak per 1000 feet of pipe. | Large Leakage w/ major repair - 1 leak per 1000 feet of pipe. |  |  |  | 1 | 1 |  |  |  | 0.55 | 1.1 |  |  |  | 0.4 | 0.4 |  |  |  | Not Specified | Not Specified |  |  |  | By User | By User |  |  |  | NO | NO | Not Rated | Not Rated | Not Rated | Not Rated | Retighten flange bolts at leaking joints. One repair per 1000 LF. | Replace 20 foot sections of pipe where breaks occur. One repair per 1000 LF. |  |  |  | NO | NO |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | NO |  |  |  | 0% | 0% |  |  |  | 0 | 0 |  |  |  | Consequence is for piping only. Enter floor wetting consequence seperately. Cost includes allowance for MEP relocation to perform work. | None | By User | By User | Not Given | none | none |  |  |  | Yes | 2016-10-26 - Corrected consequence descriptions. | YES
D2051.013b | D2051.013b | Chilled Water Piping - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC D, E, or F, BRACING FRAGILITY | Costing based upon 1000 ft segments of pipe, pipe 2.5 inches in diameter or less | Normal | SDC D, E, F (high seismic design) | Each | Each | Peak Floor Acceleration | g | 1 | DS1 |  |  |  |  | Sequential |  |  |  |  | Seq(DS1) | 745 | LF 1000 | NO | NO | Isolated support failure w/o leakage - 0.5 supports fail per 1000 feet of pipe (assuming supports every 20 feet). |  |  |  |  | 1 |  |  |  |  | 2.25 |  |  |  |  | 0.4 |  |  |  |  | Not Specified |  |  |  |  | By User |  |  |  |  | NO | NO | Not Rated | Not Rated | Not Rated | Not Rated | Replace failed lateral braces. One repair per 1000 LF. | Replace failed vertical braces. One repair per 1000 LF. |  |  |  | NO |  |  |  |  | NO |  |  |  |  | Not Applicable |  |  |  |  | 0% | 0 | [8 empty] | 0% | 0 | [8 empty] | NO |  |  |  |  | 0% |  |  |  |  | 0 |  |  |  |  | Consequence is for piping only. Enter floor wetting consequence seperately. Cost includes allowance for MEP relocation to perform work. | None | By User | By User | Not Given | none |  |  |  |  | Yes | 2016-10-26 - Corrected consequence descriptions. | YES
D2051.014a | D2051.014a | Chilled Water Piping - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC D, E, or F (OSHPD or sim), PIPING FRAGILITY | Costing based upon 1000 ft segments of pipe, pipe 2.5 inches in diameter or less | Special Regulations (e.g. OSHPD) for Piping Installations | SDC D, E, F (high seismic design) | Each | Each | Peak Floor Acceleration | g | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 746 | LF 1000 | NO | NO | Small Leakage at joints - 1 leak per 1000 feet of pipe. | Large Leakage w/ major repair - 1 leak per 1000 feet of pipe. |  |  |  | 1 | 1 |  |  |  | 0.55 | 1.1 |  |  |  | 0.4 | 0.4 |  |  |  | Not Specified | Not Specified |  |  |  | By User | By User |  |  |  | NO | NO | Not Rated | Not Rated | Not Rated | Not Rated | Retighten leaking joints, one per 1000 LF. | Replace 20 ft section of pipe at leaking joints, one per 1000 LF. |  |  |  | NO | NO |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | NO |  |  |  | 0% | 0% |  |  |  | 0 | 0 |  |  |  | Consequence is for piping only. Enter floor wetting consequence seperately. Cost includes allowance for MEP relocation to perform work. | None | By User | By User | Not Given | none | none |  |  |  | Yes | 2016-10-26 - Corrected consequence descriptions. | YES
D2051.014b | D2051.014b | Chilled Water Piping - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC D, E, or F (OSHPD or sim), BRACING FRAGILITY | Costing based upon 1000 ft segments of pipe, pipe 2.5 inches in diameter or less | Special Regulations (e.g. OSHPD) for Piping Installations | SDC D, E, F (high seismic design) | Each | Each | Peak Floor Acceleration | g | 1 | DS1 |  |  |  |  | Sequential |  |  |  |  | Seq(DS1) | 747 | LF 1000 | NO | NO | Isolated support failure w/o leakage - 0.5 supports fail per 1000 feet of pipe (assuming supports every 20 feet). |  |  |  |  | 1 |  |  |  |  | 3 |  |  |  |  | 0.4 |  |  |  |  | Not Specified |  |  |  |  | By User |  |  |  |  | NO | NO | Not Rated | Not Rated | Not Rated | Not Rated | Retighten leaking joints, one per 1000 LF. | Replace 20 ft section of pipe at leaking joints, one per 1000 LF. |  |  |  | NO |  |  |  |  | NO |  |  |  |  | Not Applicable |  |  |  |  | 0% | 0 | [8 empty] | 0% | 0 | [8 empty] | NO |  |  |  |  | 0% |  |  |  |  | 0 |  |  |  |  | Consequence is for piping only. Enter floor wetting consequence seperately. Cost includes allowance for MEP relocation to perform work. | None | By User | By User | Not Given | none |  |  |  |  | Yes | 2016-10-26 - Corrected consequence descriptions. | YES
D2051.021a | D2051.021a | Chilled Water Piping - Large Diameter Welded Steel - (greater than 2.5 inches in diameter), SDC A or B, PIPING FRAGILITY | Costing based upon 1000 ft segments of pipe, pipe greater than 2.5 inches in diameter | Normal | SDC A or B (no seismic design) | Each | Each | Peak Floor Acceleration | g | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 748 | LF 1000 | NO | NO | Minor leakage at flange connections - 1 leak per 1000 feet of pipe. Retighten flange at leaking joint. | Pipe Break - 1 break per 1000 feet of pipe. |  |  |  | 1 | 1 |  |  |  | 1.5 | 2.6 |  |  |  | 0.4 | 0.4 |  |  |  | Not Specified | Not Specified |  |  |  | By User | By User |  |  |  | NO | NO | Not Rated | Not Rated | Not Rated | Not Rated | Retighten leaking joints, one per 1000 LF. | Replace 20 ft section of pipe at leaking joints, one per 1000 LF. |  |  |  | NO | NO |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | NO |  |  |  | 0% | 0% |  |  |  | 0 | 0 |  |  |  | Consequence is for piping only. Enter floor wetting consequence seperately. Cost includes allowance for MEP relocation to perform work. | None | By User | By User | Not Given | none | none |  |  |  | Yes | 2016-10-26 - Corrected consequence descriptions. | YES
D2051.021b | D2051.021b | Chilled Water Piping - Large Diameter Welded Steel - (greater than 2.5 inches in diameter), SDC A or B, BRACING FRAGILITY | Costing based upon 1000 ft segments of pipe, pipe greater than 2.5 inches in diameter | Normal | SDC A or B (no seismic design) | Each | Each | Peak Floor Acceleration | g | 1 | DS1 |  |  |  |  | Sequential |  |  |  |  | Seq(DS1) | 749 | LF 1000 | NO | NO | Vertical Brace Failure - 1 failure per 1000 feet of pipe |  |  |  |  | 1 |  |  |  |  | 2.25 |  |  |  |  | 0.4 |  |  |  |  | Not Specified |  |  |  |  | By User |  |  |  |  | NO | NO | Not Rated | Not Rated | Not Rated | Not Rated | Replace failed supports, one per 1000 LF. |  |  |  |  | NO |  |  |  |  | NO |  |  |  |  | Not Applicable |  |  |  |  | 0% | 0 | [8 empty] | 0% | 0 | [8 empty] | NO |  |  |  |  | 0% |  |  |  |  | 0 |  |  |  |  | Consequence is for piping only. Enter floor wetting consequence seperately. Cost includes allowance for MEP relocation to perform work. | None | By User | By User | Not Given | none |  |  |  |  | Yes | 2016-10-26 - Corrected consequence descriptions. | YES
D2051.022a | D2051.022a | Chilled Water Piping - Large Diameter Welded Steel - (greater than 2.5 inches in diameter), SDC C, PIPING FRAGILITY | Costing based upon 1000 ft segments of pipe, pipe greater than 2.5 inches in diameter | Normal | SDC C (low seismic design) | Each | Each | Peak Floor Acceleration | g | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 750 | LF 1000 | NO | NO | Minor leakage at flange connections - 1 leak per 1000 feet of pipe. | Pipe Break - 1 break per 1000 feet of pipe. |  |  |  | 1 | 1 |  |  |  | 1.5 | 2.6 |  |  |  | 0.4 | 0.4 |  |  |  | Not Specified | Not Specified |  |  |  | By User | By User |  |  |  | NO | NO | Not Rated | Not Rated | Not Rated | Not Rated | Retighten leaking joints, one per 1000 LF. | Replace 20 ft section of pipe at leaking joints, one per 1000 LF. |  |  |  | NO | NO |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | NO |  |  |  | 0% | 0% |  |  |  | 0 | 0 |  |  |  | Consequence is for piping only. Enter floor wetting consequence seperately. Cost includes allowance for MEP relocation to perform work. | None | By User | By User | Not Given | none | none |  |  |  | Yes | 2016-10-26 - Corrected consequence descriptions. | YES
D2051.023a | D2051.023a | Chilled Water Piping - Large Diameter Welded Steel - (greater than 2.5 inches in diameter), SDC D, E, or F, PIPING FRAGILITY | Costing based upon 1000 ft segments of pipe, pipe greater than 2.5 inches in diameter | Normal | SDC D, E, F (high seismic design | Each | Each | Peak Floor Acceleration | g | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 751 | LF 1000 | NO | NO | Minor leakage at flange connections - 1 leak per 1000 feet of pipe. | Pipe Break - 1 break per 1000 feet of pipe. |  |  |  | 1 | 1 |  |  |  | 2.25 | 4.1 |  |  |  | 0.4 | 0.4 |  |  |  | Not Specified | Not Specified |  |  |  | By User | By User |  |  |  | NO | NO | Not Rated | Not Rated | Not Rated | Not Rated | Retighten leaking joints, one per 1000 LF. | Replace 20 ft section of pipe at leaking joints, one per 1000 LF. |  |  |  | NO | NO |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0 | 0 | [6 empty] | NO | NO |  |  |  | 0% | 0 |  |  |  | 0 | 0 |  |  |  | Consequence is for piping only. Enter floor wetting consequence seperately. Cost includes allowance for MEP relocation to perform work. | None | By User | By User | Not Given | none | none |  |  |  | Yes | 2016-10-26 - Corrected consequence descriptions. | YES
D2051.023b | D2051.023b | Chilled Water Piping - Large Diameter Welded Steel - (greater than 2.5 inches in diameter), SDC D, E, or F, BRACING FRAGILITY | Costing based upon 1000 ft segments of pipe, pipe greater than 2.5 inches in diameter | Normal | SDC D, E, F (high seismic design | Each | Each | Peak Floor Acceleration | g | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 752 | LF 1000 | NO | NO | Lateral Brace Failure - 0.01 failures per 20 foot pipe section. | Vertical Brace Failure - 1 failure per 1000 feet of pipe. |  |  |  | 1 | 1 |  |  |  | 1.5 | 2.25 |  |  |  | 0.4 | 0.4 |  |  |  | Not Specified | Not Specified |  |  |  | By User | By User |  |  |  | NO | NO | Not Rated | Not Rated | Not Rated | Not Rated | Replace failed supports, one per 1000 LF. | Replace failed supports, one per 1000 LF. |  |  |  | NO | NO |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | NO |  |  |  | 0% | 0% |  |  |  | 0 | 0 |  |  |  | Consequence is for piping only. Enter floor wetting consequence seperately. Cost includes allowance for MEP relocation to perform work. | None | By User | By User | Not Given | none | none |  |  |  | Yes | 2016-10-26 - Corrected consequence descriptions. | YES
D2051.024a | D2051.024a | Chilled Water Piping - Large Diameter Welded Steel - (greater than 2.5 inches in diameter), SDC D, E, or F (OSHPD or sim), PIPING FRAGILITY | Costing based upon 1000 ft segments of pipe, pipe greater than 2.5 inches in diameter | Special Regulation (e.g. OSHPD) for Piping Installations | SDC D, E, F (high seismic design) | Each | Each | Peak Floor Acceleration | g | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 753 | LF 1000 | NO | NO | Minor leakage at flange connections - 1 leak per 1000 feet of pipe. | Pipe Break - 1 break per 1000 feet of pipe. |  |  |  | 1 | 1 |  |  |  | 2.25 | 4.1 |  |  |  | 0.4 | 0.4 |  |  |  | Not Specified | Not Specified |  |  |  | By User | By User |  |  |  | NO | NO | Not Rated | Not Rated | Not Rated | Not Rated | Retighten leaking joints, one per 1000 LF. | Replace 20 ft section of pipe at leaking joints, one per 1000 LF. |  |  |  | NO | NO |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | NO |  |  |  | 0% | 0% |  |  |  | 0 | 0 |  |  |  | Consequence is for piping only. Enter floor wetting consequence seperately. Cost includes allowance for MEP relocation to perform work. | None | By User | By User | Not Given | none | none |  |  |  | Yes | 2016-10-26 - Corrected consequence descriptions. | YES
D2051.024b | D2051.024b | Chilled Water Piping - Large Diameter Welded Steel - (greater than 2.5 inches in diameter), SDC D, E, or F (OSHPD or sim), BRACING FRAGILITY | Costing based upon 1000 ft segments of pipe, pipe greater than 2.5 inches in diameter | Special Regulation (e.g. OSHPD) for Piping Installations | SDC D, E, F (high seismic design) | Each | Each | Peak Floor Acceleration | g | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 754 | LF 1000 | NO | NO | Lateral Brace Failure - 1 failure per 1000 foot of pipe. | Vertical Brace Failure - 1 failure per 1000 feet of pipe. |  |  |  | 1 | 1 |  |  |  | 1.5 | 2.25 |  |  |  | 0.4 | 0.4 |  |  |  | Not Specified | Not Specified |  |  |  | By User | By User |  |  |  | NO | NO | Not Rated | Not Rated | Not Rated | Not Rated | Replace failed supports, one per 1000 LF. | Replace failed supports, one per 1000 LF. |  |  |  | NO | NO |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | NO |  |  |  | 0% | 0% |  |  |  | 0 | 0 |  |  |  | Consequence is for piping only. Enter floor wetting consequence seperately. Cost includes allowance for MEP relocation to perform work. | None | By User | By User | Not Given | none | none |  |  |  | Yes | 2016-10-26 - Corrected consequence descriptions. | YES
D2061.011a | D2061.011a | Steam Piping - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC A or B, PIPING FRAGILITY | Costing based upon 1000 ft segments of pipe, pipe 2.5 inches in diameter or less | Normal | SDC A or B (no seismic design) | Each | Each | Peak Floor Acceleration | g | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 755 | LF 1000 | NO | NO | Small Leakage at joints - 1 leak per 1000 feet of pipe. | Large Leakage w/ major repair - 1 leak per 1000 feet of pipe. Replace one 20 ft section per 1000 LF pipe. |  |  |  | 1 | 1 |  |  |  | 0.55 | 1.1 |  |  |  | 0.4 | 0.4 |  |  |  | Not Specified | Not Specified |  |  |  | By User | By User |  |  |  | NO | NO | Not Rated | Not Rated | Not Rated | Not Rated | Retighten leaking joints, one per 1000 LF. | Replace 20 ft section of pipe at leaking joints, one per 1000 LF. |  |  |  | NO | NO |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | NO |  |  |  | 0% | 0% |  |  |  | 0 | 0 |  |  |  | Consequence is for piping only. Enter floor wetting consequence seperately. Cost includes allowance for MEP relocation to perform work. | Not Given | By User | By User | Not Given | none | none |  |  |  | Yes | 2016-10-26 - Corrected consequence descriptions. | YES
D2061.011b | D2061.011b | Steam Piping - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC A or B, BRACING FRAGILITY | Costing based upon 1000 ft segments of pipe, pipe 2.5 inches in diameter or less | Normal | SDC A or B (no seismic design) | Each | Each | Peak Floor Acceleration | g | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 756 | LF 1000 | NO | NO | Isolated support failure w/o leakage - 1 supports fail per 1000 feet of pipe (assuming supports every 20 feet). | Multiple supports failure and 60 feet of pipe fail per 1000 feet of pipe (assuming supports every 20 feet). |  |  |  | 1 | 1 |  |  |  | 1.2 | 2.4 |  |  |  | 0.5 | 0.5 |  |  |  | Not Specified | Not Specified |  |  |  | By User | By User |  |  |  | NO | NO | Not Rated | Not Rated | Not Rated | Not Rated | Replace failed supports, one per 1000 LF. | Replace 60 ft pipe and supports per 1000 LF. |  |  |  | NO | NO |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | NO |  |  |  | 0% | 0% |  |  |  | 0 | 0 |  |  |  | Consequence is for piping only. Enter floor wetting consequence seperately. Cost includes allowance for MEP relocation to perform work. | Not Given | By User | By User | Not Given | none | none |  |  |  | Yes | 2016-10-26 - Corrected consequence descriptions. | YES
D2061.012a | D2061.012a | Steam Piping - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC C, PIPING FRAGILITY | Costing based upon 1000 ft segments of pipe, pipe 2.5 inches in diameter or less | Normal | SDC C (low seismic design) | Each | Each | Peak Floor Acceleration | g | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 757 | LF 1000 | NO | NO | Small Leakage at joints - 1 leak per 1000 feet of pipe. | Large Leakage w/ major repair - 1 leak per 1000 feet of pipe. Replace one 20 ft section per 1000 LF pipe. |  |  |  | 1 | 1 |  |  |  | 0.55 | 1.1 |  |  |  | 0.4 | 0.4 |  |  |  | Not Specified | Not Specified |  |  |  | By User | By User |  |  |  | NO | NO | Not Rated | Not Rated | Not Rated | Not Rated | Retighten flange bolts at leaking joints, 1 joint per 1000 LF. | Replace 20 foot sections of pipe where breaks occur, one per 1000 LF. |  |  |  | NO | NO |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | NO |  |  |  | 0% | 0% |  |  |  | 0 | 0 |  |  |  | Consequence is for piping only. Enter floor wetting consequence seperately. Cost includes allowance for MEP relocation to perform work. | Not Given | By User | By User | Not Given | none | none |  |  |  | Yes | 2016-10-26 - Corrected consequence descriptions. | YES
D2061.012b | D2061.012b | Steam Piping - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC C, BRACING FRAGILITY | Costing based upon 1000 ft segments of pipe, pipe 2.5 inches in diameter or less | Normal | SDC C (low seismic design) | Each | Each | Peak Floor Acceleration | g | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 758 | LF 1000 | NO | NO | Isolated support failure w/o leakage - 1 supports fail per 1000 feet of pipe (assuming supports every 20 feet). | Multiple supports failure and 60 feet of pipe fail per 1000 feet of pipe (assuming supports every 20 feet). |  |  |  | 1 | 1 |  |  |  | 1.2 | 2.4 |  |  |  | 0.5 | 0.5 |  |  |  | Not Specified | Not Specified |  |  |  | By User | By User |  |  |  | NO | NO | Not Rated | Not Rated | Not Rated | Not Rated | Replace failed supports, one per 1000 LF. | Replace 60 ft pipe and supports per 1000 LF. |  |  |  | NO | NO |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | NO |  |  |  | 0% | 0% |  |  |  | 0 | 0 |  |  |  | Consequence is for piping only. Enter floor wetting consequence seperately. Cost includes allowance for MEP relocation to perform work. | Not Given | By User | By User | Not Given | none | none |  |  |  | Yes | 2016-10-26 - Corrected consequence descriptions. | YES
D2061.013a | D2061.013a | Steam Piping - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC D, E, or F, PIPING FRAGILITY | Costing based upon 1000 ft segments of pipe, pipe 2.5 inches in diameter or less | Normal | SDC D, E, F (high seismic design) | Each | Each | Peak Floor Acceleration | g | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 759 | LF 1000 | NO | NO | Small Leakage at joints - 1 leak per 1000 feet of pipe. | Large Leakage w/ major repair - 1 leak per 1000 feet of pipe. Replace one 20 ft section per 1000 LF pipe. |  |  |  | 1 | 1 |  |  |  | 0.55 | 1.1 |  |  |  | 0.4 | 0.4 |  |  |  | Not Specified | Not Specified |  |  |  | By User | By User |  |  |  | NO | NO | Not Rated | Not Rated | Not Rated | Not Rated | Retighten flange bolts at leaking joints, 1 joint per 1000 LF. | Replace 20 foot sections of pipe where breaks occur, one per 1000 LF. |  |  |  | NO | NO |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | NO |  |  |  | 0% | 0% |  |  |  | 0 | 0 |  |  |  | Consequence is for piping only. Enter floor wetting consequence seperately. Cost includes allowance for MEP relocation to perform work. | Not Given | By User | By User | Not Given | none | none |  |  |  | Yes | 2016-10-26 - Corrected consequence descriptions. | YES
D2061.013b | D2061.013b | Steam Piping - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC D, E, or F, BRACING FRAGILITY | Costing based upon 1000 ft segments of pipe, pipe 2.5 inches in diameter or less | Normal | SDC D, E, F (high seismic design) | Each | Each | Peak Floor Acceleration | g | 1 | DS1 |  |  |  |  | Sequential |  |  |  |  | Seq(DS1) | 760 | LF 1000 | NO | NO | Isolated support failure w/o leakage - 1 supports fail per 1000 feet of pipe (assuming supports every 20 feet). |  |  |  |  | 1 |  |  |  |  | 2.25 |  |  |  |  | 0.4 |  |  |  |  | Not Specified |  |  |  |  | By User |  |  |  |  | NO | NO | Not Rated | Not Rated | Not Rated | Not Rated | Replace failed supports, one per 1000 LF. |  |  |  |  | NO |  |  |  |  | NO |  |  |  |  | Not Applicable |  |  |  |  | 0% | 0 | [8 empty] | 0% | 0 | [8 empty] | NO |  |  |  |  | 0% |  |  |  |  | 0 |  |  |  |  | Consequence is for piping only. Enter floor wetting consequence seperately. Cost includes allowance for MEP relocation to perform work. | Not Given | By User | By User | Not Given | none |  |  |  |  | Yes | 2016-10-26 - Corrected consequence descriptions. | YES
D2061.014a | D2061.014a | Steam Piping - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC D, E, or F (OSHPD or sim), PIPING FRAGILITY | Costing based upon 1000 ft segments of pipe, pipe 2.5 inches in diameter or less | Special Regulations (e.g. OSHPD) for Piping Installations | SDC D, E, F (high seismic design) | Each | Each | Peak Floor Acceleration | g | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 761 | LF 1000 | NO | NO | Small Leakage at joints - 1 leak per 1000 feet of pipe. | Large Leakage w/ major repair - 1 leak per 1000 feet of pipe. Replace one 20 ft section per 1000 LF pipe. |  |  |  | 1 | 1 |  |  |  | 0.55 | 1.1 |  |  |  | 0.4 | 0.4 |  |  |  | Not Specified | Not Specified |  |  |  | By User | By User |  |  |  | NO | NO | Not Rated | Not Rated | Not Rated | Not Rated | Retighten flange bolts at leaking joints, 1 joint per 1000 LF. | Replace 20 foot sections of pipe where breaks occur, one per 1000 LF. |  |  |  | NO | NO |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | NO |  |  |  | 0% | 0% |  |  |  | 0 | 0 |  |  |  | Consequence is for piping only. Enter floor wetting consequence seperately. Cost includes allowance for MEP relocation to perform work. | Not Given | By User | By User | Not Given | none | none |  |  |  | Yes | 2016-10-26 - Corrected consequence descriptions. | YES
D2061.014b | D2061.014b | Steam Piping - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC D, E, or F (OSHPD or sim), BRACING FRAGILITY | Costing based upon 1000 ft segments of pipe, pipe 2.5 inches in diameter or less | Special Regulations (e.g. OSHPD) for Piping Installations | SDC D, E, F (high seismic design) | Each | Each | Peak Floor Acceleration | g | 1 | DS1 |  |  |  |  | Sequential |  |  |  |  | Seq(DS1) | 762 | LF 1000 | NO | NO | Isolated support failure w/o leakage - 1 supports fail per 1000 feet of pipe (assuming supports every 20 feet). |  |  |  |  | 1 |  |  |  |  | 3 |  |  |  |  | 0.4 |  |  |  |  | Not Specified |  |  |  |  | By User |  |  |  |  | NO | NO | Not Rated | Not Rated | Not Rated | Not Rated | Replace failed supports, one per 1000 LF. |  |  |  |  | NO |  |  |  |  | NO |  |  |  |  | Not Applicable |  |  |  |  | 0% | 0 | [8 empty] | 0% | 0 | [8 empty] | NO |  |  |  |  | 0% |  |  |  |  | 0 |  |  |  |  | Consequence is for piping only. Enter floor wetting consequence seperately. Cost includes allowance for MEP relocation to perform work. | Not Given | By User | By User | Not Given | none |  |  |  |  | Yes | 2016-10-26 - Corrected consequence descriptions. | YES
D2061.021a | D2061.021a | Steam Piping - Large Diameter Welded Steel - (greater than 2.5 inches in diameter), SDC A or B, PIPING FRAGILITY | Costing based upon 1000 ft segments of pipe, pipe greater than 2.5 inches in diameter | Normal | SDC A or B (no seismic design) | Each | Each | Peak Floor Acceleration | g | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 763 | LF 1000 | NO | NO | Minor leakage at flange connections - 1 leak per 1000 feet of pipe. | Pipe Break - 1 break per 1000 feet of pipe. Replace one 20 ft section per 1000 LF pipe. |  |  |  | 1 | 1 |  |  |  | 1.5 | 2.6 |  |  |  | 0.4 | 0.4 |  |  |  | Not Specified | Not Specified |  |  |  | By User | By User |  |  |  | NO | NO | Not Rated | Not Rated | Not Rated | Not Rated | Retighten flange bolts at leaking joints, 1 joint per 1000 LF. | Replace 20 foot sections of pipe where breaks occur, one per 1000 LF. |  |  |  | NO | NO |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0% | 0 | [6 empty] | NO | NO |  |  |  | 0% | 0% |  |  |  | 0 | 0 |  |  |  | Consequence is for piping only. Enter floor wetting consequence seperately. Cost includes allowance for MEP relocation to perform work. | Not Given | By User | By User | Not Given | none | none |  |  |  | Yes | 2016-10-26 - Corrected consequence descriptions. | YES
D2061.022a | D2061.022a | Steam Piping - Large Diameter Welded Steel - (greater than 2.5 inches in diameter), SDC C, PIPING FRAGILITY | Costing based upon 1000 ft segments of pipe, pipe greater than 2.5 inches in diameter | Normal | SDC C (low seismic design) | Each | Each | Peak Floor Acceleration | g | 2 | DS1 | DS2 |  |  |  | Sequential | Sequential |  |  |  | Seq(DS1,DS2) | 764 | LF 1000 | NO | NO | Minor leakage at flange connections - 1 leak per 1000 feet of pipe. | Pipe Break - 1 break per 1000 feet of pipe. Replace one 20 ft section per 1000 LF pipe. |  |  |  | 1 | 1 |  |  |  | 1.5 | 2.6 |  |  |  | 0.4 | 0.4 |  |  |  | Not Specified | Not Specified |  |  |  | By User | By User |  |  |  | NO | NO | Not Rated | Not Rated | Not Rated | Not Rated | Retighten flange bolts at leaking joints, 1 joint per 1000 LF. | Replace 20 foot sections of pipe where breaks occur, one per 1000 LF. |  |  |  | NO | NO |  |  |  | NO | NO |  |  |  | Not Applicable | Not Applicable |  |  |  | 0% | 0 | 0% | 0 | [6 empty] | 0% | 0 | 0 | 0 | [6 empty] | NO | NO |  |  |  | 0% | 0 |  |  |  | 0 | 0 |  |  |  | Consequence is for piping only. Enter floor wetting consequence seperately. Cost includes allowance for MEP relocation to perform work. | Not Given | By User | By User | Not Given | none | none |  |  |  | Yes | 2016-10-26 - Corrected consequence descriptions. | YES

## Cost Summary
| This sheet provides the cost and time consequence data for use by PACT. | [14 empty] | Current file | 2 | 0
2019-01-27
| Sheet Names |  | NISTIR Classification | Component Name | Repair Cost, p10, DS1 | Repair Cost, p50, DS1 | Repair Cost, p90, DS1 | Best Fit, DS1 | Mean Value, DS1 | CV / Dispersion, DS1 | Lower Qty Cutoff, DS1 | Lower Qty Mean, DS1 | 0 | 0 | 0 | Upper Qty Mean, DS1 | CV / Dispersion, DS1 | Upper Qty Cutoff, DS1 | Quantity Unit, DS1 | Repair Cost, p10, DS2 | Repair Cost, p50, DS2 | Repair Cost, p90, DS2 | Best Fit, DS2 | Mean Value, DS2 | CV / Dispersion, DS2 | Lower Qty Cutoff, DS2 | Lower Qty Mean, DS2 | 0 | 0 | 0 | Upper Qty Mean, DS2 | CV / Dispersion, DS2 | Upper Qty Cutoff, DS2 | Quantity Unit, DS2 | Repair Cost, p10, DS3 | Repair Cost, p50, DS3 | Repair Cost, p90, DS3 | Best Fit, DS3 | Mean Value, DS3 | CV / Dispersion, DS3 | Lower Qty Cutoff, DS3 | Lower Qty Mean, DS3 | 0 | 0 | 0 | Upper Qty Mean, DS3 | CV / Dispersion, DS3 | Upper Qty Cutoff, DS3 | Quantity Unit, DS3 | Repair Cost, p10, DS4 | Repair Cost, p50, DS4 | Repair Cost, p90, DS4 | Best Fit, DS4 | Mean Value, DS4 | CV / Dispersion, DS4 | Lower Qty Cutoff, DS4 | Lower Qty Mean, DS4 | 0 | 0 | 0 | Upper Qty Mean, DS4 | CV / Dispersion, DS4 | Upper Qty Cutoff, DS4 | Quantity Unit, DS4 | Repair Cost, p10, DS5 | Repair Cost, p50, DS5 | Repair Cost, p90, DS5 | Best Fit, DS5 | Mean Value, DS5 | CV / Dispersion, DS5 | Lower Qty Cutoff, DS5 | Lower Qty Mean, DS5 | 0 | 0 | 0 | Upper Qty Mean, DS5 | CV / Dispersion, DS5 | Upper Qty Cutoff, DS5 | Quantity Unit, DS5 | Time, p10, DS1 | Time, p50, DS1 | Time, p90, DS1 | Best Fit, DS1 | Mean Value, DS1 | CV / Dispersion, DS1 | Lower Qty Cutoff, DS1 | Lower Qty Mean, DS1 | 0 | 0 | 0 | Upper Qty Mean, DS1 | CV / Dispersion, DS1 | Upper Qty Cutoff, DS1 | Quantity Unit, DS1 | Time, p10, DS2 | Time, p50, DS2 | Time, p90, DS2 | Best Fit, DS2 | Mean Value, DS2 | CV / Dispersion, DS2 | Lower Qty Cutoff, DS2 | Lower Qty Mean, DS2 | 0 | 0 | 0 | Upper Qty Mean, DS2 | CV / Dispersion, DS2 | Upper Qty Cutoff, DS2 | Quantity Unit, DS2 | Time, p10, DS3 | Time, p50, DS3 | Time, p90, DS3 | Best Fit, DS3 | Mean Value, DS3 | CV / Dispersion, DS3 | Lower Qty Cutoff, DS3 | Lower Qty Mean, DS3 | 0 | 0 | 0 | Upper Qty Mean, DS3 | CV / Dispersion, DS3 | Upper Qty Cutoff, DS3 | Quantity Unit, DS3 | Time, p10, DS4 | Time, p50, DS4 | Time, p90, DS4 | Best Fit, DS4 | Mean Value, DS4 | CV / Dispersion, DS4 | Lower Qty Cutoff, DS4 | Lower Qty Mean, DS4 | 0 | 0 | 0 | Upper Qty Mean, DS4 | CV / Dispersion, DS4 | Upper Qty Cutoff, DS4 | Quantity Unit, DS4 | Time, p10, DS5 | Time, p50, DS5 | Time, p90, DS5 | Best Fit, DS5 | Mean Value, DS5 | CV / Dispersion, DS5 | Lower Qty Cutoff, DS5 | Lower Qty Mean, DS5 | 0 | 0 | 0 | Upper Qty Mean, DS5 | CV / Dispersion, DS5 | Upper Qty Cutoff, DS5 | Quantity Unit, DS5 | Cost Multiplication Scalar
| B1031.001 |  | B1031.001 | Bolted shear tab gravity connections | 0 | 0 | 0 | LogNormal | 0 | 0.25 | 5 | 0 |  |  |  | 0 | 0.25 | 20 | Each | 6050 | 12720 | 17550 | Normal | 12106.6429 | 0.3706 | 5 | 16536 |  |  |  | 10176 | 0.3706 | 20 | Each | 6050 | 12970 | 18050 | Normal | 12356.6659 | 0.37889 | 5 | 15564 |  |  |  | 11024.5 | 0.37889 | 20 | Each | 6050 | 12720 | 18150 | Normal | 12306.6298 | 0.38359 | 5 | 15264 |  |  |  | 10812 | 0.38359 | 20 | Each | [15 empty] | 0 | 0 | 0 | LogNormal | 0 | 0.35355 | 5 | 0 |  |  |  | 0 | 0.35355 | 20 | Each | 5.8721 | 12.3459 | 17.0338 | Normal | 11.7505 | 0.44704 | 5 | 16.0497 |  |  |  | 9.8767 | 0.44704 | 20 | Each | 5.8721 | 12.5885 | 17.5191 | Normal | 11.9932 | 0.45394 | 5 | 15.1062 |  |  |  | 10.7002 | 0.45394 | 20 | Each | 5.8721 | 12.3459 | 17.6162 | Normal | 11.9447 | 0.45787 | 5 | 14.8151 |  |  |  | 10.494 | 0.45787 | 20 | Each | [15 empty] | 1
| B1031.011a |  | B1031.011a | Steel Column Base Plates, Column W < 150 plf | 0 | 0 | 0 | LogNormal | 0 | 0.25 | 5 | 0 |  |  |  | 0 | 0.25 | 20 | Each | 11170 | 19510 | 32300 | LogNormal | 19223.6845 | 0.40697 | 5 | 25363 |  |  |  | 15608 | 0.40697 | 20 | Each | 17880 | 26220 | 43930 | LogNormal | 27262.9829 | 0.36644 | 5 | 31464 |  |  |  | 22287 | 0.36644 | 20 | Each | 22280 | 30620 | 50930 | LogNormal | 32423.4403 | 0.34341 | 5 | 36744 |  |  |  | 26027 | 0.34341 | 20 | Each | [15 empty] | 0 | 0 | 0 | LogNormal | 0 | 0.35355 | 5 | 0 |  |  |  | 0 | 0.35355 | 20 | Each | 10.8415 | 18.9362 | 31.35 | LogNormal | 18.6583 | 0.47762 | 5 | 24.6171 |  |  |  | 15.149 | 0.47762 | 20 | Each | 17.3541 | 25.4488 | 42.6379 | LogNormal | 26.4611 | 0.4436 | 5 | 30.5386 |  |  |  | 21.6315 | 0.4436 | 20 | Each | 21.6247 | 29.7194 | 49.4321 | LogNormal | 31.4698 | 0.42477 | 5 | 35.6633 |  |  |  | 25.2615 | 0.42477 | 20 | Each | [15 empty] | 1
| B1031.011b |  | B1031.011b | Steel Column Base Plates, Column 150 plf < W < 300 plf | 0 | 0 | 0 | LogNormal | 0 | 0.25 | 5 | 0 |  |  |  | 0 | 0.25 | 20 | Each | 11970 | 20310 | 33100 | LogNormal | 20081.8941 | 0.39156 | 5 | 26403 |  |  |  | 16248 | 0.39156 | 20 | Each | 19880 | 28220 | 45930 | LogNormal | 29395.1616 | 0.34177 | 5 | 33864 |  |  |  | 23987 | 0.34177 | 20 | Each | 26280 | 34620 | 54930 | LogNormal | 36656.9099 | 0.30576 | 5 | 41544 |  |  |  | 29427 | 0.30576 | 20 | Each | [15 empty] | 0 | 0 | 0 | LogNormal | 0 | 0.35355 | 5 | 0 |  |  |  | 0 | 0.35355 | 20 | Each | 8.8015 | 14.9338 | 24.3382 | LogNormal | 14.7661 | 0.46456 | 5 | 19.4139 |  |  |  | 11.947 | 0.46456 | 20 | Each | 14.6176 | 20.75 | 33.7721 | LogNormal | 21.6141 | 0.42345 | 5 | 24.9 |  |  |  | 17.6375 | 0.42345 | 20 | Each | 19.3235 | 25.4559 | 40.3897 | LogNormal | 26.9536 | 0.39496 | 5 | 30.5471 |  |  |  | 21.6375 | 0.39496 | 20 | Each | [15 empty] | 1
| B1031.011c |  | B1031.011c | Steel Column Base Plates, Column W > 300 plf | 0 | 0 | 0 | LogNormal | 0 | 0.25 | 5 | 0 |  |  |  | 0 | 0.25 | 20 | Each | 13170 | 21510 | 34300 | LogNormal | 21363.1929 | 0.37049 | 5 | 27963 |  |  |  | 17208 | 0.37049 | 20 | Each | 22880 | 31220 | 48930 | LogNormal | 32566.5888 | 0.31042 | 5 | 37464 |  |  |  | 26537 | 0.31042 | 20 | Each | 31280 | 39620 | 59930 | LogNormal | 41889.7261 | 0.26892 | 5 | 47544 |  |  |  | 33677 | 0.26892 | 20 | Each | [15 empty] | 0 | 0 | 0 | LogNormal | 0 | 0.35355 | 5 | 0 |  |  |  | 0 | 0.35355 | 20 | Each | 8.7154 | 14.2346 | 22.6985 | LogNormal | 14.1374 | 0.44695 | 5 | 18.505 |  |  |  | 11.3877 | 0.44695 | 20 | Each | 15.1412 | 20.6603 | 32.3801 | LogNormal | 21.5514 | 0.39857 | 5 | 24.7924 |  |  |  | 17.5613 | 0.39857 | 20 | Each | 20.7 | 26.2191 | 39.6596 | LogNormal | 27.7211 | 0.36717 | 5 | 31.4629 |  |  |  | 22.2862 | 0.36717 | 20 | Each | [15 empty] | 1
| B1031.021a |  | B1031.021a | Welded column splices, Column W < 150 plf | 0 | 0 | 0 | LogNormal | 0 | 0.25 | 5 | 0 |  |  |  | 0 | 0.25 | 20 | Each | 5567.5 | 9340 | 13430 | Normal | 9445.8514 | 0.32475 | 5 | 12142 |  |  |  | 7472 | 0.32475 | 20 | Each | 7567.5 | 11340 | 16530 | LogNormal | 11246.1663 | 0.30204 | 5 | 13608 |  |  |  | 9639 | 0.30204 | 20 | Each | [30 empty] | 0 | 0 | 0 | LogNormal | 0 | 0.35355 | 5 | 0 |  |  |  | 0 | 0.35355 | 20 | Each | 5.4038 | 9.0653 | 13.035 | Normal | 9.1681 | 0.40984 | 5 | 11.7849 |  |  |  | 7.2522 | 0.40984 | 20 | Each | 7.3449 | 11.0065 | 16.0438 | LogNormal | 10.9154 | 0.39208 | 5 | 13.2078 |  |  |  | 9.3555 | 0.39208 | 20 | Each | [30 empty] | 1
| B1031.021b |  | B1031.021b | Welded column splices, Column 150 plf < W < 300 plf | 0 | 0 | 0 | LogNormal | 0 | 0.25 | 5 | 0 |  |  |  | 0 | 0.25 | 20 | Each | 6367.5 | 10140 | 14230 | Normal | 10245.8281 | 0.2994 | 5 | 13182 |  |  |  | 8112 | 0.2994 | 20 | Each | 8367.5 | 13340 | 17330 | Normal | 13012.4994 | 0.26872 | 5 | 16008 |  |  |  | 11339 | 0.26872 | 20 | Each | [30 empty] | 0 | 0 | 0 | LogNormal | 0 | 0.35355 | 5 | 0 |  |  |  | 0 | 0.35355 | 20 | Each | 4.682 | 7.4559 | 10.4632 | Normal | 7.5337 | 0.39005 | 5 | 9.6927 |  |  |  | 5.9647 | 0.39005 | 20 | Each | 6.1526 | 9.8088 | 12.7426 | Normal | 9.568 | 0.36703 | 5 | 11.7706 |  |  |  | 8.3375 | 0.36703 | 20 | Each | [30 empty] | 1
| B1031.021c |  | B1031.021c | Welded column splices, Column W > 300 plf | 0 | 0 | 0 | LogNormal | 0 | 0.25 | 5 | 0 |  |  |  | 0 | 0.25 | 20 | Each | 7567.5 | 11340 | 15430 | Normal | 11445.8276 | 0.26801 | 5 | 14742 |  |  |  | 9072 | 0.26801 | 20 | Each | 9567.5 | 16340 | 18530 | Normal | 14812.3121 | 0.23607 | 5 | 19608 |  |  |  | 13889 | 0.23607 | 20 | Each | [30 empty] | 0 | 0 | 0 | LogNormal | 0 | 0.35355 | 5 | 0 |  |  |  | 0 | 0.35355 | 20 | Each | 5.0079 | 7.5044 | 10.211 | Normal | 7.5744 | 0.36651 | 5 | 9.7557 |  |  |  | 6.0035 | 0.36651 | 20 | Each | 6.3314 | 10.8132 | 12.2625 | Normal | 9.8023 | 0.34384 | 5 | 12.9758 |  |  |  | 9.1912 | 0.34384 | 20 | Each | [30 empty] | 1
| B1033.001a |  | B1033.001a | Special Concentric Braced Frame w WF braces, balanced design criteria, Chevron Brace, Brace w < 40 PLF | 15060 | 36378.4953 | 40960 | Normal | 30799.3567 | 0.32809 | 5 | 47292.0439 |  |  |  | 29102.7962 | 0.32809 | 20 | Each | 17360 | 39357.7429 | 45160 | Normal | 33959.07 | 0.31939 | 5 | 47229.2915 |  |  |  | 33454.0815 | 0.31939 | 20 | Each | 18760 | 41057.7429 | 47560 | Normal | 35792.5246 | 0.31393 | 5 | 49269.2915 |  |  |  | 34899.0815 | 0.31393 | 20 | Each | 18760 | 41057.7429 | 47560 | Normal | 35792.5246 | 0.31393 | 5 | 49269.2915 |  |  |  | 34899.0815 | 0.31393 | 20 | Each | [15 empty] | 9.9662 | 24.074 | 27.1059 | Normal | 20.3818 | 0.41248 | 5 | 31.2962 |  |  |  | 19.2592 | 0.41248 | 20 | Each | 11.4882 | 26.0456 | 29.8853 | Normal | 22.473 | 0.4056 | 5 | 31.2547 |  |  |  | 22.1388 | 0.4056 | 20 | Each | 12.4147 | 27.1706 | 31.4735 | Normal | 23.6865 | 0.40131 | 5 | 32.6047 |  |  |  | 23.095 | 0.40131 | 20 | Each | 12.4147 | 27.1706 | 31.4735 | Normal | 23.6865 | 0.40131 | 5 | 32.6047 |  |  |  | 23.095 | 0.40131 | 20 | Each | [15 empty] | 1
| B1033.001b |  | B1033.001b | Special Concentric Braced Frame w WF braces, balanced design criteria, Chevron Brace, Brace 41 PLF < w < 99 PLF | 15060 | 36378.4953 | 40960 | Normal | 30799.3567 | 0.32809 | 5 | 47292.0439 |  |  |  | 29102.7962 | 0.32809 | 20 | Each | 23160 | 46524.7335 | 55160 | Normal | 41614.0643 | 0.30002 | 5 | 55829.6802 |  |  |  | 39546.0235 | 0.30002 | 20 | Each | 25960 | 50024.7335 | 60060 | Normal | 45347.3025 | 0.29339 | 5 | 60029.6802 |  |  |  | 42521.0235 | 0.29339 | 20 | Each | 25960 | 50024.7335 | 60060 | Normal | 45347.3025 | 0.29339 | 5 | 60029.6802 |  |  |  | 42521.0235 | 0.29339 | 20 | Each | [15 empty] | 9.9662 | 24.074 | 27.1059 | Normal | 20.3818 | 0.41248 | 5 | 31.2962 |  |  |  | 19.2592 | 0.41248 | 20 | Each | 15.3265 | 30.7884 | 36.5029 | Normal | 27.5391 | 0.39053 | 5 | 36.9461 |  |  |  | 26.1701 | 0.39053 | 20 | Each | 17.1794 | 33.1046 | 39.7456 | Normal | 30.0093 | 0.38546 | 5 | 39.7255 |  |  |  | 28.1389 | 0.38546 | 20 | Each | 17.1794 | 33.1046 | 39.7456 | Normal | 30.0093 | 0.38546 | 5 | 39.7255 |  |  |  | 28.1389 | 0.38546 | 20 | Each | [15 empty] | 1
| B1033.001c |  | B1033.001c | Special Concentric Braced Frame w WF braces, balanced design criteria, Chevron Brace, Brace w > 100 PLF | 15060 | 36378.4953 | 40960 | Normal | 30799.3567 | 0.32809 | 5 | 47292.0439 |  |  |  | 29102.7962 | 0.32809 | 20 | Each | 30260 | 55420.9717 | 67560 | Normal | 51080.1211 | 0.28491 | 5 | 66505.166 |  |  |  | 47107.8259 | 0.28491 | 20 | Each | 34660 | 60920.9717 | 75260 | Normal | 56946.8795 | 0.27815 | 5 | 73105.166 |  |  |  | 51782.8259 | 0.27815 | 20 | Each | 34660 | 60920.9717 | 75260 | Normal | 56946.8795 | 0.27815 | 5 | 73105.166 |  |  |  | 51782.8259 | 0.27815 | 20 | Each | [15 empty] | 9.9662 | 24.074 | 27.1059 | Normal | 20.3818 | 0.41248 | 5 | 31.2962 |  |  |  | 19.2592 | 0.41248 | 20 | Each | 20.025 | 36.6756 | 44.7088 | Normal | 33.8026 | 0.37904 | 5 | 44.0107 |  |  |  | 31.1743 | 0.37904 | 20 | Each | 22.9368 | 40.3153 | 49.8044 | Normal | 37.6855 | 0.37399 | 5 | 48.3784 |  |  |  | 34.268 | 0.37399 | 20 | Each | 22.9368 | 40.3153 | 49.8044 | Normal | 37.6855 | 0.37399 | 5 | 48.3784 |  |  |  | 34.268 | 0.37399 | 20 | Each | [15 empty] | 1
| B1033.002a |  | B1033.002a | Special Concentric Braced Frame w WF braces, balanced design criteria, Single Diagonal Brace, Brace w < 40 PLF | 14460 | 35620.7811 | 39860 | Normal | 29980.1204 | 0.33055 | 5 | 46307.0154 |  |  |  | 28496.6248 | 0.33055 | 20 | Each | 17060 | 38921.1716 | 44560 | Normal | 33513.5007 | 0.32014 | 5 | 46705.4059 |  |  |  | 33082.9959 | 0.32014 | 20 | Each | 17260 | 39171.1716 | 44860 | Normal | 33763.0163 | 0.31896 | 5 | 47005.4059 |  |  |  | 33295.4959 | 0.31896 | 20 | Each | 17260 | 39171.1716 | 44860 | Normal | 33763.0163 | 0.31896 | 5 | 47005.4059 |  |  |  | 33295.4959 | 0.31896 | 20 | Each | [15 empty] | 9.5691 | 23.5726 | 26.3779 | Normal | 19.84 | 0.41444 | 5 | 30.6444 |  |  |  | 18.8581 | 0.41444 | 20 | Each | 11.2897 | 25.7567 | 29.4882 | Normal | 22.1774 | 0.40619 | 5 | 30.908 |  |  |  | 21.8932 | 0.40619 | 20 | Each | 11.4221 | 25.9221 | 29.6868 | Normal | 22.3428 | 0.40526 | 5 | 31.1065 |  |  |  | 22.0338 | 0.40526 | 20 | Each | 11.4221 | 25.9221 | 29.6868 | Normal | 22.3428 | 0.40526 | 5 | 31.1065 |  |  |  | 22.0338 | 0.40526 | 20 | Each | [15 empty] | 1
| B1033.002b |  | B1033.002b | Special Concentric Braced Frame w WF braces, balanced design criteria, Single Diagonal Brace, 41 PLF < w < 99 PLF | 14460 | 35620.7811 | 39860 | Normal | 29980.1204 | 0.33055 | 5 | 46307.0154 |  |  |  | 28496.6248 | 0.33055 | 20 | Each | 20260 | 42872.7337 | 49960 | Normal | 37697.5048 | 0.30738 | 5 | 51447.2804 |  |  |  | 36441.8237 | 0.30738 | 20 | Each | 22660 | 45872.7337 | 54160 | Normal | 40896.7545 | 0.30051 | 5 | 55047.2804 |  |  |  | 38991.8237 | 0.30051 | 20 | Each | 22660 | 45872.7337 | 54160 | Normal | 40896.7545 | 0.30051 | 5 | 55047.2804 |  |  |  | 38991.8237 | 0.30051 | 20 | Each | [15 empty] | 9.5691 | 23.5726 | 26.3779 | Normal | 19.84 | 0.41444 | 5 | 30.6444 |  |  |  | 18.8581 | 0.41444 | 20 | Each | 13.4074 | 28.3717 | 33.0618 | Normal | 24.9471 | 0.39621 | 5 | 34.046 |  |  |  | 24.116 | 0.39621 | 20 | Each | 14.9956 | 30.357 | 35.8412 | Normal | 27.0645 | 0.3909 | 5 | 36.4284 |  |  |  | 25.8035 | 0.3909 | 20 | Each | 14.9956 | 30.357 | 35.8412 | Normal | 27.0645 | 0.3909 | 5 | 36.4284 |  |  |  | 25.8035 | 0.3909 | 20 | Each | [15 empty] | 1
| B1033.002c |  | B1033.002c | Special Concentric Braced Frame w WF braces, balanced design criteria, Single Diagonal Brace, Brace w > 100 PLF | 14460 | 35620.7811 | 39860 | Normal | 29980.1204 | 0.33055 | 5 | 46307.0154 |  |  |  | 28496.6248 | 0.33055 | 20 | Each | 24660 | 48374.6864 | 57660 | Normal | 43563.8743 | 0.29555 | 5 | 58049.6236 |  |  |  | 41118.4834 | 0.29555 | 20 | Each | 29060 | 53874.6864 | 65360 | Normal | 49431.3949 | 0.28652 | 5 | 64649.6236 |  |  |  | 45793.4834 | 0.28652 | 20 | Each | 29060 | 53874.6864 | 65360 | Normal | 49431.3949 | 0.28652 | 5 | 64649.6236 |  |  |  | 45793.4834 | 0.28652 | 20 | Each | [15 empty] | 9.5691 | 23.5726 | 26.3779 | Normal | 19.84 | 0.41444 | 5 | 30.6444 |  |  |  | 18.8581 | 0.41444 | 20 | Each | 16.3191 | 32.0127 | 38.1574 | Normal | 28.8295 | 0.38711 | 5 | 38.4152 |  |  |  | 27.2108 | 0.38711 | 20 | Each | 19.2309 | 35.6524 | 43.2529 | Normal | 32.7115 | 0.38025 | 5 | 42.7829 |  |  |  | 30.3045 | 0.38025 | 20 | Each | 19.2309 | 35.6524 | 43.2529 | Normal | 32.7115 | 0.38025 | 5 | 42.7829 |  |  |  | 30.3045 | 0.38025 | 20 | Each | [15 empty] | 1
| B1033.003a |  | B1033.003a | Special Concentric Braced Frame w WF braces, balanced design criteria, X Brace, Brace w < 40 PLF | 15760 | 37221.5621 | 42160 | Normal | 31713.5586 | 0.32478 | 5 | 48388.0308 |  |  |  | 29777.2497 | 0.32478 | 20 | Each | 20160 | 42822.3432 | 49960 | Normal | 37647.4271 | 0.30883 | 5 | 51386.8118 |  |  |  | 36398.9917 | 0.30883 | 20 | Each | 20960 | 43822.3432 | 51360 | Normal | 38714.0252 | 0.30636 | 5 | 52586.8118 |  |  |  | 37248.9917 | 0.30636 | 20 | Each | 20960 | 43822.3432 | 51360 | Normal | 38714.0252 | 0.30636 | 5 | 52586.8118 |  |  |  | 37248.9917 | 0.30636 | 20 | Each | [15 empty] | 10.4294 | 24.6319 | 27.9 | Normal | 20.9866 | 0.40985 | 5 | 32.0215 |  |  |  | 19.7055 | 0.40985 | 20 | Each | 13.3412 | 28.3383 | 33.0618 | Normal | 24.9139 | 0.39733 | 5 | 34.006 |  |  |  | 24.0876 | 0.39733 | 20 | Each | 13.8706 | 29.0001 | 33.9882 | Normal | 25.6198 | 0.39542 | 5 | 34.8001 |  |  |  | 24.6501 | 0.39542 | 20 | Each | 13.8706 | 29.0001 | 33.9882 | Normal | 25.6198 | 0.39542 | 5 | 34.8001 |  |  |  | 24.6501 | 0.39542 | 20 | Each | [15 empty] | 1
| B1033.003b |  | B1033.003b | Special Concentric Braced Frame w WF braces, balanced design criteria, X Brace, 41 PLF < w < 99 PLF | 15760 | 37221.5621 | 42160 | Normal | 31713.5586 | 0.32478 | 5 | 48388.0308 |  |  |  | 29777.2497 | 0.32478 | 20 | Each | 28360 | 52975.4674 | 64160 | Normal | 48498.1287 | 0.28801 | 5 | 63570.5609 |  |  |  | 45029.1473 | 0.28801 | 20 | Each | 30760 | 55975.4674 | 68360 | Normal | 51698.1679 | 0.28376 | 5 | 67170.5609 |  |  |  | 47579.1473 | 0.28376 | 20 | Each | 30760 | 55975.4674 | 68360 | Normal | 51698.1679 | 0.28376 | 5 | 67170.5609 |  |  |  | 47579.1473 | 0.28376 | 20 | Each | [15 empty] | 10.4294 | 24.6319 | 27.9 | Normal | 20.9866 | 0.40985 | 5 | 32.0215 |  |  |  | 19.7055 | 0.40985 | 20 | Each | 18.7676 | 35.0573 | 42.4588 | Normal | 32.0941 | 0.38138 | 5 | 42.0688 |  |  |  | 29.7987 | 0.38138 | 20 | Each | 20.3559 | 37.0426 | 45.2382 | Normal | 34.2117 | 0.37818 | 5 | 44.4511 |  |  |  | 31.4862 | 0.37818 | 20 | Each | 20.3559 | 37.0426 | 45.2382 | Normal | 34.2117 | 0.37818 | 5 | 44.4511 |  |  |  | 31.4862 | 0.37818 | 20 | Each | [15 empty] | 1
| B1033.003c |  | B1033.003c | Special Concentric Braced Frame w WF braces, balanced design criteria, X Brace, Brace w > 100 PLF | 15760 | 37221.5621 | 42160 | Normal | 31713.5586 | 0.32478 | 5 | 48388.0308 |  |  |  | 29777.2497 | 0.32478 | 20 | Each | 38360 | 65479.3727 | 81660 | Normal | 61833.0926 | 0.27321 | 5 | 78575.2473 |  |  |  | 55657.4668 | 0.27321 | 20 | Each | 42760 | 70979.3727 | 89360 | Normal | 67699.7562 | 0.26855 | 5 | 85175.2473 |  |  |  | 60332.4668 | 0.26855 | 20 | Each | 42760 | 70979.3727 | 89360 | Normal | 67699.7562 | 0.26855 | 5 | 85175.2473 |  |  |  | 60332.4668 | 0.26855 | 20 | Each | [15 empty] | 10.4294 | 24.6319 | 27.9 | Normal | 20.9866 | 0.40985 | 5 | 32.0215 |  |  |  | 19.7055 | 0.40985 | 20 | Each | 25.3853 | 43.3319 | 54.0397 | Normal | 40.9189 | 0.37033 | 5 | 51.9983 |  |  |  | 36.8321 | 0.37033 | 20 | Each | 28.2971 | 46.9716 | 59.1353 | Normal | 44.8013 | 0.36691 | 5 | 56.3659 |  |  |  | 39.9259 | 0.36691 | 20 | Each | 28.2971 | 46.9716 | 59.1353 | Normal | 44.8013 | 0.36691 | 5 | 56.3659 |  |  |  | 39.9259 | 0.36691 | 20 | Each | [15 empty] | 1
| B1033.011a |  | B1033.011a | Special Concentric Braced Frame w HSS braces, balanced design criteria, Chevron Brace, Brace w < 40 PLF | 14460 | 35628.4953 | 39860 | Normal | 29982.6924 | 0.33052 | 5 | 46317.0439 |  |  |  | 28502.7962 | 0.33052 | 20 | Each | 17960 | 40022.8401 | 45960 | Normal | 34647.587 | 0.3153 | 5 | 48027.4081 |  |  |  | 34019.4141 | 0.3153 | 20 | Each | 19360 | 41722.8401 | 48360 | Normal | 36480.9219 | 0.31015 | 5 | 50067.4081 |  |  |  | 35464.4141 | 0.31015 | 20 | Each | 19360 | 41722.8401 | 48360 | Normal | 36480.9219 | 0.31015 | 5 | 50067.4081 |  |  |  | 35464.4141 | 0.31015 | 20 | Each | [15 empty] | 9.5691 | 23.5777 | 26.3779 | Normal | 19.8417 | 0.41442 | 5 | 30.651 |  |  |  | 18.8622 | 0.41442 | 20 | Each | 11.8853 | 26.4857 | 30.4147 | Normal | 22.9286 | 0.40238 | 5 | 31.7828 |  |  |  | 22.5128 | 0.40238 | 20 | Each | 12.8118 | 27.6107 | 32.0029 | Normal | 24.142 | 0.39836 | 5 | 33.1328 |  |  |  | 23.4691 | 0.39836 | 20 | Each | 12.8118 | 27.6107 | 32.0029 | Normal | 24.142 | 0.39836 | 5 | 33.1328 |  |  |  | 23.4691 | 0.39836 | 20 | Each | [15 empty] | 1
| B1033.011b |  | B1033.011b | Special Concentric Braced Frame w HSS braces, balanced design criteria, Chevron Brace, Brace 41 PLF < w < 99 PLF | 14460 | 35628.4953 | 39860 | Normal | 29982.6924 | 0.33052 | 5 | 46317.0439 |  |  |  | 28502.7962 | 0.33052 | 20 | Each | 25060 | 48926.6269 | 58460 | Normal | 44147.8802 | 0.29518 | 5 | 58711.9523 |  |  |  | 41587.6329 | 0.29518 | 20 | Each | 27860 | 52426.6269 | 63360 | Normal | 47881.8231 | 0.28927 | 5 | 62911.9523 |  |  |  | 44562.6329 | 0.28927 | 20 | Each | 27860 | 52426.6269 | 63360 | Normal | 47881.8231 | 0.28927 | 5 | 62911.9523 |  |  |  | 44562.6329 | 0.28927 | 20 | Each | [15 empty] | 9.5691 | 23.5777 | 26.3779 | Normal | 19.8417 | 0.41442 | 5 | 30.651 |  |  |  | 18.8622 | 0.41442 | 20 | Each | 16.5838 | 32.3779 | 38.6868 | Normal | 29.2159 | 0.38682 | 5 | 38.8535 |  |  |  | 27.5212 | 0.38682 | 20 | Each | 18.4368 | 34.6941 | 41.9294 | Normal | 31.6862 | 0.38233 | 5 | 41.6329 |  |  |  | 29.49 | 0.38233 | 20 | Each | 18.4368 | 34.6941 | 41.9294 | Normal | 31.6862 | 0.38233 | 5 | 41.6329 |  |  |  | 29.49 | 0.38233 | 20 | Each | [15 empty] | 1
| B1033.011c |  | B1033.011c | Special Concentric Braced Frame w HSS braces, balanced design criteria, Chevron Brace, Brace w > 100 PLF | 14460 | 35628.4953 | 39860 | Normal | 29982.6924 | 0.33052 | 5 | 42754.1943 |  |  |  | 28502.7962 | 0.33052 | 20 | Each | 33960 | 60081.3604 | 74060 | Normal | 56033.787 | 0.27921 | 5 | 72097.6325 |  |  |  | 48065.0883 | 0.27921 | 20 | Each | 37960 | 65081.3604 | 81060 | Normal | 61367.0888 | 0.27402 | 5 | 78097.6325 |  |  |  | 52065.0883 | 0.27402 | 20 | Each | 37960 | 65081.3604 | 81060 | Normal | 61367.0888 | 0.27402 | 5 | 78097.6325 |  |  |  | 52065.0883 | 0.27402 | 20 | Each | [15 empty] | 9.5691 | 23.5777 | 26.3779 | Normal | 19.8417 | 0.41442 | 5 | 28.2932 |  |  |  | 18.8622 | 0.41442 | 20 | Each | 22.4735 | 39.7597 | 49.0103 | Normal | 37.081 | 0.37478 | 5 | 47.7116 |  |  |  | 31.8078 | 0.37478 | 20 | Each | 25.1206 | 43.0685 | 53.6426 | Normal | 40.6105 | 0.37092 | 5 | 51.6822 |  |  |  | 34.4548 | 0.37092 | 20 | Each | 25.1206 | 43.0685 | 53.6426 | Normal | 40.6105 | 0.37092 | 5 | 51.6822 |  |  |  | 34.4548 | 0.37092 | 20 | Each | [15 empty] | 1
| B1033.012a |  | B1033.012a | Special Concentric Braced Frame w HSS braces, balanced design criteria, Single Diagonal Brace, Brace w < 40 PLF | 13860 | 34870.7811 | 38760 | Normal | 29163.4555 | 0.33311 | 5 | 41844.9373 |  |  |  | 27896.6248 | 0.33311 | 20 | Each | 16860 | 38631.6402 | 44060 | Normal | 33183.643 | 0.3198 | 5 | 46357.9683 |  |  |  | 30905.3122 | 0.3198 | 20 | Each | 17660 | 39631.6402 | 45460 | Normal | 34250.4998 | 0.31667 | 5 | 47557.9683 |  |  |  | 31705.3122 | 0.31667 | 20 | Each | 17660 | 39631.6402 | 45460 | Normal | 34250.4998 | 0.31667 | 5 | 47557.9683 |  |  |  | 31705.3122 | 0.31667 | 20 | Each | [15 empty] | 9.1721 | 23.0763 | 25.65 | Normal | 19.2999 | 0.41649 | 5 | 27.6916 |  |  |  | 18.461 | 0.41649 | 20 | Each | 11.1574 | 25.5651 | 29.1574 | Normal | 21.9593 | 0.40592 | 5 | 30.6781 |  |  |  | 20.4521 | 0.40592 | 20 | Each | 11.6868 | 26.2268 | 30.0838 | Normal | 22.6658 | 0.40346 | 5 | 31.4722 |  |  |  | 20.9814 | 0.40346 | 20 | Each | 11.6868 | 26.2268 | 30.0838 | Normal | 22.6658 | 0.40346 | 5 | 31.4722 |  |  |  | 20.9814 | 0.40346 | 20 | Each | [15 empty] | 1
| B1033.012b |  | B1033.012b | Special Concentric Braced Frame w HSS braces, balanced design criteria, Single Diagonal Brace, Brace 41 PLF < w < 99 PLF | 13860 | 34870.7811 | 38760 | Normal | 29163.4555 | 0.33311 | 5 | 41844.9373 |  |  |  | 27896.6248 | 0.33311 | 20 | Each | 21160 | 44013.8272 | 51660 | Normal | 38944.5382 | 0.30555 | 5 | 52816.5926 |  |  |  | 35211.0618 | 0.30555 | 20 | Each | 23960 | 47513.8272 | 56560 | Normal | 42677.128 | 0.29803 | 5 | 57016.5926 |  |  |  | 38011.0618 | 0.29803 | 20 | Each | 23960 | 47513.8272 | 56560 | Normal | 42677.128 | 0.29803 | 5 | 57016.5926 |  |  |  | 38011.0618 | 0.29803 | 20 | Each | [15 empty] | 9.1721 | 23.0763 | 25.65 | Normal | 19.2999 | 0.41649 | 5 | 27.6916 |  |  |  | 18.461 | 0.41649 | 20 | Each | 14.0029 | 29.1268 | 34.1868 | Normal | 25.7723 | 0.39479 | 5 | 34.9522 |  |  |  | 23.3014 | 0.39479 | 20 | Each | 15.8559 | 31.443 | 37.4294 | Normal | 28.2425 | 0.389 | 5 | 37.7316 |  |  |  | 25.1544 | 0.389 | 20 | Each | 15.8559 | 31.443 | 37.4294 | Normal | 28.2425 | 0.389 | 5 | 37.7316 |  |  |  | 25.1544 | 0.389 | 20 | Each | [15 empty] | 1
| B1033.012c |  | B1033.012c | Special Concentric Braced Frame w HSS braces, balanced design criteria, Single Diagonal Brace, Brace w > 100 PLF | 13860 | 34870.7811 | 38760 | Normal | 29163.4555 | 0.33311 | 5 | 41844.9373 |  |  |  | 27896.6248 | 0.33311 | 20 | Each | 26960 | 51216.5609 | 61660 | Normal | 46611.9613 | 0.29046 | 5 | 61459.8731 |  |  |  | 40973.2487 | 0.29046 | 20 | Each | 31360 | 56716.5609 | 69360 | Normal | 52478.3218 | 0.28252 | 5 | 68059.8731 |  |  |  | 45373.2487 | 0.28252 | 20 | Each | 31360 | 56716.5609 | 69360 | Normal | 52478.3218 | 0.28252 | 5 | 68059.8731 |  |  |  | 45373.2487 | 0.28252 | 20 | Each | [15 empty] | 9.1721 | 23.0763 | 25.65 | Normal | 19.2999 | 0.41649 | 5 | 27.6916 |  |  |  | 18.461 | 0.41649 | 20 | Each | 17.8412 | 33.8933 | 40.8044 | Normal | 30.8457 | 0.38323 | 5 | 40.672 |  |  |  | 27.1146 | 0.38323 | 20 | Each | 20.7529 | 37.533 | 45.9 | Normal | 34.7281 | 0.37725 | 5 | 45.0396 |  |  |  | 30.0264 | 0.37725 | 20 | Each | 20.7529 | 37.533 | 45.9 | Normal | 34.7281 | 0.37725 | 5 | 45.0396 |  |  |  | 30.0264 | 0.37725 | 20 | Each | [15 empty] | 1
| B1033.013a |  | B1033.013a | Special Concentric Braced Frame w HSS braces, balanced design criteria, X Brace, Brace w < 40 PLF | 15160 | 36471.5621 | 41060 | Normal | 30897.003 | 0.32705 | 5 | 43765.8745 |  |  |  | 29177.2497 | 0.32705 | 20 | Each | 20360 | 42993.2804 | 50160 | Normal | 37837.6809 | 0.30727 | 5 | 51591.9365 |  |  |  | 34394.6244 | 0.30727 | 20 | Each | 21560 | 44493.2804 | 52260 | Normal | 39437.7035 | 0.30371 | 5 | 53391.9365 |  |  |  | 35594.6244 | 0.30371 | 20 | Each | 21560 | 44493.2804 | 52260 | Normal | 39437.7035 | 0.30371 | 5 | 53391.9365 |  |  |  | 35594.6244 | 0.30371 | 20 | Each | [15 empty] | 10.0324 | 24.1356 | 27.1721 | Normal | 20.4465 | 0.41166 | 5 | 28.9627 |  |  |  | 19.3085 | 0.41166 | 20 | Each | 13.4735 | 28.4514 | 33.1941 | Normal | 25.0398 | 0.39613 | 5 | 34.1417 |  |  |  | 22.7611 | 0.39613 | 20 | Each | 14.2676 | 29.4441 | 34.5838 | Normal | 26.0986 | 0.39337 | 5 | 35.3329 |  |  |  | 23.5553 | 0.39337 | 20 | Each | 14.2676 | 29.4441 | 34.5838 | Normal | 26.0986 | 0.39337 | 5 | 35.3329 |  |  |  | 23.5553 | 0.39337 | 20 | Each | [15 empty] | 1
| B1033.013b |  | B1033.013b | Special Concentric Braced Frame w HSS braces, balanced design criteria, X Brace, Brace 41 PLF < w < 99 PLF | 15160 | 36471.5621 | 41060 | Normal | 30897.003 | 0.32705 | 5 | 43765.8745 |  |  |  | 29177.2497 | 0.32705 | 20 | Each | 30360 | 55457.6544 | 67660 | Normal | 51158.8551 | 0.28447 | 5 | 66549.1853 |  |  |  | 44366.1235 | 0.28447 | 20 | Each | 33160 | 58957.6544 | 72560 | Normal | 54891.7166 | 0.28004 | 5 | 70749.1853 |  |  |  | 47166.1235 | 0.28004 | 20 | Each | 33160 | 58957.6544 | 72560 | Normal | 54891.7166 | 0.28004 | 5 | 70749.1853 |  |  |  | 47166.1235 | 0.28004 | 20 | Each | [15 empty] | 10.0324 | 24.1356 | 27.1721 | Normal | 20.4465 | 0.41166 | 5 | 28.9627 |  |  |  | 19.3085 | 0.41166 | 20 | Each | 20.0912 | 36.6999 | 44.775 | Normal | 33.8548 | 0.37871 | 5 | 44.0399 |  |  |  | 29.3599 | 0.37871 | 20 | Each | 21.9441 | 39.0161 | 48.0176 | Normal | 36.3255 | 0.37539 | 5 | 46.8193 |  |  |  | 31.2129 | 0.37539 | 20 | Each | 21.9441 | 39.0161 | 48.0176 | Normal | 36.3255 | 0.37539 | 5 | 46.8193 |  |  |  | 31.2129 | 0.37539 | 20 | Each | [15 empty] | 1
| B1033.013c |  | B1033.013c | Special Concentric Braced Frame w HSS braces, balanced design criteria, X Brace, Brace w > 100 PLF | 15160 | 36471.5621 | 41060 | Normal | 30897.003 | 0.32705 | 5 | 43765.8745 |  |  |  | 29177.2497 | 0.32705 | 20 | Each | 42460 | 70663.1218 | 88960 | Normal | 67361.006 | 0.26933 | 5 | 84795.7462 |  |  |  | 56530.4974 | 0.26933 | 20 | Each | 46860 | 76163.1218 | 96660 | Normal | 73227.67 | 0.26533 | 5 | 91395.7462 |  |  |  | 60930.4974 | 0.26533 | 20 | Each | 46860 | 76163.1218 | 96660 | Normal | 73227.67 | 0.26533 | 5 | 91395.7462 |  |  |  | 60930.4974 | 0.26533 | 20 | Each | [15 empty] | 10.0324 | 24.1356 | 27.1721 | Normal | 20.4465 | 0.41166 | 5 | 28.9627 |  |  |  | 19.3085 | 0.41166 | 20 | Each | 28.0985 | 46.7624 | 58.8706 | Normal | 44.5771 | 0.36747 | 5 | 56.1149 |  |  |  | 37.4099 | 0.36747 | 20 | Each | 31.0103 | 50.4021 | 63.9662 | Normal | 48.4595 | 0.36456 | 5 | 60.4825 |  |  |  | 40.3217 | 0.36456 | 20 | Each | 31.0103 | 50.4021 | 63.9662 | Normal | 48.4595 | 0.36456 | 5 | 60.4825 |  |  |  | 40.3217 | 0.36456 | 20 | Each | [15 empty] | 1
| B1033.021a |  | B1033.021a | Special Concentric Braced Frame w HSS braces, tapered gusset plates & design to AISC minimum standard, Chevron Brace, Brace w < 40 PLF | 14860 | 36078.4953 | 40460 | Normal | 30465.9341 | 0.32783 | 5 | 43294.1943 |  |  |  | 28862.7962 | 0.32783 | 20 | Each | 18360 | 40472.8401 | 46560 | Normal | 35130.8219 | 0.31318 | 5 | 48567.4081 |  |  |  | 32378.2721 | 0.31318 | 20 | Each | 19760 | 42172.8401 | 48960 | Normal | 36964.2121 | 0.3082 | 5 | 50607.4081 |  |  |  | 33738.2721 | 0.3082 | 20 | Each | 19760 | 42172.8401 | 48960 | Normal | 36964.2121 | 0.3082 | 5 | 50607.4081 |  |  |  | 33738.2721 | 0.3082 | 20 | Each | [15 empty] | 9.8338 | 23.8755 | 26.775 | Normal | 20.1615 | 0.41228 | 5 | 28.6506 |  |  |  | 19.1004 | 0.41228 | 20 | Each | 12.15 | 26.7835 | 30.8118 | Normal | 23.2484 | 0.40072 | 5 | 32.1402 |  |  |  | 21.4268 | 0.40072 | 20 | Each | 13.0765 | 27.9085 | 32.4 | Normal | 24.4619 | 0.39685 | 5 | 33.4902 |  |  |  | 22.3268 | 0.39685 | 20 | Each | 13.0765 | 27.9085 | 32.4 | Normal | 24.4619 | 0.39685 | 5 | 33.4902 |  |  |  | 22.3268 | 0.39685 | 20 | Each | [15 empty] | 1
| B1033.021b |  | B1033.021b | Special Concentric Braced Frame w HSS braces, tapered gusset plates & design to AISC minimum standard, Chevron Brace, Brace 41 PLF < w < 99 PLF | 14860 | 36078.4953 | 40460 | Normal | 30465.9341 | 0.32783 | 5 | 43294.1943 |  |  |  | 28862.7962 | 0.32783 | 20 | Each | 25760 | 49826.6269 | 59760 | Normal | 45114.4675 | 0.29404 | 5 | 59791.9523 |  |  |  | 39861.3015 | 0.29404 | 20 | Each | 28560 | 53326.6269 | 64660 | Normal | 48848.636 | 0.28834 | 5 | 63991.9523 |  |  |  | 42661.3015 | 0.28834 | 20 | Each | 28560 | 53326.6269 | 64660 | Normal | 48848.636 | 0.28834 | 5 | 63991.9523 |  |  |  | 42661.3015 | 0.28834 | 20 | Each | [15 empty] | 9.8338 | 23.8755 | 26.775 | Normal | 20.1615 | 0.41228 | 5 | 28.6506 |  |  |  | 19.1004 | 0.41228 | 20 | Each | 17.0471 | 32.9735 | 39.5471 | Normal | 29.8553 | 0.38595 | 5 | 39.5682 |  |  |  | 26.3788 | 0.38595 | 20 | Each | 18.9 | 35.2897 | 42.7897 | Normal | 32.326 | 0.38163 | 5 | 42.3476 |  |  |  | 28.2318 | 0.38163 | 20 | Each | 18.9 | 35.2897 | 42.7897 | Normal | 32.326 | 0.38163 | 5 | 42.3476 |  |  |  | 28.2318 | 0.38163 | 20 | Each | [15 empty] | 1
| B1033.021c |  | B1033.021c | Special Concentric Braced Frame w HSS braces, tapered gusset plates & design to AISC minimum standard, Chevron Brace, Brace w > 100 PLF | 14860 | 36078.4953 | 40460 | Normal | 30465.9341 | 0.32783 | 5 | 43294.1943 |  |  |  | 28862.7962 | 0.32783 | 20 | Each | 34660 | 60981.3604 | 75360 | Normal | 56999.7427 | 0.27857 | 5 | 73177.6325 |  |  |  | 48785.0883 | 0.27857 | 20 | Each | 38660 | 65981.3604 | 82360 | Normal | 62333.755 | 0.27352 | 5 | 79177.6325 |  |  |  | 52785.0883 | 0.27352 | 20 | Each | 38660 | 65981.3604 | 82360 | Normal | 62333.755 | 0.27352 | 5 | 79177.6325 |  |  |  | 52785.0883 | 0.27352 | 20 | Each | [15 empty] | 9.8338 | 23.8755 | 26.775 | Normal | 20.1615 | 0.41228 | 5 | 28.6506 |  |  |  | 19.1004 | 0.41228 | 20 | Each | 22.9368 | 40.3553 | 49.8706 | Normal | 37.7209 | 0.3743 | 5 | 48.4264 |  |  |  | 32.2842 | 0.3743 | 20 | Each | 25.5838 | 43.6641 | 54.5029 | Normal | 41.2502 | 0.37056 | 5 | 52.3969 |  |  |  | 34.9313 | 0.37056 | 20 | Each | 25.5838 | 43.6641 | 54.5029 | Normal | 41.2502 | 0.37056 | 5 | 52.3969 |  |  |  | 34.9313 | 0.37056 | 20 | Each | [15 empty] | 1
| B1033.022a |  | B1033.022a | Special Concentric Braced Frame w HSS braces, tapered gusset plates & design to AISC minimum standard Single Diagonal Brace, Brace w < 40 PLF | 14260 | 35320.7811 | 39360 | Normal | 29646.8005 | 0.33031 | 5 | 42384.9373 |  |  |  | 28256.6248 | 0.33031 | 20 | Each | 17260 | 39081.6402 | 44660 | Normal | 33667.1706 | 0.31752 | 5 | 46897.9683 |  |  |  | 31265.3122 | 0.31752 | 20 | Each | 17860 | 39931.6402 | 45860 | Normal | 34550.4963 | 0.31618 | 5 | 47917.9683 |  |  |  | 31945.3122 | 0.31618 | 20 | Each | 17860 | 39931.6402 | 45860 | Normal | 34550.4963 | 0.31618 | 5 | 47917.9683 |  |  |  | 31945.3122 | 0.31618 | 20 | Each | [15 empty] | 9.4368 | 23.374 | 26.0471 | Normal | 19.6196 | 0.41426 | 5 | 28.0488 |  |  |  | 18.6992 | 0.41426 | 20 | Each | 11.4221 | 25.8629 | 29.5544 | Normal | 22.2791 | 0.40413 | 5 | 31.0355 |  |  |  | 20.6903 | 0.40413 | 20 | Each | 11.8191 | 26.4254 | 30.3485 | Normal | 22.8643 | 0.40308 | 5 | 31.7105 |  |  |  | 21.1403 | 0.40308 | 20 | Each | 11.8191 | 26.4254 | 30.3485 | Normal | 22.8643 | 0.40308 | 5 | 31.7105 |  |  |  | 21.1403 | 0.40308 | 20 | Each | [15 empty] | 1
| B1033.022b |  | B1033.022b | Special Concentric Braced Frame w HSS braces, tapered gusset plates & design to AISC minimum standard, Single Diagonal Brace, Brace 41 PLF < w < 99 PLF | 14260 | 35320.7811 | 39360 | Normal | 29646.8005 | 0.33031 | 5 | 42384.9373 |  |  |  | 28256.6248 | 0.33031 | 20 | Each | 21660 | 44613.8272 | 52460 | Normal | 39577.9227 | 0.30362 | 5 | 53536.5926 |  |  |  | 35691.0618 | 0.30362 | 20 | Each | 24460 | 48113.8272 | 57360 | Normal | 43311.1583 | 0.29637 | 5 | 57736.5926 |  |  |  | 38491.0618 | 0.29637 | 20 | Each | 24460 | 48113.8272 | 57360 | Normal | 43311.1583 | 0.29637 | 5 | 57736.5926 |  |  |  | 38491.0618 | 0.29637 | 20 | Each | [15 empty] | 9.4368 | 23.374 | 26.0471 | Normal | 19.6196 | 0.41426 | 5 | 28.0488 |  |  |  | 18.6992 | 0.41426 | 20 | Each | 14.3338 | 29.5239 | 34.7162 | Normal | 26.1914 | 0.3933 | 5 | 35.4287 |  |  |  | 23.6191 | 0.3933 | 20 | Each | 16.1868 | 31.84 | 37.9588 | Normal | 28.6615 | 0.38773 | 5 | 38.208 |  |  |  | 25.472 | 0.38773 | 20 | Each | 16.1868 | 31.84 | 37.9588 | Normal | 28.6615 | 0.38773 | 5 | 38.208 |  |  |  | 25.472 | 0.38773 | 20 | Each | [15 empty] | 1
| B1033.022c |  | B1033.022c | Special Concentric Braced Frame w HSS braces, tapered gusset plates & design to AISC minimum standard, Single Diagonal Brace, Brace w > 100 PLF | 14260 | 35320.7811 | 39360 | Normal | 29646.8005 | 0.33031 | 5 | 42384.9373 |  |  |  | 28256.6248 | 0.33031 | 20 | Each | 27460 | 51816.5609 | 62460 | Normal | 47245.3371 | 0.28904 | 5 | 62179.8731 |  |  |  | 41453.2487 | 0.28904 | 20 | Each | 31860 | 57316.5609 | 70160 | Normal | 53112.1405 | 0.28134 | 5 | 68779.8731 |  |  |  | 45853.2487 | 0.28134 | 20 | Each | 31860 | 57316.5609 | 70160 | Normal | 53112.1405 | 0.28134 | 5 | 68779.8731 |  |  |  | 45853.2487 | 0.28134 | 20 | Each | [15 empty] | 9.4368 | 23.374 | 26.0471 | Normal | 19.6196 | 0.41426 | 5 | 28.0488 |  |  |  | 18.6992 | 0.41426 | 20 | Each | 18.1721 | 34.2904 | 41.3338 | Normal | 31.2649 | 0.38216 | 5 | 41.1485 |  |  |  | 27.4323 | 0.38216 | 20 | Each | 21.0838 | 37.9301 | 46.4294 | Normal | 35.1473 | 0.37637 | 5 | 45.5161 |  |  |  | 30.3441 | 0.37637 | 20 | Each | 21.0838 | 37.9301 | 46.4294 | Normal | 35.1473 | 0.37637 | 5 | 45.5161 |  |  |  | 30.3441 | 0.37637 | 20 | Each | [15 empty] | 1
| B1033.023a |  | B1033.023a | Special Concentric Braced Frame w HSS braces, tapered gusset plates & design to AISC minimum standard, X Brace, Brace w < 40 PLF | 15560 | 36921.5621 | 41660 | Normal | 31380.4407 | 0.3245 | 5 | 44305.8745 |  |  |  | 29537.2497 | 0.3245 | 20 | Each | 20960 | 43743.2804 | 51260 | Normal | 38654.362 | 0.30583 | 5 | 52491.9365 |  |  |  | 34994.6244 | 0.30583 | 20 | Each | 22160 | 45243.2804 | 53360 | Normal | 40254.0168 | 0.3024 | 5 | 54291.9365 |  |  |  | 36194.6244 | 0.3024 | 20 | Each | 22160 | 45243.2804 | 53360 | Normal | 40254.0168 | 0.3024 | 5 | 54291.9365 |  |  |  | 36194.6244 | 0.3024 | 20 | Each | [15 empty] | 10.2971 | 24.4334 | 27.5691 | Normal | 20.7662 | 0.40963 | 5 | 29.3201 |  |  |  | 19.5467 | 0.40963 | 20 | Each | 13.8706 | 28.9478 | 33.9221 | Normal | 25.5803 | 0.39501 | 5 | 34.7374 |  |  |  | 23.1582 | 0.39501 | 20 | Each | 14.6647 | 29.9404 | 35.3118 | Normal | 26.6389 | 0.39236 | 5 | 35.9285 |  |  |  | 23.9523 | 0.39236 | 20 | Each | 14.6647 | 29.9404 | 35.3118 | Normal | 26.6389 | 0.39236 | 5 | 35.9285 |  |  |  | 23.9523 | 0.39236 | 20 | Each | [15 empty] | 1
| B1033.023b |  | B1033.023b | Special Concentric Braced Frame w HSS braces, tapered gusset plates & design to AISC minimum standard, X Brace, Brace 41 PLF < w < 99 PLF | 15560 | 36921.5621 | 41660 | Normal | 31380.4407 | 0.3245 | 5 | 44305.8745 |  |  |  | 29537.2497 | 0.3245 | 20 | Each | 31560 | 56957.6544 | 69760 | Normal | 52758.3062 | 0.28249 | 5 | 68349.1853 |  |  |  | 45566.1235 | 0.28249 | 20 | Each | 34360 | 60457.6544 | 74660 | Normal | 56492.6773 | 0.27831 | 5 | 72549.1853 |  |  |  | 48366.1235 | 0.27831 | 20 | Each | 34360 | 60457.6544 | 74660 | Normal | 56492.6773 | 0.27831 | 5 | 72549.1853 |  |  |  | 48366.1235 | 0.27831 | 20 | Each | [15 empty] | 10.2971 | 24.4334 | 27.5691 | Normal | 20.7662 | 0.40963 | 5 | 29.3201 |  |  |  | 19.5467 | 0.40963 | 20 | Each | 20.8853 | 37.6926 | 46.1647 | Normal | 34.9137 | 0.37723 | 5 | 45.2311 |  |  |  | 30.1541 | 0.37723 | 20 | Each | 22.7382 | 40.0087 | 49.4074 | Normal | 37.3846 | 0.37411 | 5 | 48.0104 |  |  |  | 32.007 | 0.37411 | 20 | Each | 22.7382 | 40.0087 | 49.4074 | Normal | 37.3846 | 0.37411 | 5 | 48.0104 |  |  |  | 32.007 | 0.37411 | 20 | Each | [15 empty] | 1
| B1033.023c |  | B1033.023c | Special Concentric Braced Frame w HSS braces, tapered gusset plates & design to AISC minimum standard, X Brace, Brace w > 100 PLF | 15560 | 36921.5621 | 41660 | Normal | 31380.4407 | 0.3245 | 3 | 40613.7183 |  |  |  | 33229.4059 | 0.3245 | 10 | Each | 43660 | 72163.1218 | 91060 | Normal | 68961.0052 | 0.26817 | 3 | 79379.434 |  |  |  | 64946.8096 | 0.26817 | 10 | Each | 48060 | 77663.1218 | 98760 | Normal | 74827.669 | 0.26435 | 3 | 85429.434 |  |  |  | 69896.8096 | 0.26435 | 10 | Each | 48060 | 77663.1218 | 98760 | Normal | 74827.669 | 0.26435 | 3 | 85429.434 |  |  |  | 69896.8096 | 0.26435 | 10 | Each | [15 empty] | 10.2971 | 24.4334 | 27.5691 | Normal | 20.7662 | 0.40963 | 3 | 26.8767 |  |  |  | 21.9901 | 0.40963 | 10 | Each | 28.8926 | 47.755 | 60.2603 | Normal | 45.6359 | 0.36663 | 3 | 52.5305 |  |  |  | 42.9795 | 0.36663 | 10 | Each | 31.8044 | 51.3947 | 65.3559 | Normal | 49.5183 | 0.36384 | 3 | 56.5342 |  |  |  | 46.2552 | 0.36384 | 10 | Each | 31.8044 | 51.3947 | 65.3559 | Normal | 49.5183 | 0.36384 | 3 | 56.5342 |  |  |  | 46.2552 | 0.36384 | 10 | Each | [15 empty] | 1
| B1033.031a |  | B1033.031a | Special Concentric Braced Frame, design to AISC minimum standards, Chevron Brace, Brace w < 40 PLF | 14860 | 36078.4953 | 40460 | Normal | 30465.9341 | 0.32783 | 3 | 39686.3448 |  |  |  | 32470.6458 | 0.32783 | 10 | Each | 18360 | 40472.8401 | 46560 | Normal | 35130.8219 | 0.31318 | 3 | 44520.1241 |  |  |  | 36425.5561 | 0.31318 | 10 | Each | 19760 | 42172.8401 | 48960 | Normal | 36964.2121 | 0.3082 | 3 | 46390.1241 |  |  |  | 37955.5561 | 0.3082 | 10 | Each | [30 empty] | 9.8338 | 23.8755 | 26.775 | Normal | 20.1615 | 0.41228 | 3 | 26.263 |  |  |  | 21.488 | 0.41228 | 10 | Each | 12.15 | 26.7835 | 30.8118 | Normal | 23.2484 | 0.40072 | 3 | 29.4618 |  |  |  | 24.1052 | 0.40072 | 10 | Each | 13.0765 | 27.9085 | 32.4 | Normal | 24.4619 | 0.39685 | 3 | 30.6993 |  |  |  | 25.1177 | 0.39685 | 10 | Each | [30 empty] | 1
| B1033.031b |  | B1033.031b | Special Concentric Braced Frame, design to AISC minimum standards, Chevron Brace, Brace 41 PLF < w < 99 PLF | 14860 | 36078.4953 | 40460 | Normal | 30465.9341 | 0.32783 | 3 | 39686.3448 |  |  |  | 32470.6458 | 0.32783 | 10 | Each | 25760 | 49826.6269 | 59760 | Normal | 45114.4675 | 0.29404 | 3 | 54809.2896 |  |  |  | 44843.9642 | 0.29404 | 10 | Each | 28560 | 53326.6269 | 64660 | Normal | 48848.636 | 0.28834 | 3 | 58659.2896 |  |  |  | 47993.9642 | 0.28834 | 10 | Each | [30 empty] | 9.8338 | 23.8755 | 26.775 | Normal | 20.1615 | 0.41228 | 3 | 26.263 |  |  |  | 21.488 | 0.41228 | 10 | Each | 17.0471 | 32.9735 | 39.5471 | Normal | 29.8553 | 0.38595 | 3 | 36.2709 |  |  |  | 29.6761 | 0.38595 | 10 | Each | 18.9 | 35.2897 | 42.7897 | Normal | 32.326 | 0.38163 | 3 | 38.8187 |  |  |  | 31.7607 | 0.38163 | 10 | Each | [30 empty] | 1
| B1033.031c |  | B1033.031c | Special Concentric Braced Frame, design to AISC minimum standards, Chevron Brace, Brace w > 100 PLF | 14860 | 36078.4953 | 40460 | Normal | 30465.9341 | 0.32783 | 3 | 39686.3448 |  |  |  | 32470.6458 | 0.32783 | 10 | Each | 34660 | 60981.3604 | 75360 | Normal | 56999.7427 | 0.27857 | 3 | 67079.4964 |  |  |  | 54883.2243 | 0.27857 | 10 | Each | 38660 | 65981.3604 | 82360 | Normal | 62333.755 | 0.27352 | 3 | 72579.4964 |  |  |  | 59383.2243 | 0.27352 | 10 | Each | [30 empty] | 9.8338 | 23.8755 | 26.775 | Normal | 20.1615 | 0.41228 | 3 | 26.263 |  |  |  | 21.488 | 0.41228 | 10 | Each | 22.9368 | 40.3553 | 49.8706 | Normal | 37.7209 | 0.3743 | 3 | 44.3908 |  |  |  | 36.3198 | 0.3743 | 10 | Each | 25.5838 | 43.6641 | 54.5029 | Normal | 41.2502 | 0.37056 | 3 | 48.0305 |  |  |  | 39.2977 | 0.37056 | 10 | Each | [30 empty] | 1
| B1033.032a |  | B1033.032a | Special Concentric Braced Frame, design to AISC minimum standards, Single Diagonal Brace, Brace w < 40 PLF | 14260 | 35320.7811 | 39360 | Normal | 29646.8005 | 0.33031 | 3 | 38852.8592 |  |  |  | 31788.703 | 0.33031 | 10 | Each | 17260 | 39081.6402 | 44660 | Normal | 33667.1706 | 0.31752 | 3 | 42989.8042 |  |  |  | 35173.4762 | 0.31752 | 10 | Each | 17860 | 39931.6402 | 45860 | Normal | 34550.4963 | 0.31618 | 3 | 43924.8042 |  |  |  | 35938.4762 | 0.31618 | 10 | Each | [30 empty] | 9.4368 | 23.374 | 26.0471 | Normal | 19.6196 | 0.41426 | 3 | 25.7114 |  |  |  | 21.0366 | 0.41426 | 10 | Each | 11.4221 | 25.8629 | 29.5544 | Normal | 22.2791 | 0.40413 | 3 | 28.4492 |  |  |  | 23.2766 | 0.40413 | 10 | Each | 11.8191 | 26.4254 | 30.3485 | Normal | 22.8643 | 0.40308 | 3 | 29.0679 |  |  |  | 23.7829 | 0.40308 | 10 | Each | [30 empty] | 1
| B1033.032b |  | B1033.032b | Special Concentric Braced Frame, design to AISC minimum standards, Single Diagonal Brace, Brace 41 PLF < w < 99 PLF | 14260 | 35320.7811 | 39360 | Normal | 29646.8005 | 0.33031 | 3 | 38852.8592 |  |  |  | 31788.703 | 0.33031 | 10 | Each | 21660 | 44613.8272 | 52460 | Normal | 39577.9227 | 0.30362 | 3 | 49075.2099 |  |  |  | 40152.4445 | 0.30362 | 10 | Each | 24460 | 48113.8272 | 57360 | Normal | 43311.1583 | 0.29637 | 3 | 52925.2099 |  |  |  | 43302.4445 | 0.29637 | 10 | Each | [30 empty] | 9.4368 | 23.374 | 26.0471 | Normal | 19.6196 | 0.41426 | 3 | 25.7114 |  |  |  | 21.0366 | 0.41426 | 10 | Each | 14.3338 | 29.5239 | 34.7162 | Normal | 26.1914 | 0.3933 | 3 | 32.4763 |  |  |  | 26.5715 | 0.3933 | 10 | Each | 16.1868 | 31.84 | 37.9588 | Normal | 28.6615 | 0.38773 | 3 | 35.024 |  |  |  | 28.656 | 0.38773 | 10 | Each | [30 empty] | 1
| B1033.032c |  | B1033.032c | Special Concentric Braced Frame, design to AISC minimum standards, Single Diagonal Brace, Brace w > 100 PLF | 14260 | 35320.7811 | 39360 | Normal | 29646.8005 | 0.33031 | 3 | 38852.8592 |  |  |  | 31788.703 | 0.33031 | 10 | Each | 27460 | 51816.5609 | 62460 | Normal | 47245.3371 | 0.28904 | 3 | 56998.217 |  |  |  | 46634.9048 | 0.28904 | 10 | Each | 31860 | 57316.5609 | 70160 | Normal | 53112.1405 | 0.28134 | 3 | 63048.217 |  |  |  | 51584.9048 | 0.28134 | 10 | Each | [30 empty] | 9.4368 | 23.374 | 26.0471 | Normal | 19.6196 | 0.41426 | 3 | 25.7114 |  |  |  | 21.0366 | 0.41426 | 10 | Each | 18.1721 | 34.2904 | 41.3338 | Normal | 31.2649 | 0.38216 | 3 | 37.7194 |  |  |  | 30.8614 | 0.38216 | 10 | Each | 21.0838 | 37.9301 | 46.4294 | Normal | 35.1473 | 0.37637 | 3 | 41.7231 |  |  |  | 34.1371 | 0.37637 | 10 | Each | [30 empty] | 1
| B1033.033a |  | B1033.033a | Special Concentric Braced Frame, design to AISC minimum standards, X Brace, Brace w < 40 PLF | 15560 | 36921.5621 | 41660 | Normal | 31380.4407 | 0.3245 | 3 | 40613.7183 |  |  |  | 33229.4059 | 0.3245 | 10 | Each | 20960 | 43743.2804 | 51260 | Normal | 38654.362 | 0.30583 | 3 | 48117.6085 |  |  |  | 39368.9524 | 0.30583 | 10 | Each | 22160 | 45243.2804 | 53360 | Normal | 40254.0168 | 0.3024 | 3 | 49767.6085 |  |  |  | 40718.9524 | 0.3024 | 10 | Each | 22160 | 45243.2804 | 53360 | Normal | 40254.0168 | 0.3024 | 3 | 49767.6085 |  |  |  | 40718.9524 | 0.3024 | 10 | Each | [15 empty] | 10.2971 | 24.4334 | 27.5691 | Normal | 20.7662 | 0.40963 | 3 | 26.8767 |  |  |  | 21.9901 | 0.40963 | 10 | Each | 13.8706 | 28.9478 | 33.9221 | Normal | 25.5803 | 0.39501 | 3 | 31.8426 |  |  |  | 26.053 | 0.39501 | 10 | Each | 14.6647 | 29.9404 | 35.3118 | Normal | 26.6389 | 0.39236 | 3 | 32.9344 |  |  |  | 26.9464 | 0.39236 | 10 | Each | 14.6647 | 29.9404 | 35.3118 | Normal | 26.6389 | 0.39236 | 3 | 32.9344 |  |  |  | 26.9464 | 0.39236 | 10 | Each | [15 empty] | 1
| B1033.033b |  | B1033.033b | Special Concentric Braced Frame, design to AISC minimum standards, X Brace, Brace 41 PLF < w < 99 PLF | 15560 | 36921.5621 | 41660 | Normal | 31380.4407 | 0.3245 | 3 | 40613.7183 |  |  |  | 33229.4059 | 0.3245 | 10 | Each | 31560 | 56957.6544 | 69760 | Normal | 52758.3062 | 0.28249 | 3 | 62653.4198 |  |  |  | 51261.8889 | 0.28249 | 10 | Each | 34360 | 60457.6544 | 74660 | Normal | 56492.6773 | 0.27831 | 3 | 66503.4198 |  |  |  | 54411.8889 | 0.27831 | 10 | Each | 34360 | 60457.6544 | 74660 | Normal | 56492.6773 | 0.27831 | 3 | 66503.4198 |  |  |  | 54411.8889 | 0.27831 | 10 | Each | [15 empty] | 10.2971 | 24.4334 | 27.5691 | Normal | 20.7662 | 0.40963 | 3 | 26.8767 |  |  |  | 21.9901 | 0.40963 | 10 | Each | 20.8853 | 37.6926 | 46.1647 | Normal | 34.9137 | 0.37723 | 3 | 41.4619 |  |  |  | 33.9233 | 0.37723 | 10 | Each | 22.7382 | 40.0087 | 49.4074 | Normal | 37.3846 | 0.37411 | 3 | 44.0096 |  |  |  | 36.0078 | 0.37411 | 10 | Each | 22.7382 | 40.0087 | 49.4074 | Normal | 37.3846 | 0.37411 | 3 | 44.0096 |  |  |  | 36.0078 | 0.37411 | 10 | Each | [15 empty] | 1
| B1033.033c |  | B1033.033c | Special Concentric Braced Frame, design to AISC minimum standards, X Brace, Brace w > 100 PLF | 15560 | 36921.5621 | 41660 | Normal | 31380.4407 | 0.3245 | 5 | 49844.1089 |  |  |  | 27691.1716 | 0.3245 | 20 | Each | 43660 | 72163.1218 | 91060 | Normal | 68961.0052 | 0.26817 | 5 | 97420.2144 |  |  |  | 54122.3413 | 0.26817 | 20 | Each | 48060 | 77663.1218 | 98760 | Normal | 74827.669 | 0.26435 | 5 | 104845.2144 |  |  |  | 58247.3413 | 0.26435 | 20 | Each | 48060 | 77663.1218 | 98760 | Normal | 74827.669 | 0.26435 | 5 | 104845.2144 |  |  |  | 58247.3413 | 0.26435 | 20 | Each | [15 empty] | 10.2971 | 24.4334 | 27.5691 | Normal | 20.7662 | 0.40963 | 5 | 32.9851 |  |  |  | 18.3251 | 0.40963 | 20 | Each | 28.8926 | 47.755 | 60.2603 | Normal | 45.6359 | 0.36663 | 5 | 64.4693 |  |  |  | 35.8162 | 0.36663 | 20 | Each | 31.8044 | 51.3947 | 65.3559 | Normal | 49.5183 | 0.36384 | 5 | 69.3828 |  |  |  | 38.546 | 0.36384 | 20 | Each | 31.8044 | 51.3947 | 65.3559 | Normal | 49.5183 | 0.36384 | 5 | 69.3828 |  |  |  | 38.546 | 0.36384 | 20 | Each | [15 empty] | 1
| B1033.041a |  | B1033.041a | Special Concentric Braced Frame w double angle braces, Chevron Brace, Brace w < 40 PLF | 14860 | 36078.4953 | 40460 | Normal | 30465.9341 | 0.32783 | 5 | 48705.9686 |  |  |  | 27058.8715 | 0.32783 | 20 | Each | 18860 | 41180.3887 | 47560 | Normal | 35865.7268 | 0.31225 | 5 | 55593.5247 |  |  |  | 30885.2915 | 0.31225 | 20 | Each | 20260 | 42880.3887 | 49960 | Normal | 37700.0588 | 0.30736 | 5 | 57888.5247 |  |  |  | 32160.2915 | 0.30736 | 20 | Each | [30 empty] | 9.8338 | 23.8755 | 26.775 | Normal | 20.1615 | 0.41228 | 5 | 32.2319 |  |  |  | 17.9066 | 0.41228 | 20 | Each | 12.4809 | 27.2517 | 31.4735 | Normal | 23.7356 | 0.4 | 5 | 36.7898 |  |  |  | 20.4388 | 0.4 | 20 | Each | 13.4074 | 28.3767 | 33.0618 | Normal | 24.9488 | 0.39619 | 5 | 38.3086 |  |  |  | 21.2825 | 0.39619 | 20 | Each | [30 empty] | 1
| B1033.041b |  | B1033.041b | Special Concentric Braced Frame w double angle braces, Chevron Brace, Brace 41 PLF < w < 99 PLF | 14860 | 36078.4953 | 40460 | Normal | 30465.9341 | 0.32783 | 5 | 48705.9686 |  |  |  | 27058.8715 | 0.32783 | 20 | Each | 27160 | 51477.5736 | 62060 | Normal | 46898.9921 | 0.29034 | 5 | 69494.7243 |  |  |  | 38608.1802 | 0.29034 | 20 | Each | 29960 | 54977.5736 | 66960 | Normal | 50632.276 | 0.28511 | 5 | 74219.7243 |  |  |  | 41233.1802 | 0.28511 | 20 | Each | [30 empty] | 9.8338 | 23.8755 | 26.775 | Normal | 20.1615 | 0.41228 | 5 | 32.2319 |  |  |  | 17.9066 | 0.41228 | 20 | Each | 17.9735 | 34.066 | 41.0691 | Normal | 31.0356 | 0.38314 | 5 | 45.9891 |  |  |  | 25.5495 | 0.38314 | 20 | Each | 19.8265 | 36.3822 | 44.3118 | Normal | 33.5063 | 0.3792 | 5 | 49.116 |  |  |  | 27.2866 | 0.3792 | 20 | Each | [30 empty] | 1
| B1033.041c |  | B1033.041c | Special Concentric Braced Frame w double angle braces, Chevron Brace, Brace w > 100 PLF | 14860 | 36078.4953 | 40460 | Normal | 30465.9341 | 0.32783 | 5 | 43294.1943 |  |  |  | 28862.7962 | 0.32783 | 15 | Each | 36960 | 63811.5547 | 79360 | Normal | 60044.0481 | 0.27549 | 5 | 76573.8657 |  |  |  | 51049.2438 | 0.27549 | 15 | Each | 40960 | 68811.5547 | 86360 | Normal | 65377.1514 | 0.27093 | 5 | 82573.8657 |  |  |  | 55049.2438 | 0.27093 | 15 | Each | [30 empty] | 9.8338 | 23.8755 | 26.775 | Normal | 20.1615 | 0.41228 | 5 | 28.6506 |  |  |  | 19.1004 | 0.41228 | 15 | Each | 24.4588 | 42.2282 | 52.5176 | Normal | 39.7348 | 0.37201 | 5 | 50.6738 |  |  |  | 33.7826 | 0.37201 | 15 | Each | 27.1059 | 45.5371 | 57.15 | Normal | 43.2643 | 0.36865 | 5 | 54.6445 |  |  |  | 36.4297 | 0.36865 | 15 | Each | [30 empty] | 1
| B1033.042a |  | B1033.042a | Special Concentric Braced Frame w double angle braces, Single Diagonal Brace, Brace w < 40 PLF | 14260 | 35320.7811 | 39360 | Normal | 29646.8005 | 0.33031 | 5 | 42384.9373 |  |  |  | 28256.6248 | 0.33031 | 15 | Each | 17660 | 39561.8745 | 45360 | Normal | 34193.9189 | 0.31606 | 5 | 47474.2495 |  |  |  | 31649.4996 | 0.31606 | 15 | Each | 18260 | 40411.8745 | 46560 | Normal | 35077.2566 | 0.31477 | 5 | 48494.2495 |  |  |  | 32329.4996 | 0.31477 | 15 | Each | [30 empty] | 9.4368 | 23.374 | 26.0471 | Normal | 19.6196 | 0.41426 | 5 | 28.0488 |  |  |  | 18.6992 | 0.41426 | 15 | Each | 11.6868 | 26.1807 | 30.0176 | Normal | 22.6275 | 0.40298 | 5 | 31.4168 |  |  |  | 20.9446 | 0.40298 | 15 | Each | 12.0838 | 26.7432 | 30.8118 | Normal | 23.2129 | 0.40197 | 5 | 32.0918 |  |  |  | 21.3946 | 0.40197 | 15 | Each | [30 empty] | 1
| B1033.042b |  | B1033.042b | Special Concentric Braced Frame w double angle braces, Single Diagonal Brace, Brace 41 PLF < w < 99 PLF | 14260 | 35320.7811 | 39360 | Normal | 29646.8005 | 0.33031 | 5 | 42384.9373 |  |  |  | 28256.6248 | 0.33031 | 15 | Each | 22560 | 45734.3739 | 54060 | Normal | 40784.0333 | 0.30134 | 5 | 54881.2487 |  |  |  | 36587.4991 | 0.30134 | 15 | Each | 25360 | 49234.3739 | 58960 | Normal | 44517.0996 | 0.29448 | 5 | 59081.2487 |  |  |  | 39387.4991 | 0.29448 | 15 | Each | [30 empty] | 9.4368 | 23.374 | 26.0471 | Normal | 19.6196 | 0.41426 | 5 | 28.0488 |  |  |  | 18.6992 | 0.41426 | 15 | Each | 14.9294 | 30.2654 | 35.775 | Normal | 26.9898 | 0.39154 | 5 | 36.3185 |  |  |  | 24.2123 | 0.39154 | 15 | Each | 16.7824 | 32.5816 | 39.0176 | Normal | 29.46 | 0.38629 | 5 | 39.0979 |  |  |  | 26.0653 | 0.38629 | 15 | Each | [30 empty] | 1
| B1033.042c |  | B1033.042c | Special Concentric Braced Frame w double angle braces, Single Diagonal Brace, Brace w > 100 PLF | 14260 | 35320.7811 | 39360 | Normal | 29646.8005 | 0.33031 | 3 | 44150.9763 |  |  |  | 30022.6639 | 0.33031 | 7 | Each | 28960 | 53737.4982 | 65160 | Normal | 49285.634 | 0.28657 | 3 | 67171.8727 |  |  |  | 45676.8734 | 0.28657 | 7 | Each | 33360 | 59237.4982 | 72860 | Normal | 55151.8464 | 0.27942 | 3 | 74046.8727 |  |  |  | 50351.8734 | 0.27942 | 7 | Each | [30 empty] | 9.4368 | 23.374 | 26.0471 | Normal | 19.6196 | 0.41426 | 3 | 29.2175 |  |  |  | 19.8679 | 0.41426 | 7 | Each | 19.1647 | 35.5616 | 43.1206 | Normal | 32.6151 | 0.38029 | 3 | 44.452 |  |  |  | 30.2274 | 0.38029 | 7 | Each | 22.0765 | 39.2013 | 48.2162 | Normal | 36.4975 | 0.37493 | 3 | 49.0016 |  |  |  | 33.3211 | 0.37493 | 7 | Each | [30 empty] | 1
| B1033.043a |  | B1033.043a | Special Concentric Braced Frame w double angle braces, X Brace, Brace w < 40 PLF | 15560 | 36921.5621 | 41660 | Normal | 31380.4407 | 0.3245 | 3 | 46151.9526 |  |  |  | 31383.3278 | 0.3245 | 7 | Each | 21660 | 44703.7491 | 52660 | Normal | 39674.5018 | 0.30485 | 3 | 55879.6864 |  |  |  | 37998.1867 | 0.30485 | 7 | Each | 22860 | 46203.7491 | 54760 | Normal | 41274.3258 | 0.30154 | 3 | 57754.6864 |  |  |  | 39273.1867 | 0.30154 | 7 | Each | [30 empty] | 10.2971 | 24.4334 | 27.5691 | Normal | 20.7662 | 0.40963 | 3 | 30.5417 |  |  |  | 20.7684 | 0.40963 | 7 | Each | 14.3338 | 29.5834 | 34.8485 | Normal | 26.2552 | 0.39425 | 3 | 36.9792 |  |  |  | 25.1459 | 0.39425 | 7 | Each | 15.1279 | 30.576 | 36.2382 | Normal | 27.3139 | 0.3917 | 3 | 38.22 |  |  |  | 25.9896 | 0.3917 | 7 | Each | [30 empty] | 1
| B1033.043b |  | B1033.043b | Special Concentric Braced Frame w double angle braces, X Brace, Brace 41 PLF < w < 99 PLF | 15560 | 36921.5621 | 41660 | Normal | 31380.4407 | 0.3245 | 3 | 46151.9526 |  |  |  | 31383.3278 | 0.3245 | 7 | Each | 33260 | 59198.7479 | 72860 | Normal | 55105.5572 | 0.28038 | 3 | 73998.4348 |  |  |  | 50318.9357 | 0.28038 | 7 | Each | 36060 | 62698.7479 | 77760 | Normal | 58839.6843 | 0.27649 | 3 | 78373.4348 |  |  |  | 53293.9357 | 0.27649 | 7 | Each | [30 empty] | 10.2971 | 24.4334 | 27.5691 | Normal | 20.7662 | 0.40963 | 3 | 30.5417 |  |  |  | 20.7684 | 0.40963 | 7 | Each | 22.0103 | 39.1756 | 48.2162 | Normal | 36.4668 | 0.37565 | 3 | 48.9695 |  |  |  | 33.2993 | 0.37565 | 7 | Each | 23.8632 | 41.4918 | 51.4588 | Normal | 38.9379 | 0.37275 | 3 | 51.8648 |  |  |  | 35.268 | 0.37275 | 7 | Each | [30 empty] | 1
| B1033.043c |  | B1033.043c | Special Concentric Braced Frame w double angle braces, X Brace, Brace w > 100 PLF | 15560 | 36921.5621 | 41660 | Normal | 31380.4407 | 0.3245 | 3 | 46151.9526 |  |  |  | 31383.3278 | 0.3245 | 7 | Each | 46760 | 76004.9963 | 96360 | Normal | 73041.6282 | 0.26494 | 3 | 95006.2454 |  |  |  | 64604.2469 | 0.26494 | 7 | Each | 51160 | 81504.9963 | 104060 | Normal | 78908.2902 | 0.26156 | 3 | 101881.2454 |  |  |  | 69279.2469 | 0.26156 | 7 | Each | [30 empty] | 10.2971 | 24.4334 | 27.5691 | Normal | 20.7662 | 0.40963 | 3 | 30.5417 |  |  |  | 20.7684 | 0.40963 | 7 | Each | 30.9441 | 50.2974 | 63.7676 | Normal | 48.3363 | 0.36427 | 3 | 62.8718 |  |  |  | 42.7528 | 0.36427 | 7 | Each | 33.8559 | 53.9371 | 68.8632 | Normal | 52.2187 | 0.36182 | 3 | 67.4214 |  |  |  | 45.8465 | 0.36182 | 7 | Each | [30 empty] | 1
| B1033.051a |  | B1033.051a | Ordinary Concentric Braced Frame w compact braces, Chevron Brace, Brace w < 40 PLF | 14460 | 35628.4953 | 39860 | Normal | 29982.6924 | 0.33052 | 3 | 44535.6191 |  |  |  | 30284.221 | 0.33052 | 7 | Each | 17960 | 40022.8401 | 45960 | Normal | 34647.587 | 0.3153 | 3 | 50028.5501 |  |  |  | 34019.4141 | 0.3153 | 7 | Each | 19360 | 41722.8401 | 48360 | Normal | 36480.9219 | 0.31015 | 3 | 52153.5501 |  |  |  | 35464.4141 | 0.31015 | 7 | Each | [30 empty] | 9.5691 | 23.5777 | 26.3779 | Normal | 19.8417 | 0.41442 | 3 | 29.4721 |  |  |  | 20.041 | 0.41442 | 7 | Each | 11.8853 | 26.4857 | 30.4147 | Normal | 22.9286 | 0.40238 | 3 | 33.1071 |  |  |  | 22.5128 | 0.40238 | 7 | Each | 12.8118 | 27.6107 | 32.0029 | Normal | 24.142 | 0.39836 | 3 | 34.5134 |  |  |  | 23.4691 | 0.39836 | 7 | Each | [30 empty] | 1
| B1033.051b |  | B1033.051b | Ordinary Concentric Braced Frame w compact braces, Chevron Brace, Brace w, 41 PLF < w < 99 PLF | 14460 | 35628.4953 | 39860 | Normal | 29982.6924 | 0.33052 | 3 | 44535.6191 |  |  |  | 30284.221 | 0.33052 | 7 | Each | 25060 | 48926.6269 | 58460 | Normal | 44147.8802 | 0.29518 | 3 | 61158.2836 |  |  |  | 41587.6329 | 0.29518 | 7 | Each | 27860 | 52426.6269 | 63360 | Normal | 47881.8231 | 0.28927 | 3 | 65533.2836 |  |  |  | 44562.6329 | 0.28927 | 7 | Each | [30 empty] | 9.5691 | 23.5777 | 26.3779 | Normal | 19.8417 | 0.41442 | 3 | 29.4721 |  |  |  | 20.041 | 0.41442 | 7 | Each | 16.5838 | 32.3779 | 38.6868 | Normal | 29.2159 | 0.38682 | 3 | 40.4724 |  |  |  | 27.5212 | 0.38682 | 7 | Each | 18.4368 | 34.6941 | 41.9294 | Normal | 31.6862 | 0.38233 | 3 | 43.3676 |  |  |  | 29.49 | 0.38233 | 7 | Each | [30 empty] | 1
| B1033.051c |  | B1033.051c | Ordinary Concentric Braced Frame w compact braces, Chevron Brace, Brace w > 100 PLF | 14460 | 35628.4953 | 39860 | Normal | 29982.6924 | 0.33052 | 3 | 44535.6191 |  |  |  | 30284.221 | 0.33052 | 7 | Each | 33960 | 60081.3604 | 74060 | Normal | 56033.787 | 0.27921 | 3 | 75101.7005 |  |  |  | 51069.1563 | 0.27921 | 7 | Each | 37960 | 65081.3604 | 81060 | Normal | 61367.0888 | 0.27402 | 3 | 81351.7005 |  |  |  | 55319.1563 | 0.27402 | 7 | Each | [30 empty] | 9.5691 | 23.5777 | 26.3779 | Normal | 19.8417 | 0.41442 | 3 | 29.4721 |  |  |  | 20.041 | 0.41442 | 7 | Each | 22.4735 | 39.7597 | 49.0103 | Normal | 37.081 | 0.37478 | 3 | 49.6996 |  |  |  | 33.7957 | 0.37478 | 7 | Each | 25.1206 | 43.0685 | 53.6426 | Normal | 40.6105 | 0.37092 | 3 | 53.8356 |  |  |  | 36.6082 | 0.37092 | 7 | Each | [30 empty] | 1
| B1033.052a |  | B1033.052a | Ordinary Concentric Braced Frame w compact braces, Single Diagonal Brace, Brace w < 40 PLF | 13860 | 34870.7811 | 38760 | Normal | 29163.4555 | 0.33311 | 3 | 43588.4763 |  |  |  | 29640.1639 | 0.33311 | 7 | Each | 16860 | 38631.6402 | 44060 | Normal | 33183.643 | 0.3198 | 3 | 48289.5503 |  |  |  | 32836.8942 | 0.3198 | 7 | Each | 17660 | 39631.6402 | 45460 | Normal | 34250.4998 | 0.31667 | 3 | 49539.5503 |  |  |  | 33686.8942 | 0.31667 | 7 | Each | [30 empty] | 9.1721 | 23.0763 | 25.65 | Normal | 19.2999 | 0.41649 | 3 | 28.8454 |  |  |  | 19.6149 | 0.41649 | 7 | Each | 11.1574 | 25.5651 | 29.1574 | Normal | 21.9593 | 0.40592 | 3 | 31.9564 |  |  |  | 21.7303 | 0.40592 | 7 | Each | 11.6868 | 26.2268 | 30.0838 | Normal | 22.6658 | 0.40346 | 3 | 32.7835 |  |  |  | 22.2928 | 0.40346 | 7 | Each | [30 empty] | 1
| B1033.052b |  | B1033.052b | Ordinary Concentric Braced Frame w compact braces, Single Diagonal Brace, Brace w, 41 PLF < w < 99 PLF | 13860 | 34870.7811 | 38760 | Normal | 29163.4555 | 0.33311 | 3 | 43588.4763 |  |  |  | 29640.1639 | 0.33311 | 7 | Each | 21160 | 44013.8272 | 51660 | Normal | 38944.5382 | 0.30555 | 3 | 55017.284 |  |  |  | 37411.7531 | 0.30555 | 7 | Each | 23960 | 47513.8272 | 56560 | Normal | 42677.128 | 0.29803 | 3 | 59392.284 |  |  |  | 40386.7531 | 0.29803 | 7 | Each | [30 empty] | 9.1721 | 23.0763 | 25.65 | Normal | 19.2999 | 0.41649 | 3 | 28.8454 |  |  |  | 19.6149 | 0.41649 | 7 | Each | 14.0029 | 29.1268 | 34.1868 | Normal | 25.7723 | 0.39479 | 3 | 36.4085 |  |  |  | 24.7578 | 0.39479 | 7 | Each | 15.8559 | 31.443 | 37.4294 | Normal | 28.2425 | 0.389 | 3 | 39.3037 |  |  |  | 26.7266 | 0.389 | 7 | Each | [30 empty] | 1
| B1033.052c |  | B1033.052c | Ordinary Concentric Braced Frame w compact braces, Single Diagonal Brace, Brace w > 100 PLF | 13860 | 34870.7811 | 38760 | Normal | 29163.4555 | 0.33311 | 3 | 43588.4763 |  |  |  | 29640.1639 | 0.33311 | 7 | Each | 26960 | 51216.5609 | 61660 | Normal | 46611.9613 | 0.29046 | 3 | 64020.7011 |  |  |  | 43534.0768 | 0.29046 | 7 | Each | 31360 | 56716.5609 | 69360 | Normal | 52478.3218 | 0.28252 | 3 | 70895.7011 |  |  |  | 48209.0768 | 0.28252 | 7 | Each | [30 empty] | 9.1721 | 23.0763 | 25.65 | Normal | 19.2999 | 0.41649 | 3 | 28.8454 |  |  |  | 19.6149 | 0.41649 | 7 | Each | 17.8412 | 33.8933 | 40.8044 | Normal | 30.8457 | 0.38323 | 3 | 42.3666 |  |  |  | 28.8093 | 0.38323 | 7 | Each | 20.7529 | 37.533 | 45.9 | Normal | 34.7281 | 0.37725 | 3 | 46.9163 |  |  |  | 31.903 | 0.37725 | 7 | Each | [30 empty] | 1
| B1033.053a |  | B1033.053a | Ordinary Concentric Braced Frame w compact braces, X Brace, Brace w < 40 PLF | 15160 | 36471.5621 | 41060 | Normal | 30897.003 | 0.32705 | 3 | 45589.4526 |  |  |  | 31000.8278 | 0.32705 | 7 | Each | 20360 | 42993.2804 | 50160 | Normal | 37837.6809 | 0.30727 | 3 | 53741.6006 |  |  |  | 36544.2884 | 0.30727 | 7 | Each | 21560 | 44493.2804 | 52260 | Normal | 39437.7035 | 0.30371 | 3 | 55616.6006 |  |  |  | 37819.2884 | 0.30371 | 7 | Each | [30 empty] | 10.0324 | 24.1356 | 27.1721 | Normal | 20.4465 | 0.41166 | 3 | 30.1695 |  |  |  | 20.5153 | 0.41166 | 7 | Each | 13.4735 | 28.4514 | 33.1941 | Normal | 25.0398 | 0.39613 | 3 | 35.5643 |  |  |  | 24.1837 | 0.39613 | 7 | Each | 14.2676 | 29.4441 | 34.5838 | Normal | 26.0986 | 0.39337 | 3 | 36.8051 |  |  |  | 25.0275 | 0.39337 | 7 | Each | [30 empty] | 1
| B1033.053b |  | B1033.053b | Ordinary Concentric Braced Frame w compact braces, X Brace, Brace w, 41 PLF < w < 99 PLF | 15160 | 36471.5621 | 41060 | Normal | 30897.003 | 0.32705 | 3 | 45589.4526 |  |  |  | 31000.8278 | 0.32705 | 7 | Each | 30360 | 55457.6544 | 67660 | Normal | 51158.8551 | 0.28447 | 3 | 69322.068 |  |  |  | 47139.0062 | 0.28447 | 7 | Each | 33160 | 58957.6544 | 72560 | Normal | 54891.7166 | 0.28004 | 3 | 73697.068 |  |  |  | 50114.0062 | 0.28004 | 7 | Each | [30 empty] | 10.0324 | 24.1356 | 27.1721 | Normal | 20.4465 | 0.41166 | 3 | 30.1695 |  |  |  | 20.5153 | 0.41166 | 7 | Each | 20.0912 | 36.6999 | 44.775 | Normal | 33.8548 | 0.37871 | 3 | 45.8749 |  |  |  | 31.1949 | 0.37871 | 7 | Each | 21.9441 | 39.0161 | 48.0176 | Normal | 36.3255 | 0.37539 | 3 | 48.7701 |  |  |  | 33.1637 | 0.37539 | 7 | Each | [30 empty] | 1
| B1033.053c |  | B1033.053c | Ordinary Concentric Braced Frame w compact braces, X Brace, Brace w > 100 PLF | 15160 | 36471.5621 | 41060 | Normal | 30897.003 | 0.32705 | 3 | 45589.4526 |  |  |  | 31000.8278 | 0.32705 | 7 | Each | 42460 | 70663.1218 | 88960 | Normal | 67361.006 | 0.26933 | 3 | 88328.9022 |  |  |  | 60063.6535 | 0.26933 | 7 | Each | 46860 | 76163.1218 | 96660 | Normal | 73227.67 | 0.26533 | 3 | 95203.9022 |  |  |  | 64738.6535 | 0.26533 | 7 | Each | [30 empty] | 10.0324 | 24.1356 | 27.1721 | Normal | 20.4465 | 0.41166 | 3 | 30.1695 |  |  |  | 20.5153 | 0.41166 | 7 | Each | 28.0985 | 46.7624 | 58.8706 | Normal | 44.5771 | 0.36747 | 3 | 58.453 |  |  |  | 39.748 | 0.36747 | 7 | Each | 31.0103 | 50.4021 | 63.9662 | Normal | 48.4595 | 0.36456 | 3 | 63.0026 |  |  |  | 42.8418 | 0.36456 | 7 | Each | [30 empty] | 1
| B1033.061a |  | B1033.061a | Ordinary Concentric Braced Frame, braces design to ductile slenderness limits, Chevron Brace, Brace w < 40 PLF | 14860 | 36078.4953 | 40460 | Normal | 30465.9341 | 0.32783 | 3 | 45098.1191 |  |  |  | 30666.721 | 0.32783 | 7 | Each | 18360 | 40472.8401 | 46560 | Normal | 35130.8219 | 0.31318 | 3 | 50591.0501 |  |  |  | 34401.9141 | 0.31318 | 7 | Each | 19760 | 42172.8401 | 48960 | Normal | 36964.2121 | 0.3082 | 3 | 52716.0501 |  |  |  | 35846.9141 | 0.3082 | 7 | Each | [30 empty] | 9.8338 | 23.8755 | 26.775 | Normal | 20.1615 | 0.41228 | 3 | 29.8444 |  |  |  | 20.2942 | 0.41228 | 7 | Each | 12.15 | 26.7835 | 30.8118 | Normal | 23.2484 | 0.40072 | 3 | 33.4794 |  |  |  | 22.766 | 0.40072 | 7 | Each | 13.0765 | 27.9085 | 32.4 | Normal | 24.4619 | 0.39685 | 3 | 34.8856 |  |  |  | 23.7222 | 0.39685 | 7 | Each | [30 empty] | 1
| B1033.061b |  | B1033.061b | Ordinary Concentric Braced Frame, braces design to ductile slenderness limits, Chevron Brace, Brace 41 PLF < w < 99 PLF | 14860 | 36078.4953 | 40460 | Normal | 30465.9341 | 0.32783 | 3 | 45098.1191 |  |  |  | 30666.721 | 0.32783 | 7 | Each | 25760 | 49826.6269 | 59760 | Normal | 45114.4675 | 0.29404 | 3 | 62283.2836 |  |  |  | 42352.6329 | 0.29404 | 7 | Each | 28560 | 53326.6269 | 64660 | Normal | 48848.636 | 0.28834 | 3 | 66658.2836 |  |  |  | 45327.6329 | 0.28834 | 7 | Each | [30 empty] | 9.8338 | 23.8755 | 26.775 | Normal | 20.1615 | 0.41228 | 3 | 29.8444 |  |  |  | 20.2942 | 0.41228 | 7 | Each | 17.0471 | 32.9735 | 39.5471 | Normal | 29.8553 | 0.38595 | 3 | 41.2169 |  |  |  | 28.0275 | 0.38595 | 7 | Each | 18.9 | 35.2897 | 42.7897 | Normal | 32.326 | 0.38163 | 3 | 44.1121 |  |  |  | 29.9962 | 0.38163 | 7 | Each | [30 empty] | 1
| B1033.061c |  | B1033.061c | Ordinary Concentric Braced Frame, braces design to ductile slenderness limits, Chevron Brace, Brace w > 100 PLF | 14860 | 36078.4953 | 40460 | Normal | 30465.9341 | 0.32783 | 3 | 45098.1191 |  |  |  | 30666.721 | 0.32783 | 7 | Each | 34660 | 60981.3604 | 75360 | Normal | 56999.7427 | 0.27857 | 3 | 76226.7005 |  |  |  | 51834.1563 | 0.27857 | 7 | Each | 38660 | 65981.3604 | 82360 | Normal | 62333.755 | 0.27352 | 3 | 82476.7005 |  |  |  | 56084.1563 | 0.27352 | 7 | Each | [30 empty] | 9.8338 | 23.8755 | 26.775 | Normal | 20.1615 | 0.41228 | 3 | 29.8444 |  |  |  | 20.2942 | 0.41228 | 7 | Each | 22.9368 | 40.3553 | 49.8706 | Normal | 37.7209 | 0.3743 | 3 | 50.4441 |  |  |  | 34.302 | 0.3743 | 7 | Each | 25.5838 | 43.6641 | 54.5029 | Normal | 41.2502 | 0.37056 | 3 | 54.5801 |  |  |  | 37.1145 | 0.37056 | 7 | Each | [30 empty] | 1
| B1033.062a |  | B1033.062a | Ordinary Concentric Braced Frame, braces design to ductile slenderness limits, Single Diagonal Brace, Brace w < 40 PLF | 14260 | 35320.7811 | 39360 | Normal | 29646.8005 | 0.33031 | 3 | 44150.9763 |  |  |  | 30022.6639 | 0.33031 | 7 | Each | 17260 | 39081.6402 | 44660 | Normal | 33667.1706 | 0.31752 | 3 | 48852.0503 |  |  |  | 33219.3942 | 0.31752 | 7 | Each | 17860 | 39931.6402 | 45860 | Normal | 34550.4963 | 0.31618 | 3 | 49914.5503 |  |  |  | 33941.8942 | 0.31618 | 7 | Each | [30 empty] | 9.4368 | 23.374 | 26.0471 | Normal | 19.6196 | 0.41426 | 3 | 29.2175 |  |  |  | 19.8679 | 0.41426 | 7 | Each | 11.4221 | 25.8629 | 29.5544 | Normal | 22.2791 | 0.40413 | 3 | 32.3286 |  |  |  | 21.9835 | 0.40413 | 7 | Each | 11.8191 | 26.4254 | 30.3485 | Normal | 22.8643 | 0.40308 | 3 | 33.0317 |  |  |  | 22.4616 | 0.40308 | 7 | Each | [30 empty] | 1
| B1033.062b |  | B1033.062b | Ordinary Concentric Braced Frame, braces design to ductile slenderness limits, Single Diagonal Brace, Brace 41 PLF < w < 99 PLF | 14260 | 35320.7811 | 39360 | Normal | 29646.8005 | 0.33031 | 3 | 44150.9763 |  |  |  | 30022.6639 | 0.33031 | 7 | Each | 21660 | 44613.8272 | 52460 | Normal | 39577.9227 | 0.30362 | 3 | 55767.284 |  |  |  | 37921.7531 | 0.30362 | 7 | Each | 24460 | 48113.8272 | 57360 | Normal | 43311.1583 | 0.29637 | 3 | 60142.284 |  |  |  | 40896.7531 | 0.29637 | 7 | Each | [30 empty] | 9.4368 | 23.374 | 26.0471 | Normal | 19.6196 | 0.41426 | 3 | 29.2175 |  |  |  | 19.8679 | 0.41426 | 7 | Each | 14.3338 | 29.5239 | 34.7162 | Normal | 26.1914 | 0.3933 | 3 | 36.9049 |  |  |  | 25.0953 | 0.3933 | 7 | Each | 16.1868 | 31.84 | 37.9588 | Normal | 28.6615 | 0.38773 | 3 | 39.8 |  |  |  | 27.064 | 0.38773 | 7 | Each | [30 empty] | 1
| B1033.062c |  | B1033.062c | Ordinary Concentric Braced Frame, braces design to ductile slenderness limits, Single Diagonal Brace, Brace w > 100 PLF | 14260 | 35320.7811 | 39360 | Normal | 29646.8005 | 0.33031 | 3 | 44150.9763 |  |  |  | 30022.6639 | 0.33031 | 7 | Each | 27460 | 51816.5609 | 62460 | Normal | 47245.3371 | 0.28904 | 3 | 64770.7011 |  |  |  | 44044.0768 | 0.28904 | 7 | Each | 31860 | 57316.5609 | 70160 | Normal | 53112.1405 | 0.28134 | 3 | 71645.7011 |  |  |  | 48719.0768 | 0.28134 | 7 | Each | [30 empty] | 9.4368 | 23.374 | 26.0471 | Normal | 19.6196 | 0.41426 | 3 | 29.2175 |  |  |  | 19.8679 | 0.41426 | 7 | Each | 18.1721 | 34.2904 | 41.3338 | Normal | 31.2649 | 0.38216 | 3 | 42.863 |  |  |  | 29.1468 | 0.38216 | 7 | Each | 21.0838 | 37.9301 | 46.4294 | Normal | 35.1473 | 0.37637 | 3 | 47.4126 |  |  |  | 32.2406 | 0.37637 | 7 | Each | [30 empty] | 1
| B1033.063a |  | B1033.063a | Ordinary Concentric Braced Frame, braces design to ductile slenderness limits, X Brace, Brace w < 40 PLF | 15560 | 36921.5621 | 41660 | Normal | 31380.4407 | 0.3245 | 3 | 46151.9526 |  |  |  | 31383.3278 | 0.3245 | 7 | Each | 20960 | 43743.2804 | 51260 | Normal | 38654.362 | 0.30583 | 3 | 54679.1006 |  |  |  | 37181.7884 | 0.30583 | 7 | Each | 22160 | 45243.2804 | 53360 | Normal | 40254.0168 | 0.3024 | 3 | 56554.1006 |  |  |  | 38456.7884 | 0.3024 | 7 | Each | [30 empty] | 10.2971 | 24.4334 | 27.5691 | Normal | 20.7662 | 0.40963 | 3 | 30.5417 |  |  |  | 20.7684 | 0.40963 | 7 | Each | 13.8706 | 28.9478 | 33.9221 | Normal | 25.5803 | 0.39501 | 3 | 36.1847 |  |  |  | 24.6056 | 0.39501 | 7 | Each | 14.6647 | 29.9404 | 35.3118 | Normal | 26.6389 | 0.39236 | 3 | 37.4255 |  |  |  | 25.4493 | 0.39236 | 7 | Each | [30 empty] | 1
| B1033.063b |  | B1033.063b | Ordinary Concentric Braced Frame, braces design to ductile slenderness limits, X Brace, Brace 41 PLF < w < 99 PLF | 15560 | 36921.5621 | 41660 | Normal | 31380.4407 | 0.3245 | 3 | 46151.9526 |  |  |  | 31383.3278 | 0.3245 | 7 | Each | 31560 | 56957.6544 | 69760 | Normal | 52758.3062 | 0.28249 | 3 | 71197.068 |  |  |  | 48414.0062 | 0.28249 | 7 | Each | 34360 | 60457.6544 | 74660 | Normal | 56492.6773 | 0.27831 | 3 | 75572.068 |  |  |  | 51389.0062 | 0.27831 | 7 | Each | [30 empty] | 10.2971 | 24.4334 | 27.5691 | Normal | 20.7662 | 0.40963 | 3 | 30.5417 |  |  |  | 20.7684 | 0.40963 | 7 | Each | 20.8853 | 37.6926 | 46.1647 | Normal | 34.9137 | 0.37723 | 3 | 47.1157 |  |  |  | 32.0387 | 0.37723 | 7 | Each | 22.7382 | 40.0087 | 49.4074 | Normal | 37.3846 | 0.37411 | 3 | 50.0109 |  |  |  | 34.0074 | 0.37411 | 7 | Each | [30 empty] | 1
| B1033.063c |  | B1033.063c | Ordinary Concentric Braced Frame, braces design to ductile slenderness limits, X Brace, Brace w > 100 PLF | 15560 | 36921.5621 | 41660 | Normal | 31380.4407 | 0.3245 | 3 | 46151.9526 |  |  |  | 31383.3278 | 0.3245 | 7 | Each | 43660 | 72163.1218 | 91060 | Normal | 68961.0052 | 0.26817 | 3 | 90203.9022 |  |  |  | 61338.6535 | 0.26817 | 7 | Each | 48060 | 77663.1218 | 98760 | Normal | 74827.669 | 0.26435 | 3 | 97078.9022 |  |  |  | 66013.6535 | 0.26435 | 7 | Each | [30 empty] | 10.2971 | 24.4334 | 27.5691 | Normal | 20.7662 | 0.40963 | 3 | 30.5417 |  |  |  | 20.7684 | 0.40963 | 7 | Each | 28.8926 | 47.755 | 60.2603 | Normal | 45.6359 | 0.36663 | 3 | 59.6938 |  |  |  | 40.5917 | 0.36663 | 7 | Each | 31.8044 | 51.3947 | 65.3559 | Normal | 49.5183 | 0.36384 | 3 | 64.2434 |  |  |  | 43.6855 | 0.36384 | 7 | Each | [30 empty] | 1
| B1033.071a |  | B1033.071a | Braced frame, design for factored loads, no additional seismic detailing, Chevron Brace, Brace w < 40 PLF | 18360 | 40472.8401 | 46560 | Normal | 35130.9264 | 0.31318 | 3 | 50591.0501 |  |  |  | 34401.9141 | 0.31318 | 7 | Each | [60 empty] | 12.15 | 26.7835 | 30.8118 | Normal | 23.2484 | 0.40072 | 3 | 33.4794 |  |  |  | 22.766 | 0.40072 | 7 | Each | [60 empty] | 1
| B1033.071b |  | B1033.071b | Braced frame, design for factored loads, no additional seismic detailing, Chevron Brace, 41 PLF < w < 99 PLF | 25760 | 49826.6269 | 59760 | Normal | 45115.0159 | 0.29403 | 3 | 62283.2836 |  |  |  | 42352.6329 | 0.29403 | 7 | Each | [60 empty] | 17.0471 | 32.9735 | 39.5471 | Normal | 29.8553 | 0.38595 | 3 | 41.2169 |  |  |  | 28.0275 | 0.38595 | 7 | Each | [60 empty] | 1
| B1033.071c |  | B1033.071c | Braced frame, design for factored loads, no additional seismic detailing, Chevron Brace, Brace w > 100 PLF | 34660 | 60981.3604 | 75360 | Normal | 57000.0242 | 0.27858 | 3 | 76226.7005 |  |  |  | 51834.1563 | 0.27858 | 7 | Each | [60 empty] | 22.9368 | 40.3553 | 49.8706 | Normal | 37.7209 | 0.37431 | 3 | 50.4441 |  |  |  | 34.302 | 0.37431 | 7 | Each | [60 empty] | 1
| B1033.072a |  | B1033.072a | Braced frame, design for factored loads, no additional seismic detailing, Single Diagonal Brace, Brace w < 40 PLF | 17260 | 39081.6402 | 44660 | Normal | 33667.0378 | 0.31752 | 3 | 48852.0503 |  |  |  | 33219.3942 | 0.31752 | 7 | Each | [60 empty] | 11.4221 | 25.8629 | 29.5544 | Normal | 22.2791 | 0.40413 | 3 | 32.3286 |  |  |  | 21.9835 | 0.40413 | 7 | Each | [60 empty] | 1
| B1033.072b |  | B1033.072b | Braced frame, design for factored loads, no additional seismic detailing, Single Diagonal Brace, 41 PLF < w < 99 PLF | 21660 | 44613.8272 | 52460 | Normal | 39577.5527 | 0.30362 | 3 | 55767.284 |  |  |  | 37921.7531 | 0.30362 | 7 | Each | [60 empty] | 14.3338 | 29.5239 | 34.7162 | Normal | 26.1914 | 0.3933 | 3 | 36.9049 |  |  |  | 25.0953 | 0.3933 | 7 | Each | [60 empty] | 1
| B1033.072c |  | B1033.072c | Braced frame, design for factored loads, no additional seismic detailing, Single Diagonal Brace, Brace w > 100 PLF | 27460 | 51816.5609 | 62460 | Normal | 47245.108 | 0.28903 | 3 | 64770.7011 |  |  |  | 44044.0768 | 0.28903 | 7 | Each | [60 empty] | 18.1721 | 34.2904 | 41.3338 | Normal | 31.2649 | 0.38215 | 3 | 42.863 |  |  |  | 29.1468 | 0.38215 | 7 | Each | [60 empty] | 1
| B1033.073a |  | B1033.073a | Braced frame, design for factored loads, no additional seismic detailing, X Brace, Brace w < 40 PLF | 20960 | 43743.2804 | 51260 | Normal | 38654.07 | 0.30583 | 3 | 54679.1006 |  |  |  | 37181.7884 | 0.30583 | 7 | Each | [60 empty] | 13.8706 | 28.9478 | 33.9221 | Normal | 25.5803 | 0.39501 | 3 | 36.1847 |  |  |  | 24.6056 | 0.39501 | 7 | Each | [60 empty] | 1
| B1033.073b |  | B1033.073b | Braced frame, design for factored loads, no additional seismic detailing, X Brace, Brace 41 PLF < w < 99 PLF | 31560 | 56957.6544 | 69760 | Normal | 52759.0756 | 0.28249 | 3 | 71197.068 |  |  |  | 48414.0062 | 0.28249 | 7 | Each | [60 empty] | 20.8853 | 37.6926 | 46.1647 | Normal | 34.9137 | 0.37722 | 3 | 47.1157 |  |  |  | 32.0387 | 0.37722 | 7 | Each | [60 empty] | 1
| B1033.073c |  | B1033.073c | Braced frame, design for factored loads, no additional seismic detailing, X Brace, Brace w > 100 PLF | 43660 | 72163.1218 | 91060 | Normal | 68961.0123 | 0.26817 | 3 | 90203.9022 |  |  |  | 61338.6535 | 0.26817 | 7 | Each | [60 empty] | 28.8926 | 47.755 | 60.2603 | Normal | 45.6359 | 0.36663 | 3 | 59.6938 |  |  |  | 40.5917 | 0.36663 | 7 | Each | [60 empty] | 1
| B1033.101a |  | B1033.101a | Steel Buckling Restrained Brace (BRB), Chevron Brace, Weight of brace < 40 plf. | 21360 | 44310.583 | 52060 | Normal | 39243.1547 | 0.30522 | 5 | 57603.7579 |  |  |  | 35448.4664 | 0.30522 | 20 | Each | [60 empty] | 14.1353 | 29.3232 | 34.4515 | Normal | 25.9701 | 0.39453 | 5 | 38.1202 |  |  |  | 23.4586 | 0.39453 | 20 | Each | [60 empty] | 1
| B1033.101b |  | B1033.101b | Steel Buckling Restrained Brace (BRB), Chevron brace, Weight of brace > 41 plf and < 99 plf. | 32360 | 58081.3604 | 71260 | Normal | 53900.1807 | 0.28157 | 5 | 75505.7685 |  |  |  | 46465.0883 | 0.28157 | 20 | Each | [60 empty] | 21.4147 | 38.4362 | 47.1574 | Normal | 35.669 | 0.37654 | 5 | 49.9671 |  |  |  | 30.749 | 0.37654 | 20 | Each | [60 empty] | 1
| B1033.101c |  | B1033.101c | Steel Buckling Restrained Brace (BRB), Chevron Brace, Weight of brace > 100 plf. | 46160 | 75232.3321 | 95260 | Normal | 72217.4131 | 0.26526 | 5 | 97802.0317 |  |  |  | 60185.8657 | 0.26526 | 20 | Each | [60 empty] | 30.5471 | 49.7861 | 63.0397 | Normal | 47.7909 | 0.3645 | 5 | 64.7219 |  |  |  | 39.8289 | 0.3645 | 20 | Each | [60 empty] | 1
| B1033.111a |  | B1033.111a | Steel Buckling Restrained Brace (BRB), Single Diagonal Brace, Weight of brace < 40 plf. | 19160 | 41532.8118 | 48160 | Normal | 36284.0993 | 0.31183 | 5 | 53992.6554 |  |  |  | 33226.2495 | 0.31183 | 20 | Each | [60 empty] | 12.6794 | 27.4849 | 31.8706 | Normal | 24.0119 | 0.39967 | 5 | 35.7304 |  |  |  | 21.9879 | 0.39967 | 20 | Each | [60 empty] | 1
| B1033.111b |  | B1033.111b | Steel Buckling Restrained Brace (BRB), Single Diagonal brace, Weight of brace > 41 plf and < 99 plf. | 26560 | 50716.5609 | 60960 | Normal | 46078.387 | 0.29127 | 5 | 65931.5292 |  |  |  | 40573.2487 | 0.29127 | 20 | Each | [60 empty] | 17.5765 | 33.5624 | 40.3412 | Normal | 30.4928 | 0.38385 | 5 | 43.6311 |  |  |  | 26.8499 | 0.38385 | 20 | Each | [60 empty] | 1
| B1033.111c |  | B1033.111c | Steel Buckling Restrained Brace (BRB), Single Diagonal Brace, Weight of brace > 100 plf. | 35360 | 61821.2473 | 76560 | Normal | 57913.2926 | 0.27756 | 5 | 80367.6214 |  |  |  | 49456.9978 | 0.27756 | 20 | Each | [60 empty] | 23.4 | 40.9111 | 50.6647 | Normal | 38.3252 | 0.37355 | 5 | 53.1844 |  |  |  | 32.7289 | 0.37355 | 20 | Each | [60 empty] | 1
| B1035.001 |  | B1035.001 | Post-Northridge RBS connection with welded web, beam one side of column only, beam depth <= W27 | 8100 | 17400 | 22600 | Normal | 16033.1352 | 0.35285 | 3 | 21750 |  |  |  | 14790 | 0.35285 | 7 | Each | 14100 | 29300 | 34400 | Normal | 25933.3041 | 0.3054 | 3 | 36625 |  |  |  | 24905 | 0.3054 | 7 | Each | 14100 | 29300 | 34400 | Normal | 25933.3041 | 0.3054 | 3 | 36625 |  |  |  | 24905 | 0.3054 | 7 | Each | [30 empty] | 4.7647 | 10.2353 | 13.2941 | Normal | 10.2353 | 0.43244 | 3 | 12.7941 |  |  |  | 8.7 | 0.43244 | 7 | Each | 8.2941 | 17.2353 | 20.2353 | Normal | 17.2353 | 0.39468 | 3 | 21.5441 |  |  |  | 14.65 | 0.39468 | 7 | Each | 8.2941 | 17.2353 | 20.2353 | Normal | 17.2353 | 0.39468 | 3 | 21.5441 |  |  |  | 14.65 | 0.39468 | 7 | Each | [30 empty] | 1
| B1035.002 |  | B1035.002 | Post-Northridge RBS connection with welded web, beam one side of column only, beam depth >= W30 | 9100 | 18400 | 23600 | Normal | 17033.3217 | 0.33213 | 3 | 23000 |  |  |  | 15640 | 0.33213 | 7 | Each | 16100 | 32400 | 36800 | Normal | 28432.7396 | 0.28405 | 3 | 40500 |  |  |  | 27540 | 0.28405 | 7 | Each | 16100 | 32400 | 36800 | Normal | 28432.7396 | 0.28405 | 3 | 40500 |  |  |  | 27540 | 0.28405 | 7 | Each | [30 empty] | 5.3529 | 10.8235 | 13.8824 | Normal | 10.8235 | 0.4157 | 3 | 13.5294 |  |  |  | 9.2 | 0.4157 | 7 | Each | 9.4706 | 19.0588 | 21.6471 | Normal | 19.0588 | 0.3784 | 3 | 23.8235 |  |  |  | 16.2 | 0.3784 | 7 | Each | 9.4706 | 19.0588 | 21.6471 | Normal | 19.0588 | 0.3784 | 3 | 23.8235 |  |  |  | 16.2 | 0.3784 | 7 | Each | [30 empty] | 1
| B1035.011 |  | B1035.011 | Post-Northridge RBS connection with welded web, beams both sides of column, beam depth <= W27 | 13700 | 30000 | 36000 | Normal | 26566.6574 | 0.32749 | 3 | 37500 |  |  |  | 25500 | 0.32749 | 7 | Each | 27700 | 52300 | 61000 | Normal | 46999.9775 | 0.27643 | 3 | 65375 |  |  |  | 44455 | 0.27643 | 7 | Each | 27700 | 52300 | 61000 | Normal | 46999.9775 | 0.27643 | 3 | 65375 |  |  |  | 44455 | 0.27643 | 7 | Each | [30 empty] | 8.0588 | 17.6471 | 21.1765 | Normal | 17.6471 | 0.41201 | 3 | 22.0589 |  |  |  | 15 | 0.41201 | 7 | Each | 16.2941 | 30.7647 | 35.8824 | Normal | 30.7647 | 0.37271 | 3 | 38.4559 |  |  |  | 26.15 | 0.37271 | 7 | Each | 16.2941 | 30.7647 | 35.8824 | Normal | 30.7647 | 0.37271 | 3 | 38.4559 |  |  |  | 26.15 | 0.37271 | 7 | Each | [30 empty] | 1
| B1035.012 |  | B1035.012 | Post-Northridge RBS connection with welded web, beams both sides of column, beam depth >= W30 | 15700 | 32000 | 38500 | Normal | 28733.2885 | 0.30958 | 3 | 40000 |  |  |  | 27200 | 0.30958 | 7 | Each | 32700 | 58500 | 66000 | Normal | 52398.9379 | 0.24793 | 3 | 73125 |  |  |  | 49725 | 0.24793 | 7 | Each | 32700 | 58500 | 66000 | Normal | 52398.9379 | 0.24793 | 3 | 73125 |  |  |  | 49725 | 0.24793 | 7 | Each | [30 empty] | 9.2353 | 18.8235 | 22.6471 | Normal | 18.8235 | 0.39792 | 3 | 23.5294 |  |  |  | 16 | 0.39792 | 7 | Each | 19.2353 | 34.4118 | 38.8235 | Normal | 34.4118 | 0.35209 | 3 | 43.0147 |  |  |  | 29.25 | 0.35209 | 7 | Each | 19.2353 | 34.4118 | 38.8235 | Normal | 34.4118 | 0.35209 | 3 | 43.0147 |  |  |  | 29.25 | 0.35209 | 7 | Each | [30 empty] | 1
| B1035.021 |  | B1035.021 | Post-Northridge welded steel moment connection other than RBS, beam one side, beam depth <= W27 | 8100 | 17400 | 22600 | Normal | 16033.1352 | 0.35285 | 3 | 20880 |  |  |  | 13920 | 0.35285 | 7 | Each | 14100 | 29300 | 34400 | Normal | 25933.3041 | 0.3054 | 3 | 35160 |  |  |  | 23440 | 0.3054 | 7 | Each | 14100 | 29300 | 34400 | Normal | 25933.3041 | 0.3054 | 3 | 35160 |  |  |  | 23440 | 0.3054 | 7 | Each | [30 empty] | 4.7647 | 10.2353 | 13.2941 | Normal | 10.2353 | 0.43244 | 3 | 12.2824 |  |  |  | 8.1882 | 0.43244 | 7 | Each | 8.2941 | 17.2353 | 20.2353 | Normal | 17.2353 | 0.39468 | 3 | 20.6824 |  |  |  | 13.7882 | 0.39468 | 7 | Each | 8.2941 | 17.2353 | 20.2353 | Normal | 17.2353 | 0.39468 | 3 | 20.6824 |  |  |  | 13.7882 | 0.39468 | 7 | Each | [30 empty] | 1
| B1035.022 |  | B1035.022 | Post-Northridge welded steel moment connection other than RBS, beam one side, beam depth >= W30 | 9100 | 18400 | 23600 | Normal | 17033.3217 | 0.33213 | 3 | 22080 |  |  |  | 14720 | 0.33213 | 7 | Each | 16100 | 32400 | 36800 | Normal | 28432.7396 | 0.28405 | 3 | 38880 |  |  |  | 25920 | 0.28405 | 7 | Each | 16100 | 32400 | 36800 | Normal | 28432.7396 | 0.28405 | 3 | 38880 |  |  |  | 25920 | 0.28405 | 7 | Each | [30 empty] | 5.3529 | 10.8235 | 13.8824 | Normal | 10.8235 | 0.4157 | 3 | 12.9882 |  |  |  | 8.6588 | 0.4157 | 7 | Each | 9.4706 | 19.0588 | 21.6471 | Normal | 19.0588 | 0.3784 | 3 | 22.8706 |  |  |  | 15.247 | 0.3784 | 7 | Each | 9.4706 | 19.0588 | 21.6471 | Normal | 19.0588 | 0.3784 | 3 | 22.8706 |  |  |  | 15.247 | 0.3784 | 7 | Each | [30 empty] | 1
| B1035.031 |  | B1035.031 | Post-Northridge welded steel moment connection other than RBS, beams both sides, beam depth <= W27 | 14700 | 35000 | 41500 | Normal | 30399.9899 | 0.34395 | 3 | 42000 |  |  |  | 28000 | 0.34395 | 7 | Each | 27700 | 52300 | 61000 | Normal | 46999.9775 | 0.27643 | 3 | 62760 |  |  |  | 41840 | 0.27643 | 7 | Each | 27700 | 52300 | 61000 | Normal | 46999.9775 | 0.27643 | 3 | 62760 |  |  |  | 41840 | 0.27643 | 7 | Each | [30 empty] | 8.6471 | 20.5882 | 24.4118 | Normal | 20.5882 | 0.42521 | 3 | 24.7058 |  |  |  | 16.4706 | 0.42521 | 7 | Each | 16.2941 | 30.7647 | 35.8824 | Normal | 30.7647 | 0.37271 | 3 | 36.9176 |  |  |  | 24.6118 | 0.37271 | 7 | Each | 16.2941 | 30.7647 | 35.8824 | Normal | 30.7647 | 0.37271 | 3 | 36.9176 |  |  |  | 24.6118 | 0.37271 | 7 | Each | [30 empty] | 1
| B1035.032 |  | B1035.032 | Post-Northridge welded steel moment connection other than RBS, beams both sides, beam depth >= W30 | 14700 | 35000 | 41500 | Normal | 30399.9899 | 0.34395 | 3 | 42000 |  |  |  | 28000 | 0.34395 | 7 | Each | 32700 | 58500 | 66000 | Normal | 52398.9379 | 0.24793 | 3 | 70200 |  |  |  | 46800 | 0.24793 | 7 | Each | 32700 | 58500 | 66000 | Normal | 52398.9379 | 0.24793 | 3 | 70200 |  |  |  | 46800 | 0.24793 | 7 | Each | [30 empty] | 8.6471 | 20.5882 | 24.4118 | Normal | 20.5882 | 0.42521 | 3 | 24.7058 |  |  |  | 16.4706 | 0.42521 | 7 | Each | 19.2353 | 34.4118 | 38.8235 | Normal | 34.4118 | 0.35209 | 3 | 41.2942 |  |  |  | 27.5294 | 0.35209 | 7 | Each | 19.2353 | 34.4118 | 38.8235 | Normal | 34.4118 | 0.35209 | 3 | 41.2942 |  |  |  | 27.5294 | 0.35209 | 7 | Each | [30 empty] | 1
| B1035.041 |  | B1035.041 | Pre-Northridge WUF-B beam-column joint, beam one side of column, beam depth <= W27 | 6540 | 12060 | 17340 | Normal | 11979.9989 | 0.35172 | 5 | 14472 |  |  |  | 9648 | 0.35172 | 30 | Each | 7540 | 13560 | 19840 | Normal | 13646.6762 | 0.35165 | 5 | 16272 |  |  |  | 10848 | 0.35165 | 30 | Each | 11040 | 17060 | 25340 | LogNormal | 16860.9686 | 0.31991 | 5 | 17472 |  |  |  | 11648 | 0.31991 | 30 | Each | 11080 | 17600 | 28380 | LogNormal | 17676.2977 | 0.36879 | 5 | 21120 |  |  |  | 14080 | 0.36879 | 30 | Each | 9040 | 14560 | 21840 | LogNormal | 14260.6134 | 0.33607 | 5 | 17472 |  |  |  | 11648 | 0.33607 | 30 | Each | 3.8471 | 7.0941 | 10.2 | Normal | 7.0941 | 0.43152 | 5 | 8.5129 |  |  |  | 5.6753 | 0.43152 | 30 | Each | 4.4353 | 7.9765 | 11.6706 | Normal | 7.9765 | 0.43146 | 5 | 9.5718 |  |  |  | 6.3812 | 0.43146 | 30 | Each | 6.4941 | 10.0353 | 14.9059 | LogNormal | 10.0353 | 0.40601 | 5 | 11.7482 |  |  |  | 8.3224 | 0.40601 | 30 | Each | 6.5176 | 10.3529 | 16.6941 | LogNormal | 10.3529 | 0.44554 | 5 | 12.4235 |  |  |  | 8.2823 | 0.44554 | 30 | Each | 5.3176 | 8.5647 | 12.8471 | LogNormal | 8.5647 | 0.41886 | 5 | 10.2776 |  |  |  | 6.8518 | 0.41886 | 30 | Each | 1
| B1035.042 |  | B1035.042 | Pre-Northridge WUF-B beam-column joint, beam one side of column, beam depth >= W30 | 6540 | 12560 | 17840 | Normal | 12313.2808 | 0.35805 | 5 | 15072 |  |  |  | 10048 | 0.35805 | 30 | Each | 7540 | 14560 | 20840 | Normal | 14313.2944 | 0.36253 | 5 | 17472 |  |  |  | 11648 | 0.36253 | 30 | Each | 9540 | 17060 | 26340 | Normal | 17646.7109 | 0.37143 | 5 | 17472 |  |  |  | 11648 | 0.37143 | 30 | Each | 11080 | 17600 | 28380 | LogNormal | 17676.2977 | 0.36879 | 5 | 21120 |  |  |  | 14080 | 0.36879 | 30 | Each | 9040 | 14560 | 21840 | LogNormal | 14260.6134 | 0.33607 | 5 | 17472 |  |  |  | 11648 | 0.33607 | 30 | Each | 3.8471 | 7.3882 | 10.4941 | Normal | 7.3882 | 0.43669 | 5 | 8.8658 |  |  |  | 5.9106 | 0.43669 | 30 | Each | 4.4353 | 8.5647 | 12.2588 | Normal | 8.5647 | 0.44037 | 5 | 10.2776 |  |  |  | 6.8518 | 0.44037 | 30 | Each | 5.6118 | 10.0353 | 15.4941 | Normal | 10.0353 | 0.44772 | 5 | 11.7482 |  |  |  | 8.3224 | 0.44772 | 30 | Each | 6.5176 | 10.3529 | 16.6941 | LogNormal | 10.3529 | 0.44554 | 5 | 12.4235 |  |  |  | 8.2823 | 0.44554 | 30 | Each | 5.3176 | 8.5647 | 12.8471 | LogNormal | 8.5647 | 0.41886 | 5 | 10.2776 |  |  |  | 6.8518 | 0.41886 | 30 | Each | 1
| B1035.051 |  | B1035.051 | Pre-Northridge WUF-B beam-column joint, beam both sides of column, beam depth <= W27 | 8540 | 17580 | 23840 | Normal | 16653.3052 | 0.35845 | 5 | 21096 |  |  |  | 14064 | 0.35845 | 30 | Each | 9540 | 19080 | 26340 | Normal | 18319.9704 | 0.35778 | 5 | 22896 |  |  |  | 15264 | 0.35778 | 30 | Each | 13640 | 24580 | 31840 | Normal | 23353.3327 | 0.30406 | 5 | 22656 |  |  |  | 15104 | 0.30406 | 30 | Each | 13680 | 24120 | 32880 | Normal | 23559.9879 | 0.31795 | 5 | 28944 |  |  |  | 19296 | 0.31795 | 30 | Each | 10340 | 18880 | 25640 | Normal | 18286.7013 | 0.32642 | 5 | 22656 |  |  |  | 15104 | 0.32642 | 30 | Each | 5.0235 | 10.3412 | 14.0235 | Normal | 10.3412 | 0.43702 | 5 | 12.4094 |  |  |  | 8.273 | 0.43702 | 30 | Each | 5.6118 | 11.2235 | 15.4941 | Normal | 11.2235 | 0.43647 | 5 | 13.4682 |  |  |  | 8.9788 | 0.43647 | 30 | Each | 8.0235 | 14.4588 | 18.7294 | Normal | 14.4588 | 0.39364 | 5 | 16.68 |  |  |  | 12.2376 | 0.39364 | 30 | Each | 8.0471 | 14.1882 | 19.3412 | Normal | 14.1882 | 0.40447 | 5 | 17.0258 |  |  |  | 11.3506 | 0.40447 | 30 | Each | 6.0824 | 11.1059 | 15.0824 | Normal | 11.1059 | 0.41116 | 5 | 13.3271 |  |  |  | 8.8847 | 0.41116 | 30 | Each | 1
| B1035.052 |  | B1035.052 | Pre-Northridge WUF-B beam-column joint, beam both sides of column, beam depth >= W30 | 8540 | 17580 | 23840 | Normal | 16653.3052 | 0.35845 | 5 | 21096 |  |  |  | 14064 | 0.35845 | 30 | Each | 9540 | 19080 | 26340 | Normal | 18319.9704 | 0.35778 | 5 | 22896 |  |  |  | 15264 | 0.35778 | 30 | Each | 12140 | 22080 | 31840 | Normal | 22019.9896 | 0.34905 | 5 | 28704 |  |  |  | 19136 | 0.34905 | 30 | Each | 13680 | 24120 | 34880 | Normal | 24226.6644 | 0.34141 | 5 | 28944 |  |  |  | 19296 | 0.34141 | 30 | Each | 9380 | 23920 | 26180 | Normal | 19826.6093 | 0.33059 | 5 | 28704 |  |  |  | 19136 | 0.33059 | 30 | Each | 5.0235 | 10.3412 | 14.0235 | Normal | 10.3412 | 0.43702 | 5 | 12.4094 |  |  |  | 8.273 | 0.43702 | 30 | Each | 5.6118 | 11.2235 | 15.4941 | Normal | 11.2235 | 0.43647 | 5 | 13.4682 |  |  |  | 8.9788 | 0.43647 | 30 | Each | 7.1412 | 12.9882 | 18.7294 | Normal | 12.9882 | 0.42934 | 5 | 15.8023 |  |  |  | 10.1741 | 0.42934 | 30 | Each | 8.0471 | 14.1882 | 20.5176 | Normal | 14.1882 | 0.42316 | 5 | 17.0258 |  |  |  | 11.3506 | 0.42316 | 30 | Each | 5.5176 | 14.0706 | 15.4 | Normal | 14.0706 | 0.41448 | 5 | 16.8847 |  |  |  | 11.2565 | 0.41448 | 30 | Each | 1
| B1035.061a |  | B1035.061a | EBF Shear Link, no floor beams, link w < 100 PLF | 41300 | 82600 | 100300 | Normal | 74731.7929 | 0.30801 | 2 | 99120 |  |  |  | 66080 | 0.30801 | 5 | Each | 47300 | 88600 | 104800 | Normal | 80231.0203 | 0.2796 | 2 | 106320 |  |  |  | 70880 | 0.2796 | 5 | Each | 70500 | 113300 | 128500 | Normal | 104099.8879 | 0.21738 | 2 | 135960 |  |  |  | 90640 | 0.21738 | 5 | Each | [30 empty] | 27.3309 | 54.6618 | 66.375 | Normal | 54.6618 | 0.3967 | 2 | 65.5942 |  |  |  | 43.7294 | 0.3967 | 5 | Each | 31.3015 | 58.6324 | 69.3529 | Normal | 58.6324 | 0.37507 | 2 | 70.3589 |  |  |  | 46.9059 | 0.37507 | 5 | Each | 46.6544 | 74.9779 | 85.0368 | Normal | 74.9779 | 0.33129 | 2 | 89.9735 |  |  |  | 59.9823 | 0.33129 | 5 | Each | [30 empty] | 1
| B1035.061b |  | B1035.061b | EBF Shear Link, no floor beams, link w < 200 PLF | 41300 | 82600 | 100300 | Normal | 74731.7929 | 0.30801 | 2 | 99120 |  |  |  | 66080 | 0.30801 | 5 | Each | 50300 | 91600 | 107800 | Normal | 83233.2927 | 0.26953 | 2 | 109920 |  |  |  | 73280 | 0.26953 | 5 | Each | 82500 | 125300 | 140500 | Normal | 116099.9476 | 0.19491 | 2 | 150360 |  |  |  | 100240 | 0.19491 | 5 | Each | [30 empty] | 27.3309 | 54.6618 | 66.375 | Normal | 54.6618 | 0.3967 | 2 | 65.5942 |  |  |  | 43.7294 | 0.3967 | 5 | Each | 33.2868 | 60.6176 | 71.3382 | Normal | 60.6176 | 0.36762 | 2 | 72.7411 |  |  |  | 48.4941 | 0.36762 | 5 | Each | 54.5956 | 82.9191 | 92.9779 | Normal | 82.9191 | 0.317 | 2 | 99.5029 |  |  |  | 66.3353 | 0.317 | 5 | Each | [30 empty] | 1
| B1035.062a |  | B1035.062a | EBF Shear Link, with floor beams, link w < 100 PLF | 41300 | 82600 | 100300 | Normal | 74731.7929 | 0.30801 | 2 | 99120 |  |  |  | 66080 | 0.30801 | 5 | Each | 47300 | 88600 | 104800 | Normal | 80231.0203 | 0.2796 | 2 | 106320 |  |  |  | 70880 | 0.2796 | 5 | Each | 81800 | 125600 | 143800 | Normal | 117066.6112 | 0.20663 | 2 | 150720 |  |  |  | 100480 | 0.20663 | 5 | Each | [30 empty] | 27.3309 | 54.6618 | 66.375 | Normal | 54.6618 | 0.3967 | 2 | 65.5942 |  |  |  | 43.7294 | 0.3967 | 5 | Each | 31.3015 | 58.6324 | 69.3529 | Normal | 58.6324 | 0.37507 | 2 | 70.3589 |  |  |  | 46.9059 | 0.37507 | 5 | Each | 54.1324 | 83.1176 | 95.1618 | Normal | 83.1176 | 0.32434 | 2 | 99.7411 |  |  |  | 66.4941 | 0.32434 | 5 | Each | [30 empty] | 1
| B1035.062b |  | B1035.062b | EBF Shear Link, with floor beams, link w < 200 PLF | 41300 | 82600 | 100300 | Normal | 74731.7929 | 0.30801 | 2 | 99120 |  |  |  | 66080 | 0.30801 | 5 | Each | 50300 | 91600 | 107800 | Normal | 83233.2927 | 0.26953 | 2 | 109920 |  |  |  | 73280 | 0.26953 | 5 | Each | 95800 | 140600 | 161800 | Normal | 132732.3865 | 0.194 | 2 | 168720 |  |  |  | 112480 | 0.194 | 5 | Each | [30 empty] | 27.3309 | 54.6618 | 66.375 | Normal | 54.6618 | 0.3967 | 2 | 65.5942 |  |  |  | 43.7294 | 0.3967 | 5 | Each | 33.2868 | 60.6176 | 71.3382 | Normal | 60.6176 | 0.36762 | 2 | 72.7411 |  |  |  | 48.4941 | 0.36762 | 5 | Each | 63.3971 | 93.0441 | 107.0735 | Normal | 93.0441 | 0.31644 | 2 | 111.6529 |  |  |  | 74.4353 | 0.31644 | 5 | Each | [30 empty] | 1
| B1041.001a |  | B1041.001a | ACI 318 SMF , Conc Col & Bm = 24" x 24", Beam one side | 10180 | 21420 | 31132 | Normal | 20910.6558 | 0.39092 | 5 | 25704 |  |  |  | 17136 | 0.39092 | 20 | Each | 18492 | 32482 | 44444 | Normal | 31805.9835 | 0.31834 | 5 | 38978.4 |  |  |  | 25985.6 | 0.31834 | 20 | Each | 22992 | 39982 | 52944 | Normal | 38639.3134 | 0.30243 | 5 | 47978.4 |  |  |  | 31985.6 | 0.30243 | 20 | Each | 18492 | 32482 | 44444 | Normal | 31805.9835 | 0.31834 | 5 | 38978.4 |  |  |  | 25985.6 | 0.31834 | 20 | Each | [15 empty] | 8.9824 | 18.9 | 27.4694 | Normal | 18.9 | 0.46403 | 5 | 22.68 |  |  |  | 15.12 | 0.46403 | 20 | Each | 16.3165 | 28.6606 | 39.2153 | Normal | 28.6606 | 0.40477 | 5 | 34.3927 |  |  |  | 22.9285 | 0.40477 | 20 | Each | 20.2871 | 35.2782 | 46.7153 | Normal | 35.2782 | 0.39239 | 5 | 42.3338 |  |  |  | 28.2226 | 0.39239 | 20 | Each | 16.3165 | 28.6606 | 39.2153 | Normal | 28.6606 | 0.40477 | 5 | 34.3927 |  |  |  | 22.9285 | 0.40477 | 20 | Each | [15 empty] | 1
| B1041.001b |  | B1041.001b | ACI 318 SMF , Conc Col & Bm = 24" x 24", Beam both sides | 10180 | 21420 | 31132 | Normal | 20910.6558 | 0.39092 | 5 | 25704 |  |  |  | 17136 | 0.39092 | 20 | Each | 18492 | 32482 | 44444 | Normal | 31805.9835 | 0.31834 | 5 | 38978.4 |  |  |  | 25985.6 | 0.31834 | 20 | Each | 22992 | 39982 | 52944 | Normal | 38639.3134 | 0.30243 | 5 | 47978.4 |  |  |  | 31985.6 | 0.30243 | 20 | Each | 18492 | 32482 | 44444 | Normal | 31805.9835 | 0.31834 | 5 | 38978.4 |  |  |  | 25985.6 | 0.31834 | 20 | Each | [15 empty] | 8.9824 | 18.9 | 27.4694 | Normal | 18.9 | 0.46403 | 5 | 22.68 |  |  |  | 15.12 | 0.46403 | 20 | Each | 16.3165 | 28.6606 | 39.2153 | Normal | 28.6606 | 0.40477 | 5 | 34.3927 |  |  |  | 22.9285 | 0.40477 | 20 | Each | 20.2871 | 35.2782 | 46.7153 | Normal | 35.2782 | 0.39239 | 5 | 42.3338 |  |  |  | 28.2226 | 0.39239 | 20 | Each | 16.3165 | 28.6606 | 39.2153 | Normal | 28.6606 | 0.40477 | 5 | 34.3927 |  |  |  | 22.9285 | 0.40477 | 20 | Each | [15 empty] | 1
| B1041.002a |  | B1041.002a | ACI 318 SMF , Conc Col & Bm = 24" x 36", Beam one side | 10180 | 21420 | 31132 | Normal | 20910.6558 | 0.39092 | 5 | 25704 |  |  |  | 17136 | 0.39092 | 20 | Each | 19492 | 34482 | 45444 | Normal | 33139.3163 | 0.30554 | 5 | 41378.4 |  |  |  | 27585.6 | 0.30554 | 20 | Each | 23992 | 40982 | 53944 | Normal | 39639.3128 | 0.2948 | 5 | 49178.4 |  |  |  | 32785.6 | 0.2948 | 20 | Each | 19492 | 34482 | 45444 | Normal | 33139.3163 | 0.30554 | 5 | 41378.4 |  |  |  | 27585.6 | 0.30554 | 20 | Each | [15 empty] | 8.9824 | 18.9 | 27.4694 | Normal | 18.9 | 0.46403 | 5 | 22.68 |  |  |  | 15.12 | 0.46403 | 20 | Each | 17.1988 | 30.4253 | 40.0976 | Normal | 30.4253 | 0.39478 | 5 | 36.5104 |  |  |  | 24.3402 | 0.39478 | 20 | Each | 21.1694 | 36.1606 | 47.5976 | Normal | 36.1606 | 0.38654 | 5 | 43.3927 |  |  |  | 28.9285 | 0.38654 | 20 | Each | 17.1988 | 30.4253 | 40.0976 | Normal | 30.4253 | 0.39478 | 5 | 36.5104 |  |  |  | 24.3402 | 0.39478 | 20 | Each | [15 empty] | 1
| B1041.002b |  | B1041.002b | ACI 318 SMF , Conc Col & Bm = 24" x 36", Beam both sides | 10180 | 21420 | 31132 | Normal | 20910.6558 | 0.39092 | 5 | 25704 |  |  |  | 17136 | 0.39092 | 20 | Each | 19492 | 34482 | 45444 | Normal | 33139.3163 | 0.30554 | 5 | 41378.4 |  |  |  | 27585.6 | 0.30554 | 20 | Each | 23992 | 40982 | 53944 | Normal | 39639.3128 | 0.2948 | 5 | 49178.4 |  |  |  | 32785.6 | 0.2948 | 20 | Each | 19492 | 34482 | 45444 | Normal | 33139.3163 | 0.30554 | 5 | 41378.4 |  |  |  | 27585.6 | 0.30554 | 20 | Each | [15 empty] | 8.9824 | 18.9 | 27.4694 | Normal | 18.9 | 0.46403 | 5 | 22.68 |  |  |  | 15.12 | 0.46403 | 20 | Each | 17.1988 | 30.4253 | 40.0976 | Normal | 30.4253 | 0.39478 | 5 | 36.5104 |  |  |  | 24.3402 | 0.39478 | 20 | Each | 21.1694 | 36.1606 | 47.5976 | Normal | 36.1606 | 0.38654 | 5 | 43.3927 |  |  |  | 28.9285 | 0.38654 | 20 | Each | 17.1988 | 30.4253 | 40.0976 | Normal | 30.4253 | 0.39478 | 5 | 36.5104 |  |  |  | 24.3402 | 0.39478 | 20 | Each | [15 empty] | 1
| B1041.003a |  | B1041.003a | ACI 318 SMF , Conc Col & Bm = 36" x 36", Beam one side | 10180 | 21420 | 31132 | Normal | 20910.6558 | 0.39092 | 5 | 25704 |  |  |  | 17136 | 0.39092 | 20 | Each | 19492 | 34482 | 45444 | Normal | 33139.3163 | 0.30554 | 5 | 41378.4 |  |  |  | 27585.6 | 0.30554 | 20 | Each | 23992 | 40982 | 53944 | Normal | 39639.3128 | 0.2948 | 5 | 49178.4 |  |  |  | 32785.6 | 0.2948 | 20 | Each | 19492 | 34482 | 45444 | Normal | 33139.3163 | 0.30554 | 5 | 41378.4 |  |  |  | 27585.6 | 0.30554 | 20 | Each | [15 empty] | 8.9824 | 18.9 | 27.4694 | Normal | 18.9 | 0.46403 | 5 | 22.68 |  |  |  | 15.12 | 0.46403 | 20 | Each | 17.1988 | 30.4253 | 40.0976 | Normal | 30.4253 | 0.39478 | 5 | 36.5104 |  |  |  | 24.3402 | 0.39478 | 20 | Each | 21.1694 | 36.1606 | 47.5976 | Normal | 36.1606 | 0.38654 | 5 | 43.3927 |  |  |  | 28.9285 | 0.38654 | 20 | Each | 17.1988 | 30.4253 | 40.0976 | Normal | 30.4253 | 0.39478 | 5 | 36.5104 |  |  |  | 24.3402 | 0.39478 | 20 | Each | [15 empty] | 1
| B1041.003b |  | B1041.003b | ACI 318 SMF , Conc Col & Bm = 36" x 36", Beam both sides | 10180 | 21420 | 31132 | Normal | 20910.6558 | 0.39092 | 5 | 25704 |  |  |  | 17136 | 0.39092 | 20 | Each | 19492 | 34482 | 45444 | Normal | 33139.3163 | 0.30554 | 5 | 41378.4 |  |  |  | 27585.6 | 0.30554 | 20 | Each | 23992 | 40982 | 53944 | Normal | 39639.3128 | 0.2948 | 5 | 49178.4 |  |  |  | 32785.6 | 0.2948 | 20 | Each | 19492 | 34482 | 45444 | Normal | 33139.3163 | 0.30554 | 5 | 41378.4 |  |  |  | 27585.6 | 0.30554 | 20 | Each | [15 empty] | 8.9824 | 18.9 | 27.4694 | Normal | 18.9 | 0.46403 | 5 | 22.68 |  |  |  | 15.12 | 0.46403 | 20 | Each | 17.1988 | 30.4253 | 40.0976 | Normal | 30.4253 | 0.39478 | 5 | 36.5104 |  |  |  | 24.3402 | 0.39478 | 20 | Each | 21.1694 | 36.1606 | 47.5976 | Normal | 36.1606 | 0.38654 | 5 | 43.3927 |  |  |  | 28.9285 | 0.38654 | 20 | Each | 17.1988 | 30.4253 | 40.0976 | Normal | 30.4253 | 0.39478 | 5 | 36.5104 |  |  |  | 24.3402 | 0.39478 | 20 | Each | [15 empty] | 1
| B1041.011a |  | B1041.011a | MF with SMF-conforming beam and column flexural and confinement reinforcement but weak joints , Conc Col & Bm = 24" x 24", Beam one side | 10180 | 21420 | 31132 | Normal | 20910.6558 | 0.39092 | 5 | 25704 |  |  |  | 17136 | 0.39092 | 20 | Each | 18492 | 32482 | 44444 | Normal | 31805.9835 | 0.31834 | 5 | 38978.4 |  |  |  | 25985.6 | 0.31834 | 20 | Each | 22992 | 39982 | 52944 | Normal | 38639.3134 | 0.30243 | 5 | 47978.4 |  |  |  | 31985.6 | 0.30243 | 20 | Each | 18492 | 32482 | 44444 | Normal | 31805.9835 | 0.31834 | 5 | 38978.4 |  |  |  | 25985.6 | 0.31834 | 20 | Each | [15 empty] | 8.9824 | 18.9 | 27.4694 | Normal | 18.9 | 0.46403 | 5 | 22.68 |  |  |  | 15.12 | 0.46403 | 20 | Each | 16.3165 | 28.6606 | 39.2153 | Normal | 28.6606 | 0.40477 | 5 | 34.3927 |  |  |  | 22.9285 | 0.40477 | 20 | Each | 20.2871 | 35.2782 | 46.7153 | Normal | 35.2782 | 0.39239 | 5 | 42.3338 |  |  |  | 28.2226 | 0.39239 | 20 | Each | 16.3165 | 28.6606 | 39.2153 | Normal | 28.6606 | 0.40477 | 5 | 34.3927 |  |  |  | 22.9285 | 0.40477 | 20 | Each | [15 empty] | 1
| B1041.011b |  | B1041.011b | MF with SMF-conforming beam and column flexural and confinement reinforcement but weak joints , Conc Col & Bm = 24" x 24", Beam both sides | 10180 | 21420 | 31132 | Normal | 20910.6558 | 0.39092 | 5 | 25704 |  |  |  | 17136 | 0.39092 | 20 | Each | 18492 | 32482 | 44444 | Normal | 31805.9835 | 0.31834 | 5 | 38978.4 |  |  |  | 25985.6 | 0.31834 | 20 | Each | 22992 | 39982 | 52944 | Normal | 38639.3134 | 0.30243 | 5 | 47978.4 |  |  |  | 31985.6 | 0.30243 | 20 | Each | 18492 | 32482 | 44444 | Normal | 31805.9835 | 0.31834 | 5 | 38978.4 |  |  |  | 25985.6 | 0.31834 | 20 | Each | [15 empty] | 8.9824 | 18.9 | 27.4694 | Normal | 18.9 | 0.46403 | 5 | 22.68 |  |  |  | 15.12 | 0.46403 | 20 | Each | 16.3165 | 28.6606 | 39.2153 | Normal | 28.6606 | 0.40477 | 5 | 34.3927 |  |  |  | 22.9285 | 0.40477 | 20 | Each | 20.2871 | 35.2782 | 46.7153 | Normal | 35.2782 | 0.39239 | 5 | 42.3338 |  |  |  | 28.2226 | 0.39239 | 20 | Each | 16.3165 | 28.6606 | 39.2153 | Normal | 28.6606 | 0.40477 | 5 | 34.3927 |  |  |  | 22.9285 | 0.40477 | 20 | Each | [15 empty] | 1
| B1041.012a |  | B1041.012a | MF with SMF-conforming beam and column flexural and confinement reinforcement but weak joints , Conc Col & Bm = 24" x 36", Beam one side | 10180 | 21420 | 31132 | Normal | 20910.6558 | 0.39092 | 5 | 25704 |  |  |  | 17136 | 0.39092 | 20 | Each | 19492 | 34482 | 45444 | Normal | 33139.3163 | 0.30554 | 5 | 41378.4 |  |  |  | 27585.6 | 0.30554 | 20 | Each | 23992 | 40982 | 53944 | Normal | 39639.3128 | 0.2948 | 5 | 49178.4 |  |  |  | 32785.6 | 0.2948 | 20 | Each | 19492 | 34482 | 45444 | Normal | 33139.3163 | 0.30554 | 5 | 41378.4 |  |  |  | 27585.6 | 0.30554 | 20 | Each | [15 empty] | 8.9824 | 18.9 | 27.4694 | Normal | 18.9 | 0.46403 | 5 | 22.68 |  |  |  | 15.12 | 0.46403 | 20 | Each | 17.1988 | 30.4253 | 40.0976 | Normal | 30.4253 | 0.39478 | 5 | 36.5104 |  |  |  | 24.3402 | 0.39478 | 20 | Each | 21.1694 | 36.1606 | 47.5976 | Normal | 36.1606 | 0.38654 | 5 | 43.3927 |  |  |  | 28.9285 | 0.38654 | 20 | Each | 17.1988 | 30.4253 | 40.0976 | Normal | 30.4253 | 0.39478 | 5 | 36.5104 |  |  |  | 24.3402 | 0.39478 | 20 | Each | [15 empty] | 1
| B1041.012b |  | B1041.012b | MF with SMF-conforming beam and column flexural and confinement reinforcement but weak joints , Conc Col & Bm = 24" x 36", Beam both sides | 10180 | 21420 | 31132 | Normal | 20910.6558 | 0.39092 | 5 | 25704 |  |  |  | 17136 | 0.39092 | 20 | Each | 19492 | 34482 | 45444 | Normal | 33139.3163 | 0.30554 | 5 | 41378.4 |  |  |  | 27585.6 | 0.30554 | 20 | Each | 23992 | 40982 | 53944 | Normal | 39639.3128 | 0.2948 | 5 | 49178.4 |  |  |  | 32785.6 | 0.2948 | 20 | Each | 19492 | 34482 | 45444 | Normal | 33139.3163 | 0.30554 | 5 | 41378.4 |  |  |  | 27585.6 | 0.30554 | 20 | Each | [15 empty] | 8.9824 | 18.9 | 27.4694 | Normal | 18.9 | 0.46403 | 5 | 22.68 |  |  |  | 15.12 | 0.46403 | 20 | Each | 17.1988 | 30.4253 | 40.0976 | Normal | 30.4253 | 0.39478 | 5 | 36.5104 |  |  |  | 24.3402 | 0.39478 | 20 | Each | 21.1694 | 36.1606 | 47.5976 | Normal | 36.1606 | 0.38654 | 5 | 43.3927 |  |  |  | 28.9285 | 0.38654 | 20 | Each | 17.1988 | 30.4253 | 40.0976 | Normal | 30.4253 | 0.39478 | 5 | 36.5104 |  |  |  | 24.3402 | 0.39478 | 20 | Each | [15 empty] | 1
| B1041.013a |  | B1041.013a | MF with SMF-conforming beam and column flexural and confinement reinforcement but weak joints , Conc Col & Bm = 36" x 36", Beam one side | 10180 | 21420 | 31132 | Normal | 20910.6558 | 0.39092 | 5 | 25704 |  |  |  | 17136 | 0.39092 | 20 | Each | 19492 | 34482 | 45444 | Normal | 33139.3163 | 0.30554 | 5 | 41378.4 |  |  |  | 27585.6 | 0.30554 | 20 | Each | 23992 | 40982 | 53944 | Normal | 39639.3128 | 0.2948 | 5 | 49178.4 |  |  |  | 32785.6 | 0.2948 | 20 | Each | 19492 | 34482 | 45444 | Normal | 33139.3163 | 0.30554 | 5 | 41378.4 |  |  |  | 27585.6 | 0.30554 | 20 | Each | [15 empty] | 8.9824 | 18.9 | 27.4694 | Normal | 18.9 | 0.46403 | 5 | 22.68 |  |  |  | 15.12 | 0.46403 | 20 | Each | 17.1988 | 30.4253 | 40.0976 | Normal | 30.4253 | 0.39478 | 5 | 36.5104 |  |  |  | 24.3402 | 0.39478 | 20 | Each | 21.1694 | 36.1606 | 47.5976 | Normal | 36.1606 | 0.38654 | 5 | 43.3927 |  |  |  | 28.9285 | 0.38654 | 20 | Each | 17.1988 | 30.4253 | 40.0976 | Normal | 30.4253 | 0.39478 | 5 | 36.5104 |  |  |  | 24.3402 | 0.39478 | 20 | Each | [15 empty] | 1
| B1041.013b |  | B1041.013b | MF with SMF-conforming beam and column flexural and confinement reinforcement but weak joints , Conc Col & Bm = 36" x 36", Beam both sides | 10180 | 21420 | 31132 | Normal | 20910.6558 | 0.39092 | 5 | 25704 |  |  |  | 17136 | 0.39092 | 20 | Each | 19492 | 34482 | 45444 | Normal | 33139.3163 | 0.30554 | 5 | 41378.4 |  |  |  | 27585.6 | 0.30554 | 20 | Each | 23992 | 40982 | 53944 | Normal | 39639.3128 | 0.2948 | 5 | 49178.4 |  |  |  | 32785.6 | 0.2948 | 20 | Each | 19492 | 34482 | 45444 | Normal | 33139.3163 | 0.30554 | 5 | 41378.4 |  |  |  | 27585.6 | 0.30554 | 20 | Each | [15 empty] | 8.9824 | 18.9 | 27.4694 | Normal | 18.9 | 0.46403 | 5 | 22.68 |  |  |  | 15.12 | 0.46403 | 20 | Each | 17.1988 | 30.4253 | 40.0976 | Normal | 30.4253 | 0.39478 | 5 | 36.5104 |  |  |  | 24.3402 | 0.39478 | 20 | Each | 21.1694 | 36.1606 | 47.5976 | Normal | 36.1606 | 0.38654 | 5 | 43.3927 |  |  |  | 28.9285 | 0.38654 | 20 | Each | 17.1988 | 30.4253 | 40.0976 | Normal | 30.4253 | 0.39478 | 5 | 36.5104 |  |  |  | 24.3402 | 0.39478 | 20 | Each | [15 empty] | 1
| B1041.021a |  | B1041.021a | ACI 318 IMF, Conc Col & Bm = 24" x 24", Beam one side | 10180 | 21420 | 31132 | Normal | 20910.6558 | 0.39092 | 5 | 25704 |  |  |  | 17136 | 0.39092 | 20 | Each | 18492 | 32482 | 44444 | Normal | 31805.9835 | 0.31834 | 5 | 38978.4 |  |  |  | 25985.6 | 0.31834 | 20 | Each | 22992 | 39982 | 52944 | Normal | 38639.3134 | 0.30243 | 5 | 47978.4 |  |  |  | 31985.6 | 0.30243 | 20 | Each | 18492 | 32482 | 44444 | Normal | 31805.9835 | 0.31834 | 5 | 38978.4 |  |  |  | 25985.6 | 0.31834 | 20 | Each | [15 empty] | 8.9824 | 18.9 | 27.4694 | Normal | 18.9 | 0.46403 | 5 | 22.68 |  |  |  | 15.12 | 0.46403 | 20 | Each | 16.3165 | 28.6606 | 39.2153 | Normal | 28.6606 | 0.40477 | 5 | 34.3927 |  |  |  | 22.9285 | 0.40477 | 20 | Each | 20.2871 | 35.2782 | 46.7153 | Normal | 35.2782 | 0.39239 | 5 | 42.3338 |  |  |  | 28.2226 | 0.39239 | 20 | Each | 16.3165 | 28.6606 | 39.2153 | Normal | 28.6606 | 0.40477 | 5 | 34.3927 |  |  |  | 22.9285 | 0.40477 | 20 | Each | [15 empty] | 1
| B1041.021b |  | B1041.021b | ACI 318 IMF, Conc Col & Bm = 24" x 24", Beam both sides | 10180 | 21420 | 31132 | Normal | 20910.6558 | 0.39092 | 5 | 25704 |  |  |  | 17136 | 0.39092 | 20 | Each | 18492 | 32482 | 44444 | Normal | 31805.9835 | 0.31834 | 5 | 38978.4 |  |  |  | 25985.6 | 0.31834 | 20 | Each | 22992 | 39982 | 52944 | Normal | 38639.3134 | 0.30243 | 5 | 47978.4 |  |  |  | 31985.6 | 0.30243 | 20 | Each | 18492 | 32482 | 44444 | Normal | 31805.9835 | 0.31834 | 5 | 38978.4 |  |  |  | 25985.6 | 0.31834 | 20 | Each | [15 empty] | 8.9824 | 18.9 | 27.4694 | Normal | 18.9 | 0.46403 | 5 | 22.68 |  |  |  | 15.12 | 0.46403 | 20 | Each | 16.3165 | 28.6606 | 39.2153 | Normal | 28.6606 | 0.40477 | 5 | 34.3927 |  |  |  | 22.9285 | 0.40477 | 20 | Each | 20.2871 | 35.2782 | 46.7153 | Normal | 35.2782 | 0.39239 | 5 | 42.3338 |  |  |  | 28.2226 | 0.39239 | 20 | Each | 16.3165 | 28.6606 | 39.2153 | Normal | 28.6606 | 0.40477 | 5 | 34.3927 |  |  |  | 22.9285 | 0.40477 | 20 | Each | [15 empty] | 1
| B1041.022a |  | B1041.022a | ACI 318 IMF, Conc Col & Bm = 24" x 36", Beam one side | 10180 | 21420 | 31132 | Normal | 20910.6558 | 0.39092 | 5 | 25704 |  |  |  | 17136 | 0.39092 | 20 | Each | 19492 | 34482 | 45444 | Normal | 33139.3163 | 0.30554 | 5 | 41378.4 |  |  |  | 27585.6 | 0.30554 | 20 | Each | 23992 | 40982 | 53944 | Normal | 39639.3128 | 0.2948 | 5 | 49178.4 |  |  |  | 32785.6 | 0.2948 | 20 | Each | 19492 | 34482 | 45444 | Normal | 33139.3163 | 0.30554 | 5 | 41378.4 |  |  |  | 27585.6 | 0.30554 | 20 | Each | [15 empty] | 8.9824 | 18.9 | 27.4694 | Normal | 18.9 | 0.46403 | 5 | 22.68 |  |  |  | 15.12 | 0.46403 | 20 | Each | 17.1988 | 30.4253 | 40.0976 | Normal | 30.4253 | 0.39478 | 5 | 36.5104 |  |  |  | 24.3402 | 0.39478 | 20 | Each | 21.1694 | 36.1606 | 47.5976 | Normal | 36.1606 | 0.38654 | 5 | 43.3927 |  |  |  | 28.9285 | 0.38654 | 20 | Each | 17.1988 | 30.4253 | 40.0976 | Normal | 30.4253 | 0.39478 | 5 | 36.5104 |  |  |  | 24.3402 | 0.39478 | 20 | Each | [15 empty] | 1
| B1041.022b |  | B1041.022b | ACI 318 IMF, Conc Col & Bm = 24" x 36", Beam both sides | 10180 | 21420 | 31132 | Normal | 20910.6558 | 0.39092 | 5 | 25704 |  |  |  | 17136 | 0.39092 | 20 | Each | 19492 | 34482 | 45444 | Normal | 33139.3163 | 0.30554 | 5 | 41378.4 |  |  |  | 27585.6 | 0.30554 | 20 | Each | 23992 | 40982 | 53944 | Normal | 39639.3128 | 0.2948 | 5 | 49178.4 |  |  |  | 32785.6 | 0.2948 | 20 | Each | 19492 | 34482 | 45444 | Normal | 33139.3163 | 0.30554 | 5 | 41378.4 |  |  |  | 27585.6 | 0.30554 | 20 | Each | [15 empty] | 8.9824 | 18.9 | 27.4694 | Normal | 18.9 | 0.46403 | 5 | 22.68 |  |  |  | 15.12 | 0.46403 | 20 | Each | 17.1988 | 30.4253 | 40.0976 | Normal | 30.4253 | 0.39478 | 5 | 36.5104 |  |  |  | 24.3402 | 0.39478 | 20 | Each | 21.1694 | 36.1606 | 47.5976 | Normal | 36.1606 | 0.38654 | 5 | 43.3927 |  |  |  | 28.9285 | 0.38654 | 20 | Each | 17.1988 | 30.4253 | 40.0976 | Normal | 30.4253 | 0.39478 | 5 | 36.5104 |  |  |  | 24.3402 | 0.39478 | 20 | Each | [15 empty] | 1
| B1041.023a |  | B1041.023a | ACI 318 IMF, Conc Col & Bm = 36" x 36", Beam one side | 10180 | 21420 | 31132 | Normal | 20910.6558 | 0.39092 | 5 | 25704 |  |  |  | 17136 | 0.39092 | 20 | Each | 19492 | 34482 | 45444 | Normal | 33139.3163 | 0.30554 | 5 | 41378.4 |  |  |  | 27585.6 | 0.30554 | 20 | Each | 23992 | 40982 | 53944 | Normal | 39639.3128 | 0.2948 | 5 | 49178.4 |  |  |  | 32785.6 | 0.2948 | 20 | Each | 19492 | 34482 | 45444 | Normal | 33139.3163 | 0.30554 | 5 | 41378.4 |  |  |  | 27585.6 | 0.30554 | 20 | Each | [15 empty] | 8.9824 | 18.9 | 27.4694 | Normal | 18.9 | 0.46403 | 5 | 22.68 |  |  |  | 15.12 | 0.46403 | 20 | Each | 17.1988 | 30.4253 | 40.0976 | Normal | 30.4253 | 0.39478 | 5 | 36.5104 |  |  |  | 24.3402 | 0.39478 | 20 | Each | 21.1694 | 36.1606 | 47.5976 | Normal | 36.1606 | 0.38654 | 5 | 43.3927 |  |  |  | 28.9285 | 0.38654 | 20 | Each | 17.1988 | 30.4253 | 40.0976 | Normal | 30.4253 | 0.39478 | 5 | 36.5104 |  |  |  | 24.3402 | 0.39478 | 20 | Each | [15 empty] | 1
| B1041.023b |  | B1041.023b | ACI 318 IMF, Conc Col & Bm = 36" x 36", Beam both sides | 10180 | 21420 | 31132 | Normal | 20910.6558 | 0.39092 | 5 | 25704 |  |  |  | 17136 | 0.39092 | 20 | Each | 19492 | 34482 | 45444 | Normal | 33139.3163 | 0.30554 | 5 | 41378.4 |  |  |  | 27585.6 | 0.30554 | 20 | Each | 23992 | 40982 | 53944 | Normal | 39639.3128 | 0.2948 | 5 | 49178.4 |  |  |  | 32785.6 | 0.2948 | 20 | Each | 19492 | 34482 | 45444 | Normal | 33139.3163 | 0.30554 | 5 | 41378.4 |  |  |  | 27585.6 | 0.30554 | 20 | Each | [15 empty] | 8.9824 | 18.9 | 27.4694 | Normal | 18.9 | 0.46403 | 5 | 22.68 |  |  |  | 15.12 | 0.46403 | 20 | Each | 17.1988 | 30.4253 | 40.0976 | Normal | 30.4253 | 0.39478 | 5 | 36.5104 |  |  |  | 24.3402 | 0.39478 | 20 | Each | 21.1694 | 36.1606 | 47.5976 | Normal | 36.1606 | 0.38654 | 5 | 43.3927 |  |  |  | 28.9285 | 0.38654 | 20 | Each | 17.1988 | 30.4253 | 40.0976 | Normal | 30.4253 | 0.39478 | 5 | 36.5104 |  |  |  | 24.3402 | 0.39478 | 20 | Each | [15 empty] | 1
| B1041.031a |  | B1041.031a | ACI 318 OMF with weak joints and beam flexural response, Conc Col & Bm = 24" x 24", Beam one side | 10180 | 21420 | 31132 | Normal | 20910.6558 | 0.39092 | 5 | 25704 |  |  |  | 17136 | 0.39092 | 20 | Each | 18492 | 32482 | 44444 | Normal | 31805.9835 | 0.31834 | 5 | 38978.4 |  |  |  | 25985.6 | 0.31834 | 20 | Each | 22992 | 39982 | 52944 | Normal | 38639.3134 | 0.30243 | 5 | 47978.4 |  |  |  | 31985.6 | 0.30243 | 20 | Each | [30 empty] | 8.9824 | 18.9 | 27.4694 | Normal | 18.9 | 0.46403 | 5 | 22.68 |  |  |  | 15.12 | 0.46403 | 20 | Each | 16.3165 | 28.6606 | 39.2153 | Normal | 28.6606 | 0.40477 | 5 | 34.3927 |  |  |  | 22.9285 | 0.40477 | 20 | Each | 20.2871 | 35.2782 | 46.7153 | Normal | 35.2782 | 0.39239 | 5 | 42.3338 |  |  |  | 28.2226 | 0.39239 | 20 | Each | [30 empty] | 1
| B1041.031b |  | B1041.031b | ACI 318 OMF with weak joints and beam flexural response, Conc Col & Bm = 24" x 24", Beam both sides | 10180 | 21420 | 31132 | Normal | 20910.6558 | 0.39092 | 5 | 25704 |  |  |  | 17136 | 0.39092 | 20 | Each | 18492 | 32482 | 44444 | Normal | 31805.9835 | 0.31834 | 5 | 38978.4 |  |  |  | 25985.6 | 0.31834 | 20 | Each | 22992 | 39982 | 52944 | Normal | 38639.3134 | 0.30243 | 5 | 47978.4 |  |  |  | 31985.6 | 0.30243 | 20 | Each | [30 empty] | 8.9824 | 18.9 | 27.4694 | Normal | 18.9 | 0.46403 | 5 | 22.68 |  |  |  | 15.12 | 0.46403 | 20 | Each | 16.3165 | 28.6606 | 39.2153 | Normal | 28.6606 | 0.40477 | 5 | 34.3927 |  |  |  | 22.9285 | 0.40477 | 20 | Each | 20.2871 | 35.2782 | 46.7153 | Normal | 35.2782 | 0.39239 | 5 | 42.3338 |  |  |  | 28.2226 | 0.39239 | 20 | Each | [30 empty] | 1
| B1041.032a |  | B1041.032a | ACI 318 OMF with weak joints and beam flexural response, Conc Col & Bm = 24" x 36", Beam one side | 10180 | 21420 | 31132 | Normal | 20910.6558 | 0.39092 | 5 | 25704 |  |  |  | 17136 | 0.39092 | 20 | Each | 19492 | 34482 | 45444 | Normal | 33139.3163 | 0.30554 | 5 | 41378.4 |  |  |  | 27585.6 | 0.30554 | 20 | Each | 23992 | 40982 | 53944 | Normal | 39639.3128 | 0.2948 | 5 | 49178.4 |  |  |  | 32785.6 | 0.2948 | 20 | Each | [30 empty] | 8.9824 | 18.9 | 27.4694 | Normal | 18.9 | 0.46403 | 5 | 22.68 |  |  |  | 15.12 | 0.46403 | 20 | Each | 17.1988 | 30.4253 | 40.0976 | Normal | 30.4253 | 0.39478 | 5 | 36.5104 |  |  |  | 24.3402 | 0.39478 | 20 | Each | 21.1694 | 36.1606 | 47.5976 | Normal | 36.1606 | 0.38654 | 5 | 43.3927 |  |  |  | 28.9285 | 0.38654 | 20 | Each | [30 empty] | 1
| B1041.032b |  | B1041.032b | ACI 318 OMF with weak joints and beam flexural response, Conc Col & Bm = 24" x 36", Beam both sides | 10180 | 21420 | 31132 | Normal | 20910.6558 | 0.39092 | 5 | 25704 |  |  |  | 17136 | 0.39092 | 20 | Each | 19492 | 34482 | 45444 | Normal | 33139.3163 | 0.30554 | 5 | 41378.4 |  |  |  | 27585.6 | 0.30554 | 20 | Each | 23992 | 40982 | 53944 | Normal | 39639.3128 | 0.2948 | 5 | 49178.4 |  |  |  | 32785.6 | 0.2948 | 20 | Each | [30 empty] | 8.9824 | 18.9 | 27.4694 | Normal | 18.9 | 0.46403 | 5 | 22.68 |  |  |  | 15.12 | 0.46403 | 20 | Each | 17.1988 | 30.4253 | 40.0976 | Normal | 30.4253 | 0.39478 | 5 | 36.5104 |  |  |  | 24.3402 | 0.39478 | 20 | Each | 21.1694 | 36.1606 | 47.5976 | Normal | 36.1606 | 0.38654 | 5 | 43.3927 |  |  |  | 28.9285 | 0.38654 | 20 | Each | [30 empty] | 1
| B1041.033a |  | B1041.033a | ACI 318 OMF with weak joints and beam flexural response, Conc Col & Bm = 36" x 36", Beam one side | 10180 | 21420 | 31132 | Normal | 20910.6558 | 0.39092 | 5 | 25704 |  |  |  | 17136 | 0.39092 | 20 | Each | 19492 | 34482 | 45444 | Normal | 33139.3163 | 0.30554 | 5 | 41378.4 |  |  |  | 27585.6 | 0.30554 | 20 | Each | 23992 | 40982 | 53944 | Normal | 39639.3128 | 0.2948 | 5 | 49178.4 |  |  |  | 32785.6 | 0.2948 | 20 | Each | [30 empty] | 8.9824 | 18.9 | 27.4694 | Normal | 18.9 | 0.46403 | 5 | 22.68 |  |  |  | 15.12 | 0.46403 | 20 | Each | 17.1988 | 30.4253 | 40.0976 | Normal | 30.4253 | 0.39478 | 5 | 36.5104 |  |  |  | 24.3402 | 0.39478 | 20 | Each | 21.1694 | 36.1606 | 47.5976 | Normal | 36.1606 | 0.38654 | 5 | 43.3927 |  |  |  | 28.9285 | 0.38654 | 20 | Each | [30 empty] | 1
| B1041.033b |  | B1041.033b | ACI 318 OMF with weak joints and beam flexural response, Conc Col & Bm = 36" x 36", Beam both sides | 10180 | 21420 | 31132 | Normal | 20910.6558 | 0.39092 | 5 | 25704 |  |  |  | 17136 | 0.39092 | 20 | Each | 19492 | 34482 | 45444 | Normal | 33139.3163 | 0.30554 | 5 | 41378.4 |  |  |  | 27585.6 | 0.30554 | 20 | Each | 23992 | 40982 | 53944 | Normal | 39639.3128 | 0.2948 | 5 | 49178.4 |  |  |  | 32785.6 | 0.2948 | 20 | Each | [30 empty] | 8.9824 | 18.9 | 27.4694 | Normal | 18.9 | 0.46403 | 5 | 22.68 |  |  |  | 15.12 | 0.46403 | 20 | Each | 17.1988 | 30.4253 | 40.0976 | Normal | 30.4253 | 0.39478 | 5 | 36.5104 |  |  |  | 24.3402 | 0.39478 | 20 | Each | 21.1694 | 36.1606 | 47.5976 | Normal | 36.1606 | 0.38654 | 5 | 43.3927 |  |  |  | 28.9285 | 0.38654 | 20 | Each | [30 empty] | 1
| B1041.041a |  | B1041.041a | ACI 318 OMF with weak joints and column flexural response, Conc Col & Bm = 24" x 24", Beam one side | 10180 | 21420 | 31132 | Normal | 20910.6558 | 0.39092 | 5 | 25704 |  |  |  | 17136 | 0.39092 | 20 | Each | 18492 | 32482 | 44444 | Normal | 31805.9835 | 0.31834 | 5 | 38978.4 |  |  |  | 25985.6 | 0.31834 | 20 | Each | 22992 | 39982 | 52944 | Normal | 38639.3134 | 0.30243 | 5 | 47978.4 |  |  |  | 31985.6 | 0.30243 | 20 | Each | [30 empty] | 8.9824 | 18.9 | 27.4694 | Normal | 18.9 | 0.46403 | 5 | 22.68 |  |  |  | 15.12 | 0.46403 | 20 | Each | 16.3165 | 28.6606 | 39.2153 | Normal | 28.6606 | 0.40477 | 5 | 34.3927 |  |  |  | 22.9285 | 0.40477 | 20 | Each | 20.2871 | 35.2782 | 46.7153 | Normal | 35.2782 | 0.39239 | 5 | 42.3338 |  |  |  | 28.2226 | 0.39239 | 20 | Each | [30 empty] | 1
| B1041.041b |  | B1041.041b | ACI 318 OMF with weak joints and column flexural response, Conc Col & Bm = 24" x 24", Beam both sides | 10180 | 21420 | 31132 | Normal | 20910.6558 | 0.39092 | 5 | 25704 |  |  |  | 17136 | 0.39092 | 20 | Each | 18492 | 32482 | 44444 | Normal | 31805.9835 | 0.31834 | 5 | 38978.4 |  |  |  | 25985.6 | 0.31834 | 20 | Each | 22992 | 39982 | 52944 | Normal | 38639.3134 | 0.30243 | 5 | 47978.4 |  |  |  | 31985.6 | 0.30243 | 20 | Each | [30 empty] | 8.9824 | 18.9 | 27.4694 | Normal | 18.9 | 0.46403 | 5 | 22.68 |  |  |  | 15.12 | 0.46403 | 20 | Each | 16.3165 | 28.6606 | 39.2153 | Normal | 28.6606 | 0.40477 | 5 | 34.3927 |  |  |  | 22.9285 | 0.40477 | 20 | Each | 20.2871 | 35.2782 | 46.7153 | Normal | 35.2782 | 0.39239 | 5 | 42.3338 |  |  |  | 28.2226 | 0.39239 | 20 | Each | [30 empty] | 1
| B1041.042a |  | B1041.042a | ACI 318 OMF with weak joints and column flexural response, Conc Col & Bm = 24" x 36", Beam one side | 10180 | 21420 | 31132 | Normal | 20910.6558 | 0.39092 | 5 | 25704 |  |  |  | 17136 | 0.39092 | 20 | Each | 19492 | 34482 | 45444 | Normal | 33139.3163 | 0.30554 | 5 | 41378.4 |  |  |  | 27585.6 | 0.30554 | 20 | Each | 23992 | 40982 | 53944 | Normal | 39639.3128 | 0.2948 | 5 | 49178.4 |  |  |  | 32785.6 | 0.2948 | 20 | Each | [30 empty] | 8.9824 | 18.9 | 27.4694 | Normal | 18.9 | 0.46403 | 5 | 22.68 |  |  |  | 15.12 | 0.46403 | 20 | Each | 17.1988 | 30.4253 | 40.0976 | Normal | 30.4253 | 0.39478 | 5 | 36.5104 |  |  |  | 24.3402 | 0.39478 | 20 | Each | 21.1694 | 36.1606 | 47.5976 | Normal | 36.1606 | 0.38654 | 5 | 43.3927 |  |  |  | 28.9285 | 0.38654 | 20 | Each | [30 empty] | 1
| B1041.042b |  | B1041.042b | ACI 318 OMF with weak joints and column flexural response, Conc Col & Bm = 24" x 36", Beam both sides | 10180 | 21420 | 31132 | Normal | 20910.6558 | 0.39092 | 5 | 25704 |  |  |  | 17136 | 0.39092 | 20 | Each | 19492 | 34482 | 45444 | Normal | 33139.3163 | 0.30554 | 5 | 41378.4 |  |  |  | 27585.6 | 0.30554 | 20 | Each | 23992 | 40982 | 53944 | Normal | 39639.3128 | 0.2948 | 5 | 49178.4 |  |  |  | 32785.6 | 0.2948 | 20 | Each | [30 empty] | 8.9824 | 18.9 | 27.4694 | Normal | 18.9 | 0.46403 | 5 | 22.68 |  |  |  | 15.12 | 0.46403 | 20 | Each | 17.1988 | 30.4253 | 40.0976 | Normal | 30.4253 | 0.39478 | 5 | 36.5104 |  |  |  | 24.3402 | 0.39478 | 20 | Each | 21.1694 | 36.1606 | 47.5976 | Normal | 36.1606 | 0.38654 | 5 | 43.3927 |  |  |  | 28.9285 | 0.38654 | 20 | Each | [30 empty] | 1
| B1041.043a |  | B1041.043a | ACI 318 OMF with weak joints and column flexural response, Conc Col & Bm = 36" x 36", Beam one side | 10180 | 21420 | 31132 | Normal | 20910.6558 | 0.39092 | 5 | 25704 |  |  |  | 17136 | 0.39092 | 20 | Each | 19492 | 34482 | 45444 | Normal | 33139.3163 | 0.30554 | 5 | 41378.4 |  |  |  | 27585.6 | 0.30554 | 20 | Each | 23992 | 40982 | 53944 | Normal | 39639.3128 | 0.2948 | 5 | 49178.4 |  |  |  | 32785.6 | 0.2948 | 20 | Each | [30 empty] | 8.9824 | 18.9 | 27.4694 | Normal | 18.9 | 0.46403 | 5 | 22.68 |  |  |  | 15.12 | 0.46403 | 20 | Each | 17.1988 | 30.4253 | 40.0976 | Normal | 30.4253 | 0.39478 | 5 | 36.5104 |  |  |  | 24.3402 | 0.39478 | 20 | Each | 21.1694 | 36.1606 | 47.5976 | Normal | 36.1606 | 0.38654 | 5 | 43.3927 |  |  |  | 28.9285 | 0.38654 | 20 | Each | [30 empty] | 1
| B1041.043b |  | B1041.043b | ACI 318 OMF with weak joints and column flexural response, Conc Col & Bm = 36" x 36", Beam both sides | 10180 | 21420 | 31132 | Normal | 20910.6558 | 0.39092 | 5 | 25704 |  |  |  | 17136 | 0.39092 | 20 | Each | 19492 | 34482 | 45444 | Normal | 33139.3163 | 0.30554 | 5 | 41378.4 |  |  |  | 27585.6 | 0.30554 | 20 | Each | 23992 | 40982 | 53944 | Normal | 39639.3128 | 0.2948 | 5 | 49178.4 |  |  |  | 32785.6 | 0.2948 | 20 | Each | [30 empty] | 8.9824 | 18.9 | 27.4694 | Normal | 18.9 | 0.46403 | 5 | 22.68 |  |  |  | 15.12 | 0.46403 | 20 | Each | 17.1988 | 30.4253 | 40.0976 | Normal | 30.4253 | 0.39478 | 5 | 36.5104 |  |  |  | 24.3402 | 0.39478 | 20 | Each | 21.1694 | 36.1606 | 47.5976 | Normal | 36.1606 | 0.38654 | 5 | 43.3927 |  |  |  | 28.9285 | 0.38654 | 20 | Each | [30 empty] | 1
| B1041.051a |  | B1041.051a | ACI 318 OMF with weak beams and weak joints, beam flexural or shear response, Conc Col & Bm = 24" x 24", Beam one side | 10180 | 21420 | 31132 | Normal | 20910.6558 | 0.39092 | 5 | 25704 |  |  |  | 17136 | 0.39092 | 20 | Each | 18492 | 32482 | 44444 | Normal | 31805.9835 | 0.31834 | 5 | 38978.4 |  |  |  | 25985.6 | 0.31834 | 20 | Each | 22992 | 39982 | 52944 | Normal | 38639.3134 | 0.30243 | 5 | 47978.4 |  |  |  | 31985.6 | 0.30243 | 20 | Each | [30 empty] | 8.9824 | 18.9 | 27.4694 | Normal | 18.9 | 0.46403 | 5 | 22.68 |  |  |  | 15.12 | 0.46403 | 20 | Each | 16.3165 | 28.6606 | 39.2153 | Normal | 28.6606 | 0.40477 | 5 | 34.3927 |  |  |  | 22.9285 | 0.40477 | 20 | Each | 20.2871 | 35.2782 | 46.7153 | Normal | 35.2782 | 0.39239 | 5 | 42.3338 |  |  |  | 28.2226 | 0.39239 | 20 | Each | [30 empty] | 1
| B1041.051b |  | B1041.051b | ACI 318 OMF with weak beams and weak joints, beam flexural or shear response, Conc Col & Bm = 24" x 24", Beam both sides | 10180 | 21420 | 31132 | Normal | 20910.6558 | 0.39092 | 5 | 25704 |  |  |  | 17136 | 0.39092 | 20 | Each | 18492 | 32482 | 44444 | Normal | 31805.9835 | 0.31834 | 5 | 38978.4 |  |  |  | 25985.6 | 0.31834 | 20 | Each | 22992 | 39982 | 52944 | Normal | 38639.3134 | 0.30243 | 5 | 47978.4 |  |  |  | 31985.6 | 0.30243 | 20 | Each | [30 empty] | 8.9824 | 18.9 | 27.4694 | Normal | 18.9 | 0.46403 | 5 | 22.68 |  |  |  | 15.12 | 0.46403 | 20 | Each | 16.3165 | 28.6606 | 39.2153 | Normal | 28.6606 | 0.40477 | 5 | 34.3927 |  |  |  | 22.9285 | 0.40477 | 20 | Each | 20.2871 | 35.2782 | 46.7153 | Normal | 35.2782 | 0.39239 | 5 | 42.3338 |  |  |  | 28.2226 | 0.39239 | 20 | Each | [30 empty] | 1
| B1041.052a |  | B1041.052a | ACI 318 OMF with weak beams and weak joints, beam flexural or shear response, Conc Col & Bm = 24" x 36", Beam one side | 10180 | 21420 | 31132 | Normal | 20910.6558 | 0.39092 | 5 | 25704 |  |  |  | 17136 | 0.39092 | 20 | Each | 19492 | 34482 | 45444 | Normal | 33139.3163 | 0.30554 | 5 | 41378.4 |  |  |  | 27585.6 | 0.30554 | 20 | Each | 23992 | 40982 | 53944 | Normal | 39639.3128 | 0.2948 | 5 | 49178.4 |  |  |  | 32785.6 | 0.2948 | 20 | Each | [30 empty] | 8.9824 | 18.9 | 27.4694 | Normal | 18.9 | 0.46403 | 5 | 22.68 |  |  |  | 15.12 | 0.46403 | 20 | Each | 17.1988 | 30.4253 | 40.0976 | Normal | 30.4253 | 0.39478 | 5 | 36.5104 |  |  |  | 24.3402 | 0.39478 | 20 | Each | 21.1694 | 36.1606 | 47.5976 | Normal | 36.1606 | 0.38654 | 5 | 43.3927 |  |  |  | 28.9285 | 0.38654 | 20 | Each | [30 empty] | 1
| B1041.052b |  | B1041.052b | ACI 318 OMF with weak beams and weak joints, beam flexural or shear response, Conc Col & Bm = 24" x 36", Beam both sides | 10180 | 21420 | 31132 | Normal | 20910.6558 | 0.39092 | 5 | 25704 |  |  |  | 17136 | 0.39092 | 20 | Each | 19492 | 34482 | 45444 | Normal | 33139.3163 | 0.30554 | 5 | 41378.4 |  |  |  | 27585.6 | 0.30554 | 20 | Each | 23992 | 40982 | 53944 | Normal | 39639.3128 | 0.2948 | 5 | 49178.4 |  |  |  | 32785.6 | 0.2948 | 20 | Each | [30 empty] | 8.9824 | 18.9 | 27.4694 | Normal | 18.9 | 0.46403 | 5 | 22.68 |  |  |  | 15.12 | 0.46403 | 20 | Each | 17.1988 | 30.4253 | 40.0976 | Normal | 30.4253 | 0.39478 | 5 | 36.5104 |  |  |  | 24.3402 | 0.39478 | 20 | Each | 21.1694 | 36.1606 | 47.5976 | Normal | 36.1606 | 0.38654 | 5 | 43.3927 |  |  |  | 28.9285 | 0.38654 | 20 | Each | [30 empty] | 1
| B1041.053a |  | B1041.053a | ACI 318 OMF with weak beams and weak joints, beam flexural or shear response, Conc Col & Bm = 36" x 36", Beam one side | 10180 | 21420 | 31132 | Normal | 20910.6558 | 0.39092 | 5 | 25704 |  |  |  | 17136 | 0.39092 | 20 | Each | 19492 | 34482 | 45444 | Normal | 33139.3163 | 0.30554 | 5 | 41378.4 |  |  |  | 27585.6 | 0.30554 | 20 | Each | 23992 | 40982 | 53944 | Normal | 39639.3128 | 0.2948 | 5 | 49178.4 |  |  |  | 32785.6 | 0.2948 | 20 | Each | [30 empty] | 8.9824 | 18.9 | 27.4694 | Normal | 18.9 | 0.46403 | 5 | 22.68 |  |  |  | 15.12 | 0.46403 | 20 | Each | 17.1988 | 30.4253 | 40.0976 | Normal | 30.4253 | 0.39478 | 5 | 36.5104 |  |  |  | 24.3402 | 0.39478 | 20 | Each | 21.1694 | 36.1606 | 47.5976 | Normal | 36.1606 | 0.38654 | 5 | 43.3927 |  |  |  | 28.9285 | 0.38654 | 20 | Each | [30 empty] | 1
| B1041.053b |  | B1041.053b | ACI 318 OMF with weak beams and weak joints, beam flexural or shear response, Conc Col & Bm = 36" x 36", Beam both sides | 10180 | 21420 | 31132 | Normal | 20910.6558 | 0.39092 | 5 | 25704 |  |  |  | 17136 | 0.39092 | 20 | Each | 19492 | 34482 | 45444 | Normal | 33139.3163 | 0.30554 | 5 | 41378.4 |  |  |  | 27585.6 | 0.30554 | 20 | Each | 23992 | 40982 | 53944 | Normal | 39639.3128 | 0.2948 | 5 | 49178.4 |  |  |  | 32785.6 | 0.2948 | 20 | Each | [30 empty] | 8.9824 | 18.9 | 27.4694 | Normal | 18.9 | 0.46403 | 5 | 22.68 |  |  |  | 15.12 | 0.46403 | 20 | Each | 17.1988 | 30.4253 | 40.0976 | Normal | 30.4253 | 0.39478 | 5 | 36.5104 |  |  |  | 24.3402 | 0.39478 | 20 | Each | 21.1694 | 36.1606 | 47.5976 | Normal | 36.1606 | 0.38654 | 5 | 43.3927 |  |  |  | 28.9285 | 0.38654 | 20 | Each | [30 empty] | 1
| B1041.061a |  | B1041.061a | ACI 318 OMF with weak columns, Conc Col & Bm = 24" x 24", Beam one side | 10180 | 21420 | 31132 | Normal | 20910.6558 | 0.39092 | 5 | 25704 |  |  |  | 17136 | 0.39092 | 20 | Each | 18492 | 32482 | 44444 | Normal | 31805.9835 | 0.31834 | 5 | 38978.4 |  |  |  | 25985.6 | 0.31834 | 20 | Each | 22992 | 39982 | 52944 | Normal | 38639.3134 | 0.30243 | 5 | 47978.4 |  |  |  | 31985.6 | 0.30243 | 20 | Each | [30 empty] | 8.9824 | 18.9 | 27.4694 | Normal | 18.9 | 0.46403 | 5 | 22.68 |  |  |  | 15.12 | 0.46403 | 20 | Each | 16.3165 | 28.6606 | 39.2153 | Normal | 28.6606 | 0.40477 | 5 | 34.3927 |  |  |  | 22.9285 | 0.40477 | 20 | Each | 20.2871 | 35.2782 | 46.7153 | Normal | 35.2782 | 0.39239 | 5 | 42.3338 |  |  |  | 28.2226 | 0.39239 | 20 | Each | [30 empty] | 1
| B1041.061b |  | B1041.061b | ACI 318 OMF with weak columns, Conc Col & Bm = 24" x 24", Beam both sides | 10180 | 21420 | 31132 | Normal | 20910.6558 | 0.39092 | 5 | 25704 |  |  |  | 17136 | 0.39092 | 20 | Each | 18492 | 32482 | 44444 | Normal | 31805.9835 | 0.31834 | 5 | 38978.4 |  |  |  | 25985.6 | 0.31834 | 20 | Each | 22992 | 39982 | 52944 | Normal | 38639.3134 | 0.30243 | 5 | 47978.4 |  |  |  | 31985.6 | 0.30243 | 20 | Each | [30 empty] | 8.9824 | 18.9 | 27.4694 | Normal | 18.9 | 0.46403 | 5 | 22.68 |  |  |  | 15.12 | 0.46403 | 20 | Each | 16.3165 | 28.6606 | 39.2153 | Normal | 28.6606 | 0.40477 | 5 | 34.3927 |  |  |  | 22.9285 | 0.40477 | 20 | Each | 20.2871 | 35.2782 | 46.7153 | Normal | 35.2782 | 0.39239 | 5 | 42.3338 |  |  |  | 28.2226 | 0.39239 | 20 | Each | [30 empty] | 1
| B1041.062a |  | B1041.062a | ACI 318 OMF with weak columns, Conc Col & Bm = 24" x 36", Beam one side | 10180 | 21420 | 31132 | Normal | 20910.6558 | 0.39092 | 5 | 25704 |  |  |  | 17136 | 0.39092 | 20 | Each | 19492 | 34482 | 45444 | Normal | 33139.3163 | 0.30554 | 5 | 41378.4 |  |  |  | 27585.6 | 0.30554 | 20 | Each | 23992 | 40982 | 53944 | Normal | 39639.3128 | 0.2948 | 5 | 49178.4 |  |  |  | 32785.6 | 0.2948 | 20 | Each | [30 empty] | 8.9824 | 18.9 | 27.4694 | Normal | 18.9 | 0.46403 | 5 | 22.68 |  |  |  | 15.12 | 0.46403 | 20 | Each | 17.1988 | 30.4253 | 40.0976 | Normal | 30.4253 | 0.39478 | 5 | 36.5104 |  |  |  | 24.3402 | 0.39478 | 20 | Each | 21.1694 | 36.1606 | 47.5976 | Normal | 36.1606 | 0.38654 | 5 | 43.3927 |  |  |  | 28.9285 | 0.38654 | 20 | Each | [30 empty] | 1
| B1041.062b |  | B1041.062b | ACI 318 OMF with weak columns, Conc Col & Bm = 24" x 36", Beam both sides | 10180 | 21420 | 31132 | Normal | 20910.6558 | 0.39092 | 5 | 25704 |  |  |  | 17136 | 0.39092 | 20 | Each | 19492 | 34482 | 45444 | Normal | 33139.3163 | 0.30554 | 5 | 41378.4 |  |  |  | 27585.6 | 0.30554 | 20 | Each | 23992 | 40982 | 53944 | Normal | 39639.3128 | 0.2948 | 5 | 49178.4 |  |  |  | 32785.6 | 0.2948 | 20 | Each | [30 empty] | 8.9824 | 18.9 | 27.4694 | Normal | 18.9 | 0.46403 | 5 | 22.68 |  |  |  | 15.12 | 0.46403 | 20 | Each | 17.1988 | 30.4253 | 40.0976 | Normal | 30.4253 | 0.39478 | 5 | 36.5104 |  |  |  | 24.3402 | 0.39478 | 20 | Each | 21.1694 | 36.1606 | 47.5976 | Normal | 36.1606 | 0.38654 | 5 | 43.3927 |  |  |  | 28.9285 | 0.38654 | 20 | Each | [30 empty] | 1
| B1041.063a |  | B1041.063a | ACI 318 OMF with weak columns, Conc Col & Bm = 36" x 36", Beam one side | 10180 | 21420 | 31132 | Normal | 20910.6558 | 0.39092 | 5 | 25704 |  |  |  | 17136 | 0.39092 | 20 | Each | 19492 | 34482 | 45444 | Normal | 33139.3163 | 0.30554 | 5 | 41378.4 |  |  |  | 27585.6 | 0.30554 | 20 | Each | 23992 | 40982 | 53944 | Normal | 39639.3128 | 0.2948 | 5 | 49178.4 |  |  |  | 32785.6 | 0.2948 | 20 | Each | [30 empty] | 8.9824 | 18.9 | 27.4694 | Normal | 18.9 | 0.46403 | 5 | 22.68 |  |  |  | 15.12 | 0.46403 | 20 | Each | 17.1988 | 30.4253 | 40.0976 | Normal | 30.4253 | 0.39478 | 5 | 36.5104 |  |  |  | 24.3402 | 0.39478 | 20 | Each | 21.1694 | 36.1606 | 47.5976 | Normal | 36.1606 | 0.38654 | 5 | 43.3927 |  |  |  | 28.9285 | 0.38654 | 20 | Each | [30 empty] | 1
| B1041.063b |  | B1041.063b | ACI 318 OMF with weak columns, Conc Col & Bm = 36" x 36", Beam both sides | 10180 | 21420 | 31132 | Normal | 20910.6558 | 0.39092 | 5 | 25704 |  |  |  | 17136 | 0.39092 | 20 | Each | 19492 | 34482 | 45444 | Normal | 33139.3163 | 0.30554 | 5 | 41378.4 |  |  |  | 27585.6 | 0.30554 | 20 | Each | 23992 | 40982 | 53944 | Normal | 39639.3128 | 0.2948 | 5 | 49178.4 |  |  |  | 32785.6 | 0.2948 | 20 | Each | [30 empty] | 8.9824 | 18.9 | 27.4694 | Normal | 18.9 | 0.46403 | 5 | 22.68 |  |  |  | 15.12 | 0.46403 | 20 | Each | 17.1988 | 30.4253 | 40.0976 | Normal | 30.4253 | 0.39478 | 5 | 36.5104 |  |  |  | 24.3402 | 0.39478 | 20 | Each | 21.1694 | 36.1606 | 47.5976 | Normal | 36.1606 | 0.38654 | 5 | 43.3927 |  |  |  | 28.9285 | 0.38654 | 20 | Each | [30 empty] | 1
| B1041.071a |  | B1041.071a | ACI 318 OMF weak columns w/ high axial load, Conc Col & Bm = 24" x 24", Beam one side | 10180 | 21420 | 31132 | Normal | 20910.6558 | 0.39092 | 5 | 25704 |  |  |  | 17136 | 0.39092 | 20 | Each | 18492 | 32482 | 44444 | Normal | 31805.9835 | 0.31834 | 5 | 38978.4 |  |  |  | 25985.6 | 0.31834 | 20 | Each | [45 empty] | 8.9824 | 18.9 | 27.4694 | Normal | 18.9 | 0.46403 | 5 | 22.68 |  |  |  | 15.12 | 0.46403 | 20 | Each | 16.3165 | 28.6606 | 39.2153 | Normal | 28.6606 | 0.40477 | 5 | 34.3927 |  |  |  | 22.9285 | 0.40477 | 20 | Each | [45 empty] | 1
| B1041.071b |  | B1041.071b | ACI 318 OMF weak columns w/ high axial load, Conc Col & Bm = 24" x 24", Beam both sides | 10180 | 21420 | 31132 | Normal | 20910.6558 | 0.39092 | 5 | 25704 |  |  |  | 17136 | 0.39092 | 20 | Each | 18492 | 32482 | 44444 | Normal | 31805.9835 | 0.31834 | 5 | 38978.4 |  |  |  | 25985.6 | 0.31834 | 20 | Each | [45 empty] | 8.9824 | 18.9 | 27.4694 | Normal | 18.9 | 0.46403 | 5 | 22.68 |  |  |  | 15.12 | 0.46403 | 20 | Each | 16.3165 | 28.6606 | 39.2153 | Normal | 28.6606 | 0.40477 | 5 | 34.3927 |  |  |  | 22.9285 | 0.40477 | 20 | Each | [45 empty] | 1
| B1041.072a |  | B1041.072a | ACI 318 OMF weak columns w/ high axial load, Conc Col & Bm = 24" x 36", Beam one side | 10180 | 21420 | 31132 | Normal | 20910.6558 | 0.39092 | 5 | 25704 |  |  |  | 17136 | 0.39092 | 20 | Each | 19492 | 34482 | 45444 | Normal | 33139.3163 | 0.30554 | 5 | 41378.4 |  |  |  | 27585.6 | 0.30554 | 20 | Each | [45 empty] | 8.9824 | 18.9 | 27.4694 | Normal | 18.9 | 0.46403 | 5 | 22.68 |  |  |  | 15.12 | 0.46403 | 20 | Each | 17.1988 | 30.4253 | 40.0976 | Normal | 30.4253 | 0.39478 | 5 | 36.5104 |  |  |  | 24.3402 | 0.39478 | 20 | Each | [45 empty] | 1
| B1041.072b |  | B1041.072b | ACI 318 OMF weak columns w/ high axial load, Conc Col & Bm = 24" x 36", Beam both sides | 10180 | 21420 | 31132 | Normal | 20910.6558 | 0.39092 | 5 | 25704 |  |  |  | 17136 | 0.39092 | 20 | Each | 19492 | 34482 | 45444 | Normal | 33139.3163 | 0.30554 | 5 | 41378.4 |  |  |  | 27585.6 | 0.30554 | 20 | Each | [45 empty] | 8.9824 | 18.9 | 27.4694 | Normal | 18.9 | 0.46403 | 5 | 22.68 |  |  |  | 15.12 | 0.46403 | 20 | Each | 17.1988 | 30.4253 | 40.0976 | Normal | 30.4253 | 0.39478 | 5 | 36.5104 |  |  |  | 24.3402 | 0.39478 | 20 | Each | [45 empty] | 1
| B1041.073a |  | B1041.073a | ACI 318 OMF weak columns w/ high axial load, Conc Col & Bm = 36" x 36", Beam one side | 10180 | 21420 | 31132 | Normal | 20910.6558 | 0.39092 | 5 | 25704 |  |  |  | 17136 | 0.39092 | 20 | Each | 19492 | 34482 | 45444 | Normal | 33139.3163 | 0.30554 | 5 | 41378.4 |  |  |  | 27585.6 | 0.30554 | 20 | Each | [45 empty] | 8.9824 | 18.9 | 27.4694 | Normal | 18.9 | 0.46403 | 5 | 22.68 |  |  |  | 15.12 | 0.46403 | 20 | Each | 17.1988 | 30.4253 | 40.0976 | Normal | 30.4253 | 0.39478 | 5 | 36.5104 |  |  |  | 24.3402 | 0.39478 | 20 | Each | [45 empty] | 1
| B1041.073b |  | B1041.073b | ACI 318 OMF weak columns w/ high axial load, Conc Col & Bm = 36" x 36", Beam both sides | 10180 | 21420 | 31132 | Normal | 20910.6558 | 0.39092 | 5 | 25704 |  |  |  | 17136 | 0.39092 | 20 | Each | 19492 | 34482 | 45444 | Normal | 33139.3163 | 0.30554 | 5 | 41378.4 |  |  |  | 27585.6 | 0.30554 | 20 | Each | [45 empty] | 8.9824 | 18.9 | 27.4694 | Normal | 18.9 | 0.46403 | 5 | 22.68 |  |  |  | 15.12 | 0.46403 | 20 | Each | 17.1988 | 30.4253 | 40.0976 | Normal | 30.4253 | 0.39478 | 5 | 36.5104 |  |  |  | 24.3402 | 0.39478 | 20 | Each | [45 empty] | 1
| B1041.081a |  | B1041.081a | Non-conforming MF with weak joints and beam flexural response, Conc Col & Bm = 24" x 24", Beam one side | 10180 | 21420 | 31132 | Normal | 20910.6558 | 0.39092 | 5 | 25704 |  |  |  | 17136 | 0.39092 | 20 | Each | 18492 | 32482 | 44444 | Normal | 31805.9835 | 0.31834 | 5 | 38978.4 |  |  |  | 25985.6 | 0.31834 | 20 | Each | 22992 | 39982 | 52944 | Normal | 38639.3134 | 0.30243 | 5 | 47978.4 |  |  |  | 31985.6 | 0.30243 | 20 | Each | [30 empty] | 8.9824 | 18.9 | 27.4694 | Normal | 18.9 | 0.46403 | 5 | 22.68 |  |  |  | 15.12 | 0.46403 | 20 | Each | 16.3165 | 28.6606 | 39.2153 | Normal | 28.6606 | 0.40477 | 5 | 34.3927 |  |  |  | 22.9285 | 0.40477 | 20 | Each | 20.2871 | 35.2782 | 46.7153 | Normal | 35.2782 | 0.39239 | 5 | 42.3338 |  |  |  | 28.2226 | 0.39239 | 20 | Each | [30 empty] | 1
| B1041.081b |  | B1041.081b | Non-conforming MF with weak joints and beam flexural response, Conc Col & Bm = 24" x 24", Beam both sides | 10180 | 21420 | 31132 | Normal | 20910.6558 | 0.39092 | 5 | 25704 |  |  |  | 17136 | 0.39092 | 20 | Each | 18492 | 32482 | 44444 | Normal | 31805.9835 | 0.31834 | 5 | 38978.4 |  |  |  | 25985.6 | 0.31834 | 20 | Each | 22992 | 39982 | 52944 | Normal | 38639.3134 | 0.30243 | 5 | 47978.4 |  |  |  | 31985.6 | 0.30243 | 20 | Each | [30 empty] | 8.9824 | 18.9 | 27.4694 | Normal | 18.9 | 0.46403 | 5 | 22.68 |  |  |  | 15.12 | 0.46403 | 20 | Each | 16.3165 | 28.6606 | 39.2153 | Normal | 28.6606 | 0.40477 | 5 | 34.3927 |  |  |  | 22.9285 | 0.40477 | 20 | Each | 20.2871 | 35.2782 | 46.7153 | Normal | 35.2782 | 0.39239 | 5 | 42.3338 |  |  |  | 28.2226 | 0.39239 | 20 | Each | [30 empty] | 1
| B1041.082a |  | B1041.082a | Non-conforming MF with weak joints and beam flexural response, Conc Col & Bm = 24" x 36", Beam one side | 10180 | 21420 | 31132 | Normal | 20910.6558 | 0.39092 | 5 | 25704 |  |  |  | 17136 | 0.39092 | 20 | Each | 19492 | 34482 | 45444 | Normal | 33139.3163 | 0.30554 | 5 | 41378.4 |  |  |  | 27585.6 | 0.30554 | 20 | Each | 23992 | 40982 | 53944 | Normal | 39639.3128 | 0.2948 | 5 | 49178.4 |  |  |  | 32785.6 | 0.2948 | 20 | Each | [30 empty] | 8.9824 | 18.9 | 27.4694 | Normal | 18.9 | 0.46403 | 5 | 22.68 |  |  |  | 15.12 | 0.46403 | 20 | Each | 17.1988 | 30.4253 | 40.0976 | Normal | 30.4253 | 0.39478 | 5 | 36.5104 |  |  |  | 24.3402 | 0.39478 | 20 | Each | 21.1694 | 36.1606 | 47.5976 | Normal | 36.1606 | 0.38654 | 5 | 43.3927 |  |  |  | 28.9285 | 0.38654 | 20 | Each | [30 empty] | 1
| B1041.082b |  | B1041.082b | Non-conforming MF with weak joints and beam flexural response, Conc Col & Bm = 24" x 36", Beam both sides | 10180 | 21420 | 31132 | Normal | 20910.6558 | 0.39092 | 5 | 25704 |  |  |  | 17136 | 0.39092 | 20 | Each | 19492 | 34482 | 45444 | Normal | 33139.3163 | 0.30554 | 5 | 41378.4 |  |  |  | 27585.6 | 0.30554 | 20 | Each | 23992 | 40982 | 53944 | Normal | 39639.3128 | 0.2948 | 5 | 49178.4 |  |  |  | 32785.6 | 0.2948 | 20 | Each | [30 empty] | 8.9824 | 18.9 | 27.4694 | Normal | 18.9 | 0.46403 | 5 | 22.68 |  |  |  | 15.12 | 0.46403 | 20 | Each | 17.1988 | 30.4253 | 40.0976 | Normal | 30.4253 | 0.39478 | 5 | 36.5104 |  |  |  | 24.3402 | 0.39478 | 20 | Each | 21.1694 | 36.1606 | 47.5976 | Normal | 36.1606 | 0.38654 | 5 | 43.3927 |  |  |  | 28.9285 | 0.38654 | 20 | Each | [30 empty] | 1
| B1041.083a |  | B1041.083a | Non-conforming MF with weak joints and beam flexural response, Conc Col & Bm = 36" x 36", Beam one side | 10180 | 21420 | 31132 | Normal | 20910.6558 | 0.39092 | 5 | 25704 |  |  |  | 17136 | 0.39092 | 20 | Each | 19492 | 34482 | 45444 | Normal | 33139.3163 | 0.30554 | 5 | 41378.4 |  |  |  | 27585.6 | 0.30554 | 20 | Each | 23992 | 40982 | 53944 | Normal | 39639.3128 | 0.2948 | 5 | 49178.4 |  |  |  | 32785.6 | 0.2948 | 20 | Each | [30 empty] | 8.9824 | 18.9 | 27.4694 | Normal | 18.9 | 0.46403 | 5 | 22.68 |  |  |  | 15.12 | 0.46403 | 20 | Each | 17.1988 | 30.4253 | 40.0976 | Normal | 30.4253 | 0.39478 | 5 | 36.5104 |  |  |  | 24.3402 | 0.39478 | 20 | Each | 21.1694 | 36.1606 | 47.5976 | Normal | 36.1606 | 0.38654 | 5 | 43.3927 |  |  |  | 28.9285 | 0.38654 | 20 | Each | [30 empty] | 1
| B1041.083b |  | B1041.083b | Non-conforming MF with weak joints and beam flexural response, Conc Col & Bm = 36" x 36", Beam both sides | 10180 | 21420 | 31132 | Normal | 20910.6558 | 0.39092 | 5 | 25704 |  |  |  | 17136 | 0.39092 | 20 | Each | 19492 | 34482 | 45444 | Normal | 33139.3163 | 0.30554 | 5 | 41378.4 |  |  |  | 27585.6 | 0.30554 | 20 | Each | 23992 | 40982 | 53944 | Normal | 39639.3128 | 0.2948 | 5 | 49178.4 |  |  |  | 32785.6 | 0.2948 | 20 | Each | [30 empty] | 8.9824 | 18.9 | 27.4694 | Normal | 18.9 | 0.46403 | 5 | 22.68 |  |  |  | 15.12 | 0.46403 | 20 | Each | 17.1988 | 30.4253 | 40.0976 | Normal | 30.4253 | 0.39478 | 5 | 36.5104 |  |  |  | 24.3402 | 0.39478 | 20 | Each | 21.1694 | 36.1606 | 47.5976 | Normal | 36.1606 | 0.38654 | 5 | 43.3927 |  |  |  | 28.9285 | 0.38654 | 20 | Each | [30 empty] | 1
| B1041.091a |  | B1041.091a | Non-conforming MF with weak joints and column flexural response, Conc Col & Bm = 24" x 24", Beam one side | 10180 | 21420 | 31132 | Normal | 20910.6558 | 0.39092 | 5 | 25704 |  |  |  | 17136 | 0.39092 | 20 | Each | 18492 | 32482 | 44444 | Normal | 31805.9835 | 0.31834 | 5 | 38978.4 |  |  |  | 25985.6 | 0.31834 | 20 | Each | 22992 | 39982 | 52944 | Normal | 38639.3134 | 0.30243 | 5 | 47978.4 |  |  |  | 31985.6 | 0.30243 | 20 | Each | [30 empty] | 8.9824 | 18.9 | 27.4694 | Normal | 18.9 | 0.46403 | 5 | 22.68 |  |  |  | 15.12 | 0.46403 | 20 | Each | 16.3165 | 28.6606 | 39.2153 | Normal | 28.6606 | 0.40477 | 5 | 34.3927 |  |  |  | 22.9285 | 0.40477 | 20 | Each | 20.2871 | 35.2782 | 46.7153 | Normal | 35.2782 | 0.39239 | 5 | 42.3338 |  |  |  | 28.2226 | 0.39239 | 20 | Each | [30 empty] | 1
| B1041.091b |  | B1041.091b | Non-conforming MF with weak joints and column flexural response, Conc Col & Bm = 24" x 24", Beam both sides | 10180 | 21420 | 31132 | Normal | 20910.6558 | 0.39092 | 5 | 25704 |  |  |  | 17136 | 0.39092 | 20 | Each | 18492 | 32482 | 44444 | Normal | 31805.9835 | 0.31834 | 5 | 38978.4 |  |  |  | 25985.6 | 0.31834 | 20 | Each | 22992 | 39982 | 52944 | Normal | 38639.3134 | 0.30243 | 5 | 47978.4 |  |  |  | 31985.6 | 0.30243 | 20 | Each | [30 empty] | 8.9824 | 18.9 | 27.4694 | Normal | 18.9 | 0.46403 | 5 | 22.68 |  |  |  | 15.12 | 0.46403 | 20 | Each | 16.3165 | 28.6606 | 39.2153 | Normal | 28.6606 | 0.40477 | 5 | 34.3927 |  |  |  | 22.9285 | 0.40477 | 20 | Each | 20.2871 | 35.2782 | 46.7153 | Normal | 35.2782 | 0.39239 | 5 | 42.3338 |  |  |  | 28.2226 | 0.39239 | 20 | Each | [30 empty] | 1
| B1041.092a |  | B1041.092a | Non-conforming MF with weak joints and column flexural response, Conc Col & Bm = 24" x 36", Beam one side | 10180 | 21420 | 31132 | Normal | 20910.6558 | 0.39092 | 5 | 26775 |  |  |  | 18207 | 0.39092 | 20 | Each | 19492 | 34482 | 45444 | Normal | 33139.3163 | 0.30554 | 5 | 43102.5 |  |  |  | 29309.7 | 0.30554 | 20 | Each | 23992 | 40982 | 53944 | Normal | 39639.3128 | 0.2948 | 5 | 51227.5 |  |  |  | 34834.7 | 0.2948 | 20 | Each | [30 empty] | 8.9824 | 18.9 | 27.4694 | Normal | 18.9 | 0.46403 | 5 | 23.625 |  |  |  | 16.065 | 0.46403 | 20 | Each | 17.1988 | 30.4253 | 40.0976 | Normal | 30.4253 | 0.39478 | 5 | 38.0316 |  |  |  | 25.8615 | 0.39478 | 20 | Each | 21.1694 | 36.1606 | 47.5976 | Normal | 36.1606 | 0.38654 | 5 | 45.2007 |  |  |  | 30.7365 | 0.38654 | 20 | Each | [30 empty] | 1
| B1041.092b |  | B1041.092b | Non-conforming MF with weak joints and column flexural response, Conc Col & Bm = 24" x 36", Beam both sides | 10180 | 21420 | 31132 | Normal | 20910.6558 | 0.39092 | 5 | 26775 |  |  |  | 18207 | 0.39092 | 20 | Each | 19492 | 34482 | 45444 | Normal | 33139.3163 | 0.30554 | 5 | 43102.5 |  |  |  | 29309.7 | 0.30554 | 20 | Each | 23992 | 40982 | 53944 | Normal | 39639.3128 | 0.2948 | 5 | 51227.5 |  |  |  | 34834.7 | 0.2948 | 20 | Each | [30 empty] | 8.9824 | 18.9 | 27.4694 | Normal | 18.9 | 0.46403 | 5 | 23.625 |  |  |  | 16.065 | 0.46403 | 20 | Each | 17.1988 | 30.4253 | 40.0976 | Normal | 30.4253 | 0.39478 | 5 | 38.0316 |  |  |  | 25.8615 | 0.39478 | 20 | Each | 21.1694 | 36.1606 | 47.5976 | Normal | 36.1606 | 0.38654 | 5 | 45.2007 |  |  |  | 30.7365 | 0.38654 | 20 | Each | [30 empty] | 1
| B1041.093a |  | B1041.093a | Non-conforming MF with weak joints and column flexural response, Conc Col & Bm = 36" x 36", Beam one side | 10180 | 21420 | 31132 | Normal | 20910.6558 | 0.39092 | 5 | 26775 |  |  |  | 18207 | 0.39092 | 20 | Each | 19492 | 34482 | 45444 | Normal | 33139.3163 | 0.30554 | 5 | 43102.5 |  |  |  | 29309.7 | 0.30554 | 20 | Each | 23992 | 40982 | 53944 | Normal | 39639.3128 | 0.2948 | 5 | 51227.5 |  |  |  | 34834.7 | 0.2948 | 20 | Each | [30 empty] | 8.9824 | 18.9 | 27.4694 | Normal | 18.9 | 0.46403 | 5 | 23.625 |  |  |  | 16.065 | 0.46403 | 20 | Each | 17.1988 | 30.4253 | 40.0976 | Normal | 30.4253 | 0.39478 | 5 | 38.0316 |  |  |  | 25.8615 | 0.39478 | 20 | Each | 21.1694 | 36.1606 | 47.5976 | Normal | 36.1606 | 0.38654 | 5 | 45.2007 |  |  |  | 30.7365 | 0.38654 | 20 | Each | [30 empty] | 1
| B1041.093b |  | B1041.093b | Non-conforming MF with weak joints and column flexural response, Conc Col & Bm = 36" x 36", Beam both sides | 10180 | 21420 | 31132 | Normal | 20910.6558 | 0.39092 | 5 | 26775 |  |  |  | 18207 | 0.39092 | 20 | Each | 19492 | 34482 | 45444 | Normal | 33139.3163 | 0.30554 | 5 | 43102.5 |  |  |  | 29309.7 | 0.30554 | 20 | Each | 23992 | 40982 | 53944 | Normal | 39639.3128 | 0.2948 | 5 | 51227.5 |  |  |  | 34834.7 | 0.2948 | 20 | Each | [30 empty] | 8.9824 | 18.9 | 27.4694 | Normal | 18.9 | 0.46403 | 5 | 23.625 |  |  |  | 16.065 | 0.46403 | 20 | Each | 17.1988 | 30.4253 | 40.0976 | Normal | 30.4253 | 0.39478 | 5 | 38.0316 |  |  |  | 25.8615 | 0.39478 | 20 | Each | 21.1694 | 36.1606 | 47.5976 | Normal | 36.1606 | 0.38654 | 5 | 45.2007 |  |  |  | 30.7365 | 0.38654 | 20 | Each | [30 empty] | 1
| B1041.101a |  | B1041.101a | Non-conforming MF, weak beams and strong joints, Conc Col & Bm = 24" x 24", Beam one side | 10180 | 21420 | 31132 | Normal | 20910.6558 | 0.39092 | 5 | 26775 |  |  |  | 18207 | 0.39092 | 20 | Each | 18492 | 32482 | 44444 | Normal | 31805.9835 | 0.31834 | 5 | 40602.5 |  |  |  | 27609.7 | 0.31834 | 20 | Each | 22992 | 39982 | 52944 | Normal | 38639.3134 | 0.30243 | 5 | 49977.5 |  |  |  | 33984.7 | 0.30243 | 20 | Each | [30 empty] | 8.9824 | 18.9 | 27.4694 | Normal | 18.9 | 0.46403 | 5 | 23.625 |  |  |  | 16.065 | 0.46403 | 20 | Each | 16.3165 | 28.6606 | 39.2153 | Normal | 28.6606 | 0.40477 | 5 | 35.8257 |  |  |  | 24.3615 | 0.40477 | 20 | Each | 20.2871 | 35.2782 | 46.7153 | Normal | 35.2782 | 0.39239 | 5 | 44.0978 |  |  |  | 29.9865 | 0.39239 | 20 | Each | [30 empty] | 1
| B1041.101b |  | B1041.101b | Non-conforming MF, weak beams and strong joints, Conc Col & Bm = 24" x 24", Beam both sides | 10180 | 21420 | 31132 | Normal | 20910.6558 | 0.39092 | 5 | 26775 |  |  |  | 18207 | 0.39092 | 20 | Each | 18492 | 32482 | 44444 | Normal | 31805.9835 | 0.31834 | 5 | 40602.5 |  |  |  | 27609.7 | 0.31834 | 20 | Each | 22992 | 39982 | 52944 | Normal | 38639.3134 | 0.30243 | 5 | 49977.5 |  |  |  | 33984.7 | 0.30243 | 20 | Each | [30 empty] | 8.9824 | 18.9 | 27.4694 | Normal | 18.9 | 0.46403 | 5 | 23.625 |  |  |  | 16.065 | 0.46403 | 20 | Each | 16.3165 | 28.6606 | 39.2153 | Normal | 28.6606 | 0.40477 | 5 | 35.8257 |  |  |  | 24.3615 | 0.40477 | 20 | Each | 20.2871 | 35.2782 | 46.7153 | Normal | 35.2782 | 0.39239 | 5 | 44.0978 |  |  |  | 29.9865 | 0.39239 | 20 | Each | [30 empty] | 1
| B1041.102a |  | B1041.102a | Non-conforming MF, weak beams and strong joints, Conc Col & Bm = 24" x 36", Beam one side | 10180 | 21420 | 31132 | Normal | 20910.6558 | 0.39092 | 5 | 26775 |  |  |  | 18207 | 0.39092 | 20 | Each | 19492 | 34482 | 45444 | Normal | 33139.3163 | 0.30554 | 5 | 43102.5 |  |  |  | 29309.7 | 0.30554 | 20 | Each | 23992 | 40982 | 53944 | Normal | 39639.3128 | 0.2948 | 5 | 51227.5 |  |  |  | 34834.7 | 0.2948 | 20 | Each | [30 empty] | 8.9824 | 18.9 | 27.4694 | Normal | 18.9 | 0.46403 | 5 | 23.625 |  |  |  | 16.065 | 0.46403 | 20 | Each | 17.1988 | 30.4253 | 40.0976 | Normal | 30.4253 | 0.39478 | 5 | 38.0316 |  |  |  | 25.8615 | 0.39478 | 20 | Each | 21.1694 | 36.1606 | 47.5976 | Normal | 36.1606 | 0.38654 | 5 | 45.2007 |  |  |  | 30.7365 | 0.38654 | 20 | Each | [30 empty] | 1
| B1041.102b |  | B1041.102b | Non-conforming MF, weak beams and strong joints, Conc Col & Bm = 24" x 36", Beam both sides | 10180 | 21420 | 31132 | Normal | 20910.6558 | 0.39092 | 5 | 26775 |  |  |  | 18207 | 0.39092 | 20 | Each | 19492 | 34482 | 45444 | Normal | 33139.3163 | 0.30554 | 5 | 43102.5 |  |  |  | 29309.7 | 0.30554 | 20 | Each | 23992 | 40982 | 53944 | Normal | 39639.3128 | 0.2948 | 5 | 51227.5 |  |  |  | 34834.7 | 0.2948 | 20 | Each | [30 empty] | 8.9824 | 18.9 | 27.4694 | Normal | 18.9 | 0.46403 | 5 | 23.625 |  |  |  | 16.065 | 0.46403 | 20 | Each | 17.1988 | 30.4253 | 40.0976 | Normal | 30.4253 | 0.39478 | 5 | 38.0316 |  |  |  | 25.8615 | 0.39478 | 20 | Each | 21.1694 | 36.1606 | 47.5976 | Normal | 36.1606 | 0.38654 | 5 | 45.2007 |  |  |  | 30.7365 | 0.38654 | 20 | Each | [30 empty] | 1
| B1041.103a |  | B1041.103a | Non-conforming MF, weak beams and strong joints, Conc Col & Bm = 36" x 36", Beam one side | 10180 | 21420 | 31132 | Normal | 20910.6558 | 0.39092 | 5 | 26775 |  |  |  | 18207 | 0.39092 | 20 | Each | 19492 | 34482 | 45444 | Normal | 33139.3163 | 0.30554 | 5 | 43102.5 |  |  |  | 29309.7 | 0.30554 | 20 | Each | 23992 | 40982 | 53944 | Normal | 39639.3128 | 0.2948 | 5 | 51227.5 |  |  |  | 34834.7 | 0.2948 | 20 | Each | [30 empty] | 8.9824 | 18.9 | 27.4694 | Normal | 18.9 | 0.46403 | 5 | 23.625 |  |  |  | 16.065 | 0.46403 | 20 | Each | 17.1988 | 30.4253 | 40.0976 | Normal | 30.4253 | 0.39478 | 5 | 38.0316 |  |  |  | 25.8615 | 0.39478 | 20 | Each | 21.1694 | 36.1606 | 47.5976 | Normal | 36.1606 | 0.38654 | 5 | 45.2007 |  |  |  | 30.7365 | 0.38654 | 20 | Each | [30 empty] | 1
| B1041.103b |  | B1041.103b | Non-conforming MF, weak beams and strong joints, Conc Col & Bm = 36" x 36", Beam both sides | 10180 | 21420 | 31132 | Normal | 20910.6558 | 0.39092 | 5 | 26775 |  |  |  | 18207 | 0.39092 | 20 | Each | 19492 | 34482 | 45444 | Normal | 33139.3163 | 0.30554 | 5 | 43102.5 |  |  |  | 29309.7 | 0.30554 | 20 | Each | 23992 | 40982 | 53944 | Normal | 39639.3128 | 0.2948 | 5 | 51227.5 |  |  |  | 34834.7 | 0.2948 | 20 | Each | [30 empty] | 8.9824 | 18.9 | 27.4694 | Normal | 18.9 | 0.46403 | 5 | 23.625 |  |  |  | 16.065 | 0.46403 | 20 | Each | 17.1988 | 30.4253 | 40.0976 | Normal | 30.4253 | 0.39478 | 5 | 38.0316 |  |  |  | 25.8615 | 0.39478 | 20 | Each | 21.1694 | 36.1606 | 47.5976 | Normal | 36.1606 | 0.38654 | 5 | 45.2007 |  |  |  | 30.7365 | 0.38654 | 20 | Each | [30 empty] | 1
| B1041.111a |  | B1041.111a | Non-conforming MF, weak columns, Conc Col & Bm = 24" x 24", Beam one side | 10180 | 21420 | 31132 | Normal | 20910.6558 | 0.39092 | 5 | 26775 |  |  |  | 18207 | 0.39092 | 20 | Each | 18492 | 32482 | 44444 | Normal | 31805.9835 | 0.31834 | 5 | 40602.5 |  |  |  | 27609.7 | 0.31834 | 20 | Each | 22992 | 39982 | 52944 | Normal | 38639.3134 | 0.30243 | 5 | 49977.5 |  |  |  | 33984.7 | 0.30243 | 20 | Each | [30 empty] | 8.9824 | 18.9 | 27.4694 | Normal | 18.9 | 0.46403 | 5 | 23.625 |  |  |  | 16.065 | 0.46403 | 20 | Each | 16.3165 | 28.6606 | 39.2153 | Normal | 28.6606 | 0.40477 | 5 | 35.8257 |  |  |  | 24.3615 | 0.40477 | 20 | Each | 20.2871 | 35.2782 | 46.7153 | Normal | 35.2782 | 0.39239 | 5 | 44.0978 |  |  |  | 29.9865 | 0.39239 | 20 | Each | [30 empty] | 1
| B1041.111b |  | B1041.111b | Non-conforming MF, weak columns, Conc Col & Bm = 24" x 24", Beam both sides | 10180 | 21420 | 31132 | Normal | 20910.6558 | 0.39092 | 5 | 26775 |  |  |  | 18207 | 0.39092 | 20 | Each | 18492 | 32482 | 44444 | Normal | 31805.9835 | 0.31834 | 5 | 40602.5 |  |  |  | 27609.7 | 0.31834 | 20 | Each | 22992 | 39982 | 52944 | Normal | 38639.3134 | 0.30243 | 5 | 49977.5 |  |  |  | 33984.7 | 0.30243 | 20 | Each | [30 empty] | 8.9824 | 18.9 | 27.4694 | Normal | 18.9 | 0.46403 | 5 | 23.625 |  |  |  | 16.065 | 0.46403 | 20 | Each | 16.3165 | 28.6606 | 39.2153 | Normal | 28.6606 | 0.40477 | 5 | 35.8257 |  |  |  | 24.3615 | 0.40477 | 20 | Each | 20.2871 | 35.2782 | 46.7153 | Normal | 35.2782 | 0.39239 | 5 | 44.0978 |  |  |  | 29.9865 | 0.39239 | 20 | Each | [30 empty] | 1
| B1041.112a |  | B1041.112a | Non-conforming MF, weak columns, Conc Col & Bm = 24" x 36", Beam one side | 10180 | 21420 | 31132 | Normal | 20910.6558 | 0.39092 | 5 | 26775 |  |  |  | 18207 | 0.39092 | 20 | Each | 19492 | 34482 | 45444 | Normal | 33139.3163 | 0.30554 | 5 | 43102.5 |  |  |  | 29309.7 | 0.30554 | 20 | Each | 23992 | 40982 | 53944 | Normal | 39639.3128 | 0.2948 | 5 | 51227.5 |  |  |  | 34834.7 | 0.2948 | 20 | Each | [30 empty] | 8.9824 | 18.9 | 27.4694 | Normal | 18.9 | 0.46403 | 5 | 23.625 |  |  |  | 16.065 | 0.46403 | 20 | Each | 17.1988 | 30.4253 | 40.0976 | Normal | 30.4253 | 0.39478 | 5 | 38.0316 |  |  |  | 25.8615 | 0.39478 | 20 | Each | 21.1694 | 36.1606 | 47.5976 | Normal | 36.1606 | 0.38654 | 5 | 45.2007 |  |  |  | 30.7365 | 0.38654 | 20 | Each | [30 empty] | 1
| B1041.112b |  | B1041.112b | Non-conforming MF, weak columns, Conc Col & Bm = 24" x 36", Beam both sides | 10180 | 21420 | 31132 | Normal | 20910.6558 | 0.39092 | 5 | 26775 |  |  |  | 18207 | 0.39092 | 20 | Each | 19492 | 34482 | 45444 | Normal | 33139.3163 | 0.30554 | 5 | 43102.5 |  |  |  | 29309.7 | 0.30554 | 20 | Each | 23992 | 40982 | 53944 | Normal | 39639.3128 | 0.2948 | 5 | 51227.5 |  |  |  | 34834.7 | 0.2948 | 20 | Each | [30 empty] | 8.9824 | 18.9 | 27.4694 | Normal | 18.9 | 0.46403 | 5 | 23.625 |  |  |  | 16.065 | 0.46403 | 20 | Each | 17.1988 | 30.4253 | 40.0976 | Normal | 30.4253 | 0.39478 | 5 | 38.0316 |  |  |  | 25.8615 | 0.39478 | 20 | Each | 21.1694 | 36.1606 | 47.5976 | Normal | 36.1606 | 0.38654 | 5 | 45.2007 |  |  |  | 30.7365 | 0.38654 | 20 | Each | [30 empty] | 1
| B1041.113a |  | B1041.113a | Non-conforming MF, weak columns, Conc Col & Bm = 36" x 36", Beam one side | 10180 | 21420 | 31132 | Normal | 20910.6558 | 0.39092 | 5 | 26775 |  |  |  | 18207 | 0.39092 | 20 | Each | 19492 | 34482 | 45444 | Normal | 33139.3163 | 0.30554 | 5 | 43102.5 |  |  |  | 29309.7 | 0.30554 | 20 | Each | 23992 | 40982 | 53944 | Normal | 39639.3128 | 0.2948 | 5 | 51227.5 |  |  |  | 34834.7 | 0.2948 | 20 | Each | [30 empty] | 8.9824 | 18.9 | 27.4694 | Normal | 18.9 | 0.46403 | 5 | 23.625 |  |  |  | 16.065 | 0.46403 | 20 | Each | 17.1988 | 30.4253 | 40.0976 | Normal | 30.4253 | 0.39478 | 5 | 38.0316 |  |  |  | 25.8615 | 0.39478 | 20 | Each | 21.1694 | 36.1606 | 47.5976 | Normal | 36.1606 | 0.38654 | 5 | 45.2007 |  |  |  | 30.7365 | 0.38654 | 20 | Each | [30 empty] | 1
| B1041.113b |  | B1041.113b | Non-conforming MF, weak columns, Conc Col & Bm = 36" x 36", Beam both sides | 10180 | 21420 | 31132 | Normal | 20910.6558 | 0.39092 | 5 | 26775 |  |  |  | 18207 | 0.39092 | 20 | Each | 19492 | 34482 | 45444 | Normal | 33139.3163 | 0.30554 | 5 | 43102.5 |  |  |  | 29309.7 | 0.30554 | 20 | Each | 23992 | 40982 | 53944 | Normal | 39639.3128 | 0.2948 | 5 | 51227.5 |  |  |  | 34834.7 | 0.2948 | 20 | Each | [30 empty] | 8.9824 | 18.9 | 27.4694 | Normal | 18.9 | 0.46403 | 5 | 23.625 |  |  |  | 16.065 | 0.46403 | 20 | Each | 17.1988 | 30.4253 | 40.0976 | Normal | 30.4253 | 0.39478 | 5 | 38.0316 |  |  |  | 25.8615 | 0.39478 | 20 | Each | 21.1694 | 36.1606 | 47.5976 | Normal | 36.1606 | 0.38654 | 5 | 45.2007 |  |  |  | 30.7365 | 0.38654 | 20 | Each | [30 empty] | 1
| B1041.121a |  | B1041.121a | Non-conforming MF, weak columns and strong joints, Conc Col & Bm = 24" x 24", Beam both sides | 10180 | 21420 | 31132 | Normal | 20910.6558 | 0.39092 | 5 | 26775 |  |  |  | 18207 | 0.39092 | 20 | Each | 24492 | 40482 | 53444 | Normal | 39472.5578 | 0.28616 | 5 | 50602.5 |  |  |  | 34409.7 | 0.28616 | 20 | Each | [45 empty] | 8.9824 | 18.9 | 27.4694 | Normal | 18.9 | 0.46403 | 5 | 23.625 |  |  |  | 16.065 | 0.46403 | 20 | Each | 21.6106 | 35.7194 | 47.1565 | Normal | 35.7194 | 0.37999 | 5 | 44.6493 |  |  |  | 30.3615 | 0.37999 | 20 | Each | [45 empty] | 1
| B1041.121b |  | B1041.121b | Non-conforming MF, weak columns and strong joints, Conc Col & Bm = 24" x 24", Beam one side | 10180 | 21420 | 31132 | Normal | 20910.6558 | 0.39092 | 5 | 26775 |  |  |  | 18207 | 0.39092 | 20 | Each | 24492 | 40482 | 53444 | Normal | 39472.5578 | 0.28616 | 5 | 50602.5 |  |  |  | 34409.7 | 0.28616 | 20 | Each | [45 empty] | 8.9824 | 18.9 | 27.4694 | Normal | 18.9 | 0.46403 | 5 | 23.625 |  |  |  | 16.065 | 0.46403 | 20 | Each | 21.6106 | 35.7194 | 47.1565 | Normal | 35.7194 | 0.37999 | 5 | 44.6493 |  |  |  | 30.3615 | 0.37999 | 20 | Each | [45 empty] | 1
| B1041.122a |  | B1041.122a | Non-conforming MF, weak columns and strong joints, Conc Col & Bm = 24" x 36", Beam one side | 10180 | 21420 | 31132 | Normal | 20910.6558 | 0.39092 | 5 | 26775 |  |  |  | 18207 | 0.39092 | 20 | Each | 25492 | 41482 | 54444 | Normal | 40472.6656 | 0.27909 | 5 | 51852.5 |  |  |  | 35259.7 | 0.27909 | 20 | Each | [45 empty] | 8.9824 | 18.9 | 27.4694 | Normal | 18.9 | 0.46403 | 5 | 23.625 |  |  |  | 16.065 | 0.46403 | 20 | Each | 22.4929 | 36.6018 | 48.0388 | Normal | 36.6018 | 0.37469 | 5 | 45.7522 |  |  |  | 31.1115 | 0.37469 | 20 | Each | [45 empty] | 1
| B1041.122b |  | B1041.122b | Non-conforming MF, weak columns and strong joints, Conc Col & Bm = 24" x 36", Beam both sides | 10180 | 21420 | 31132 | Normal | 20910.6558 | 0.39092 | 5 | 26775 |  |  |  | 18207 | 0.39092 | 20 | Each | 25492 | 41482 | 54444 | Normal | 40472.6656 | 0.27909 | 5 | 51852.5 |  |  |  | 35259.7 | 0.27909 | 20 | Each | [45 empty] | 8.9824 | 18.9 | 27.4694 | Normal | 18.9 | 0.46403 | 5 | 23.625 |  |  |  | 16.065 | 0.46403 | 20 | Each | 22.4929 | 36.6018 | 48.0388 | Normal | 36.6018 | 0.37469 | 5 | 45.7522 |  |  |  | 31.1115 | 0.37469 | 20 | Each | [45 empty] | 1
| B1041.123a |  | B1041.123a | Non-conforming MF, weak columns and strong joints, Conc Col & Bm = 36" x 36", Beam one side | 10180 | 21420 | 31132 | Normal | 20910.6558 | 0.39092 | 5 | 26775 |  |  |  | 18207 | 0.39092 | 20 | Each | 25492 | 41482 | 54444 | Normal | 40472.6656 | 0.27909 | 5 | 51852.5 |  |  |  | 35259.7 | 0.27909 | 20 | Each | [45 empty] | 8.9824 | 18.9 | 27.4694 | Normal | 18.9 | 0.46403 | 5 | 23.625 |  |  |  | 16.065 | 0.46403 | 20 | Each | 22.4929 | 36.6018 | 48.0388 | Normal | 36.6018 | 0.37469 | 5 | 45.7522 |  |  |  | 31.1115 | 0.37469 | 20 | Each | [45 empty] | 1
| B1041.123b |  | B1041.123b | Non-conforming MF, weak columns and strong joints, Conc Col & Bm = 36" x 36", Beam both sides | 10180 | 21420 | 31132 | Normal | 20910.6558 | 0.39092 | 5 | 26775 |  |  |  | 18207 | 0.39092 | 20 | Each | 25492 | 41482 | 54444 | Normal | 40472.6656 | 0.27909 | 5 | 51852.5 |  |  |  | 35259.7 | 0.27909 | 20 | Each | [45 empty] | 8.9824 | 18.9 | 27.4694 | Normal | 18.9 | 0.46403 | 5 | 23.625 |  |  |  | 16.065 | 0.46403 | 20 | Each | 22.4929 | 36.6018 | 48.0388 | Normal | 36.6018 | 0.37469 | 5 | 45.7522 |  |  |  | 31.1115 | 0.37469 | 20 | Each | [45 empty] | 1
| B1041.131a |  | B1041.131a | Non-conforming MF with inadequate development of reinforcing, Conc Col & Bm = 24" x 24", Beam one side | 10180 | 21420 | 31132 | Normal | 20910.6558 | 0.39092 | 5 | 26775 |  |  |  | 18207 | 0.39092 | 20 | Each | 24492 | 40482 | 53444 | Normal | 39472.5578 | 0.28616 | 5 | 50602.5 |  |  |  | 34409.7 | 0.28616 | 20 | Each | [45 empty] | 8.9824 | 18.9 | 27.4694 | Normal | 18.9 | 0.46403 | 5 | 23.625 |  |  |  | 16.065 | 0.46403 | 20 | Each | 21.6106 | 35.7194 | 47.1565 | Normal | 35.7194 | 0.37999 | 5 | 44.6493 |  |  |  | 30.3615 | 0.37999 | 20 | Each | [45 empty] | 1
| B1041.131b |  | B1041.131b | Non-conforming MF with inadequate development of reinforcing, Conc Col & Bm = 24" x 24", Beam both sides | 10180 | 21420 | 31132 | Normal | 20910.6558 | 0.39092 | 5 | 26775 |  |  |  | 18207 | 0.39092 | 20 | Each | 24492 | 40482 | 53444 | Normal | 39472.5578 | 0.28616 | 5 | 50602.5 |  |  |  | 34409.7 | 0.28616 | 20 | Each | [45 empty] | 8.9824 | 18.9 | 27.4694 | Normal | 18.9 | 0.46403 | 5 | 23.625 |  |  |  | 16.065 | 0.46403 | 20 | Each | 21.6106 | 35.7194 | 47.1565 | Normal | 35.7194 | 0.37999 | 5 | 44.6493 |  |  |  | 30.3615 | 0.37999 | 20 | Each | [45 empty] | 1
| B1041.132a |  | B1041.132a | Non-conforming MF with inadequate development of reinforcing, Conc Col & Bm = 24" x 36", Beam one side | 10180 | 21420 | 31132 | Normal | 20910.6558 | 0.39092 | 5 | 26775 |  |  |  | 18207 | 0.39092 | 20 | Each | 25492 | 41482 | 54444 | Normal | 40472.6656 | 0.27909 | 5 | 51852.5 |  |  |  | 35259.7 | 0.27909 | 20 | Each | [45 empty] | 8.9824 | 18.9 | 27.4694 | Normal | 18.9 | 0.46403 | 5 | 23.625 |  |  |  | 16.065 | 0.46403 | 20 | Each | 22.4929 | 36.6018 | 48.0388 | Normal | 36.6018 | 0.37469 | 5 | 45.7522 |  |  |  | 31.1115 | 0.37469 | 20 | Each | [45 empty] | 1
| B1041.132b |  | B1041.132b | Non-conforming MF with inadequate development of reinforcing, Conc Col & Bm = 24" x 36", Beam both sides | 10180 | 21420 | 31132 | Normal | 20910.6558 | 0.39092 | 5 | 26775 |  |  |  | 18207 | 0.39092 | 20 | Each | 25492 | 41482 | 54444 | Normal | 40472.6656 | 0.27909 | 5 | 51852.5 |  |  |  | 35259.7 | 0.27909 | 20 | Each | [45 empty] | 8.9824 | 18.9 | 27.4694 | Normal | 18.9 | 0.46403 | 5 | 23.625 |  |  |  | 16.065 | 0.46403 | 20 | Each | 22.4929 | 36.6018 | 48.0388 | Normal | 36.6018 | 0.37469 | 5 | 45.7522 |  |  |  | 31.1115 | 0.37469 | 20 | Each | [45 empty] | 1
| B1041.133a |  | B1041.133a | Non-conforming MF with inadequate development of reinforcing, Conc Col & Bm = 36" x 36", Beam one side | 10180 | 21420 | 31132 | Normal | 20910.6558 | 0.39092 | 5 | 26775 |  |  |  | 18207 | 0.39092 | 20 | Each | 25492 | 41482 | 54444 | Normal | 40472.6656 | 0.27909 | 5 | 51852.5 |  |  |  | 35259.7 | 0.27909 | 20 | Each | [45 empty] | 8.9824 | 18.9 | 27.4694 | Normal | 18.9 | 0.46403 | 5 | 23.625 |  |  |  | 16.065 | 0.46403 | 20 | Each | 22.4929 | 36.6018 | 48.0388 | Normal | 36.6018 | 0.37469 | 5 | 45.7522 |  |  |  | 31.1115 | 0.37469 | 20 | Each | [45 empty] | 1
| B1041.133b |  | B1041.133b | Non-conforming MF with inadequate development of reinforcing, Conc Col & Bm = 36" x 36", Beam both sides | 10180 | 21420 | 31132 | Normal | 20910.6558 | 0.39092 | 5 | 26775 |  |  |  | 18207 | 0.39092 | 20 | Each | 25492 | 41482 | 54444 | Normal | 40472.6656 | 0.27909 | 5 | 51852.5 |  |  |  | 35259.7 | 0.27909 | 20 | Each | [45 empty] | 8.9824 | 18.9 | 27.4694 | Normal | 18.9 | 0.46403 | 5 | 23.625 |  |  |  | 16.065 | 0.46403 | 20 | Each | 22.4929 | 36.6018 | 48.0388 | Normal | 36.6018 | 0.37469 | 5 | 45.7522 |  |  |  | 31.1115 | 0.37469 | 20 | Each | [45 empty] | 1
| B1044.001 |  | B1044.001 | Rectangular low aspect ratio concrete walls 8" or less thick single curtain up to 15' high | 4608 | 5184 | 7104 | LogNormal | 5530.1893 | 0.18018 | 3 | 6480 |  |  |  | 4406.4 | 0.18018 | 7 | 144 ft^2 Units | 10503.936 | 12231.936 | 15687.936 | LogNormal | 12624.0347 | 0.16158 | 3 | 15289.92 |  |  |  | 10397.1456 | 0.16158 | 7 | 144 ft^2 Units | 20208 | 22915.2 | 28982.4 | LogNormal | 23752.8384 | 0.14586 | 3 | 28644 |  |  |  | 19477.92 | 0.14586 | 7 | 144 ft^2 Units | [30 empty] | 3.5856 | 4.0464 | 5.544 | LogNormal | 4.0464 | 0.30816 | 3 | 5.0565 |  |  |  | 3.4403 | 0.30816 | 7 | 144 ft^2 Units | 8.1936 | 9.5328 | 12.2256 | LogNormal | 9.5328 | 0.29767 | 3 | 11.9162 |  |  |  | 8.1027 | 0.29767 | 7 | 144 ft^2 Units | 15.7536 | 17.856 | 22.5936 | LogNormal | 17.856 | 0.28944 | 3 | 22.3211 |  |  |  | 15.1769 | 0.28944 | 7 | 144 ft^2 Units | [30 empty] | 144
| B1044.002 |  | B1044.002 | Rectangular low aspect ratio concrete walls 8" or less thick single curtain 16' high to 24' high | 14400 | 16400 | 19600 | LogNormal | 16662.3695 | 0.12222 | 3 | 20500 |  |  |  | 13940 | 0.12222 | 7 | 400 ft^2 Units | 33160 | 37160 | 44760 | LogNormal | 38056.5246 | 0.11987 | 3 | 46450 |  |  |  | 31586 | 0.11987 | 7 | 400 ft^2 Units | 53220 | 60340 | 76660 | LogNormal | 62641.0573 | 0.14784 | 3 | 75425 |  |  |  | 51289 | 0.14784 | 7 | 400 ft^2 Units | [30 empty] | 13.36 | 15.2 | 18.16 | LogNormal | 15.2 | 0.27828 | 3 | 18.9985 |  |  |  | 12.9209 | 0.27828 | 7 | 400 ft^2 Units | 30.72 | 34.44 | 41.48 | LogNormal | 34.44 | 0.27725 | 3 | 43.0469 |  |  |  | 29.2759 | 0.27725 | 7 | 400 ft^2 Units | 49.32 | 55.92 | 71.04 | LogNormal | 55.92 | 0.29044 | 3 | 69.8958 |  |  |  | 47.5345 | 0.29044 | 7 | 400 ft^2 Units | [30 empty] | 400
| B1044.003 |  | B1044.003 | Rectangular low aspect ratio concrete walls 8" or less thick single curtain 25' high to 40' high | 31371.4286 | 34200 | 41914.2857 | LogNormal | 35554.2348 | 0.11749 | 3 | 42750 |  |  |  | 29070 | 0.11749 | 7 | 900 ft^2 Units | 73649.8286 | 79049.8286 | 91649.8286 | LogNormal | 81105.0811 | 0.087515 | 3 | 98812.2857 |  |  |  | 67192.3543 | 0.087515 | 7 | 900 ft^2 Units | 100182.8571 | 118774.2857 | 147780 | LogNormal | 120659.3809 | 0.15411 | 3 | 148467.8571 |  |  |  | 100958.1429 | 0.15411 | 7 | 900 ft^2 Units | [30 empty] | 29.97 | 32.67 | 40.05 | LogNormal | 32.67 | 0.27623 | 3 | 40.8428 |  |  |  | 27.7663 | 0.27623 | 7 | 900 ft^2 Units | 70.38 | 75.6 | 87.57 | LogNormal | 75.6 | 0.26488 | 3 | 94.4906 |  |  |  | 64.2656 | 0.26488 | 7 | 900 ft^2 Units | 95.76 | 113.49 | 141.3 | LogNormal | 113.49 | 0.29368 | 3 | 141.8736 |  |  |  | 96.4599 | 0.29368 | 7 | 900 ft^2 Units | [30 empty] | 900
| B1044.011 |  | B1044.011 | Rectangular low aspect ratio concrete walls 8"-16" double curtain; with heights of up to 15' | 5472 | 6048 | 7968 | LogNormal | 6408.6825 | 0.15533 | 3 | 7560 |  |  |  | 5140.8 | 0.15533 | 7 | 144 ft^2 Units | 14073.6 | 15609.6 | 19311.36 | LogNormal | 16183.5121 | 0.12798 | 3 | 19512 |  |  |  | 13268.16 | 0.12798 | 7 | 144 ft^2 Units | 26688 | 29155.2 | 35462.4 | LogNormal | 30212.5678 | 0.11491 | 3 | 36444 |  |  |  | 24781.92 | 0.11491 | 7 | 144 ft^2 Units | [30 empty] | 4.2624 | 4.7088 | 6.2064 | LogNormal | 4.7088 | 0.29432 | 3 | 5.8873 |  |  |  | 4.0017 | 0.29432 | 7 | 144 ft^2 Units | 10.9728 | 12.168 | 15.048 | LogNormal | 12.168 | 0.28085 | 3 | 15.2096 |  |  |  | 10.3431 | 0.28085 | 7 | 144 ft^2 Units | 20.808 | 22.7232 | 27.6336 | LogNormal | 22.7232 | 0.27514 | 3 | 28.4042 |  |  |  | 19.3146 | 0.27514 | 7 | 144 ft^2 Units | [30 empty] | 144
| B1044.012 |  | B1044.012 | Rectangular low aspect ratio concrete walls 8"-16" double curtain; with heights of 16' to 24' | 16800 | 18800 | 22000 | LogNormal | 19079.8244 | 0.10678 | 3 | 23500 |  |  |  | 15980 | 0.10678 | 7 | 400 ft^2 Units | 38700 | 42500 | 50100 | LogNormal | 43510.0241 | 0.10312 | 3 | 53125 |  |  |  | 36125 | 0.10312 | 7 | 400 ft^2 Units | 69000 | 75720 | 90840 | LogNormal | 77990.1508 | 0.1105 | 3 | 94650 |  |  |  | 64362 | 0.1105 | 7 | 400 ft^2 Units | [30 empty] | 15.56 | 17.4 | 20.4 | LogNormal | 17.4 | 0.27185 | 3 | 21.7544 |  |  |  | 14.7874 | 0.27185 | 7 | 400 ft^2 Units | 35.84 | 39.36 | 46.4 | LogNormal | 39.36 | 0.27043 | 3 | 49.2037 |  |  |  | 33.4537 | 0.27043 | 7 | 400 ft^2 Units | 63.92 | 70.16 | 84.16 | LogNormal | 70.16 | 0.27333 | 3 | 87.6981 |  |  |  | 59.6371 | 0.27333 | 7 | 400 ft^2 Units | [30 empty] | 400
| B1044.013 |  | B1044.013 | Rectangular low aspect ratio concrete walls 8"-16" double curtain; with heights of 24' to 40' | 36771.4286 | 39600 | 47314.2857 | LogNormal | 40991.7536 | 0.10179 | 3 | 49500 |  |  |  | 33660 | 0.10179 | 7 | 900 ft^2 Units | 85654.2857 | 91054.2857 | 103654.2857 | LogNormal | 93155.1271 | 0.076126 | 3 | 113817.8571 |  |  |  | 77396.1429 | 0.076126 | 7 | 900 ft^2 Units | 129471.4286 | 147420 | 174497.1429 | LogNormal | 149316.1221 | 0.11795 | 3 | 184275 |  |  |  | 125307 | 0.11795 | 7 | 900 ft^2 Units | [30 empty] | 35.19 | 37.89 | 45.27 | LogNormal | 37.89 | 0.26993 | 3 | 47.3532 |  |  |  | 32.2121 | 0.26993 | 7 | 900 ft^2 Units | 81.9 | 87.03 | 99.09 | LogNormal | 87.03 | 0.26133 | 3 | 108.7893 |  |  |  | 73.9744 | 0.26133 | 7 | 900 ft^2 Units | 123.75 | 140.94 | 166.77 | LogNormal | 140.94 | 0.27643 | 3 | 176.169 |  |  |  | 119.8026 | 0.27643 | 7 | 900 ft^2 Units | [30 empty] | 900
| B1044.021 |  | B1044.021 | Rectangular low aspect ratio concrete walls 18"-24" thick with double curtain and heights up to 15' | 7632 | 8208 | 10128 | LogNormal | 8591.7231 | 0.11551 | 3 | 10260 |  |  |  | 6976.8 | 0.11551 | 7 | 144 ft^2 Units | 17310.72 | 18846.72 | 23416.32 | LogNormal | 19690.6833 | 0.12311 | 3 | 23558.4 |  |  |  | 16019.712 | 0.12311 | 7 | 144 ft^2 Units | 32956.8 | 36864 | 41731.2 | LogNormal | 37010.2257 | 0.092464 | 3 | 46080 |  |  |  | 31334.4 | 0.092464 | 7 | 144 ft^2 Units | [30 empty] | 5.9472 | 6.3936 | 7.8912 | LogNormal | 6.3936 | 0.2754 | 3 | 7.993 |  |  |  | 5.434 | 0.2754 | 7 | 144 ft^2 Units | 13.4928 | 14.688 | 18.2448 | LogNormal | 14.688 | 0.27867 | 3 | 18.3603 |  |  |  | 12.4846 | 0.27867 | 7 | 144 ft^2 Units | 25.6896 | 28.728 | 32.5296 | LogNormal | 28.728 | 0.26655 | 3 | 35.9111 |  |  |  | 24.4182 | 0.26655 | 7 | 144 ft^2 Units | [30 empty] | 144
| B1044.022 |  | B1044.022 | Rectangular low aspect ratio concrete walls 18"-24" thick with double curtain and heights 16' - 24' | 22800 | 24800 | 28000 | LogNormal | 25108.8231 | 0.081153 | 3 | 31000 |  |  |  | 21080 | 0.081153 | 7 | 400 ft^2 Units | 47700 | 51500 | 59100 | LogNormal | 52554.9201 | 0.085318 | 3 | 64375 |  |  |  | 43775 | 0.085318 | 7 | 400 ft^2 Units | 86580 | 97300 | 109220 | LogNormal | 97262.5429 | 0.090595 | 3 | 121625 |  |  |  | 82705 | 0.090595 | 7 | 400 ft^2 Units | [30 empty] | 21.12 | 22.96 | 25.96 | LogNormal | 22.96 | 0.26284 | 3 | 28.7041 |  |  |  | 19.5135 | 0.26284 | 7 | 400 ft^2 Units | 44.2 | 47.72 | 54.76 | LogNormal | 47.72 | 0.26416 | 3 | 59.6483 |  |  |  | 40.563 | 0.26416 | 7 | 400 ft^2 Units | 80.2 | 90.16 | 101.2 | LogNormal | 90.16 | 0.26591 | 3 | 112.6964 |  |  |  | 76.6382 | 0.26591 | 7 | 400 ft^2 Units | [30 empty] | 400
| B1044.023 |  | B1044.023 | Rectangular low aspect ratio concrete walls 18"-24" thick with double curtain and heights 25' - 40' | 50271.4286 | 53100 | 60814.2857 | LogNormal | 54552.2558 | 0.076297 | 3 | 66375 |  |  |  | 45135 | 0.076297 | 7 | 900 ft^2 Units | 105896.5714 | 111296.5714 | 123896.5714 | LogNormal | 113452.0454 | 0.062428 | 3 | 139120.7143 |  |  |  | 94602.0857 | 0.062428 | 7 | 900 ft^2 Units | 161948.5714 | 188897.1429 | 227802.8571 | LogNormal | 190973.4857 | 0.1346 | 3 | 236121.4286 |  |  |  | 160562.5714 | 0.1346 | 7 | 900 ft^2 Units | [30 empty] | 48.06 | 50.76 | 58.14 | LogNormal | 50.76 | 0.26138 | 3 | 63.4493 |  |  |  | 43.1464 | 0.26138 | 7 | 900 ft^2 Units | 101.25 | 106.38 | 118.44 | LogNormal | 106.38 | 0.25768 | 3 | 132.9766 |  |  |  | 90.422 | 0.25768 | 7 | 900 ft^2 Units | 154.8 | 180.54 | 217.71 | LogNormal | 180.54 | 0.28393 | 3 | 225.6809 |  |  |  | 153.4555 | 0.28393 | 7 | 900 ft^2 Units | [30 empty] | 900
| B1044.031 |  | B1044.031 | Low-rise reinforced concrete walls with return flanges, less than 8" thick up to 15' high | 11924.736 | 13460.736 | 16724.736 | LogNormal | 13893.0081 | 0.13623 | 3 | 16825.92 |  |  |  | 11441.6256 | 0.13623 | 7 | 144 ft^2 Units | 19920 | 22915.2 | 30710.4 | LogNormal | 24087.3041 | 0.1776 | 3 | 28644 |  |  |  | 19477.92 | 0.1776 | 7 | 144 ft^2 Units | [45 empty] | 9.288 | 10.4976 | 13.032 | LogNormal | 10.4976 | 0.28471 | 3 | 13.1205 |  |  |  | 8.9239 | 0.28471 | 7 | 144 ft^2 Units | 15.5232 | 17.856 | 23.9328 | LogNormal | 17.856 | 0.30666 | 3 | 22.3211 |  |  |  | 15.1769 | 0.30666 | 7 | 144 ft^2 Units | [45 empty] | 144
| B1044.032 |  | B1044.032 | Low-rise reinforced concrete walls with return flanges, less than 8" thick, 16' to 24' high | 32720 | 36520 | 44120 | LogNormal | 37488.0971 | 0.11972 | 3 | 45650 |  |  |  | 31042 | 0.11972 | 7 | 400 ft^2 Units | 55620 | 60340 | 83060 | LogNormal | 65275.0028 | 0.16913 | 3 | 75425 |  |  |  | 51289 | 0.16913 | 7 | 400 ft^2 Units | [45 empty] | 30.32 | 33.84 | 40.88 | LogNormal | 33.84 | 0.27719 | 3 | 42.2987 |  |  |  | 28.7648 | 0.27719 | 7 | 400 ft^2 Units | 51.52 | 55.92 | 76.96 | LogNormal | 55.92 | 0.30183 | 3 | 69.8958 |  |  |  | 47.5345 | 0.30183 | 7 | 400 ft^2 Units | [45 empty] | 400
| B1044.033 |  | B1044.033 | Low-rise reinforced concrete walls with return flanges, less than 8" thick, 25' to 40' high | 72209.8286 | 77609.8286 | 90209.8286 | LogNormal | 79658.6588 | 0.089115 | 3 | 97012.2857 |  |  |  | 65968.3543 | 0.089115 | 7 | 900 ft^2 Units | 100182.8571 | 118774.2857 | 149580 | LogNormal | 121135.1591 | 0.15955 | 3 | 148467.8571 |  |  |  | 100958.1429 | 0.15955 | 7 | 900 ft^2 Units | [45 empty] | 69.03 | 74.16 | 86.22 | LogNormal | 74.16 | 0.26541 | 3 | 92.7065 |  |  |  | 63.0321 | 0.26541 | 7 | 900 ft^2 Units | 95.76 | 113.49 | 143.01 | LogNormal | 113.49 | 0.29657 | 3 | 141.8736 |  |  |  | 96.4599 | 0.29657 | 7 | 900 ft^2 Units | [45 empty] | 900
| B1044.041 |  | B1044.041 | Low-rise reinforced concrete walls with return flanges, 8" to 16" thick up to 15' high | 13785.6 | 15321.6 | 18585.6 | LogNormal | 15771.2701 | 0.11999 | 3 | 19152 |  |  |  | 13023.36 | 0.11999 | 7 | 144 ft^2 Units | 25440 | 29155.2 | 36038.4 | LogNormal | 29888.8136 | 0.13932 | 3 | 36444 |  |  |  | 24781.92 | 0.13932 | 7 | 144 ft^2 Units | [45 empty] | 10.7424 | 11.9376 | 14.4864 | LogNormal | 11.9376 | 0.2773 | 3 | 14.9231 |  |  |  | 10.1463 | 0.2773 | 7 | 144 ft^2 Units | 19.8288 | 22.7232 | 28.0944 | LogNormal | 22.7232 | 0.2862 | 3 | 28.4042 |  |  |  | 19.3146 | 0.2862 | 7 | 144 ft^2 Units | [45 empty] | 144
| B1044.042 |  | B1044.042 | Low-rise reinforced concrete walls with return flanges, 8" to 16" thick, 16' to 24' high | 37900 | 41700 | 49300 | LogNormal | 42705.1046 | 0.10507 | 3 | 52125 |  |  |  | 35445 | 0.10507 | 7 | 400 ft^2 Units | 69000 | 77640 | 100280 | LogNormal | 81243.9493 | 0.15265 | 3 | 97050 |  |  |  | 65994 | 0.15265 | 7 | 400 ft^2 Units | [45 empty] | 35.12 | 38.64 | 45.68 | LogNormal | 38.64 | 0.27118 | 3 | 48.2985 |  |  |  | 32.8449 | 0.27118 | 7 | 400 ft^2 Units | 63.92 | 71.92 | 92.92 | LogNormal | 71.92 | 0.29292 | 3 | 89.9028 |  |  |  | 61.1303 | 0.29292 | 7 | 400 ft^2 Units | [45 empty] | 400
| B1044.043 |  | B1044.043 | Low-rise reinforced concrete walls with return flanges, 8" to 16" thick, 25' to 40' high | 83854.2857 | 89254.2857 | 101854.2857 | LogNormal | 91349.0862 | 0.077642 | 3 | 111567.8571 |  |  |  | 75866.1429 | 0.077642 | 7 | 900 ft^2 Units | 124328.5714 | 151740 | 181851.4286 | Normal | 152639.9272 | 0.14703 | 3 | 189675 |  |  |  | 128979 | 0.14703 | 7 | 900 ft^2 Units | [45 empty] | 80.19 | 85.32 | 97.38 | LogNormal | 85.32 | 0.26178 | 3 | 106.6491 |  |  |  | 72.5225 | 0.26178 | 7 | 900 ft^2 Units | 118.8 | 145.08 | 173.79 | Normal | 145.08 | 0.29003 | 3 | 181.3414 |  |  |  | 123.3232 | 0.29003 | 7 | 900 ft^2 Units | [45 empty] | 900
| B1044.051 |  | B1044.051 | Low-rise reinforced concrete walls with return flanges, 17" to 24" thick" up to 15' high | 16878.72 | 18414.72 | 21678.72 | LogNormal | 18885.5993 | 0.10014 | 3 | 19152 |  |  |  | 13023.36 | 0.10014 | 7 | 144 ft^2 Units | 31708.8 | 36864 | 43267.2 | LogNormal | 36979.3444 | 0.12164 | 3 | 37668 |  |  |  | 25614.24 | 0.12164 | 7 | 144 ft^2 Units | [45 empty] | 10.7424 | 11.9376 | 14.4864 | LogNormal | 11.9376 | 0.26931 | 3 | 14.9231 |  |  |  | 10.1463 | 0.26931 | 7 | 144 ft^2 Units | 20.0592 | 23.4864 | 29.3904 | LogNormal | 23.4864 | 0.27802 | 3 | 29.3582 |  |  |  | 19.9633 | 0.27802 | 7 | 144 ft^2 Units | [45 empty] | 144
| B1044.052 |  | B1044.052 | Low-rise reinforced concrete walls with return flanges, 17" to 24" thick, 16' to 24' high | 46500 | 50300 | 57900 | LogNormal | 51349.8412 | 0.087328 | 3 | 62875 |  |  |  | 42755 | 0.087328 | 7 | 400 ft^2 Units | 86580 | 99220 | 117860 | LogNormal | 100398.4421 | 0.12178 | 3 | 124025 |  |  |  | 84337 | 0.12178 | 7 | 400 ft^2 Units | [45 empty] | 43.08 | 46.6 | 53.64 | LogNormal | 46.6 | 0.26481 | 3 | 58.2504 |  |  |  | 39.6098 | 0.26481 | 7 | 400 ft^2 Units | 80.2 | 91.92 | 109.2 | LogNormal | 91.92 | 0.27808 | 3 | 114.9011 |  |  |  | 78.1313 | 0.27808 | 7 | 400 ft^2 Units | [45 empty] | 400
| B1044.053 |  | B1044.053 | Low-rise reinforced concrete walls with return flanges, 17" to 24" thick, 25' to 40' high | 103196.5714 | 108596.5714 | 121196.5714 | LogNormal | 110745.9319 | 0.063963 | 3 | 135745.7143 |  |  |  | 92307.0857 | 0.063963 | 7 | 900 ft^2 Units | 156805.7143 | 193217.1429 | 226157.1429 | Normal | 192059.902 | 0.14088 | 3 | 241521.4286 |  |  |  | 164234.5714 | 0.14088 | 7 | 900 ft^2 Units | [45 empty] | 98.64 | 103.77 | 115.83 | LogNormal | 103.77 | 0.25805 | 3 | 129.7214 |  |  |  | 88.1992 | 0.25805 | 7 | 900 ft^2 Units | 149.85 | 184.68 | 216.18 | Normal | 184.68 | 0.28696 | 3 | 230.8532 |  |  |  | 156.9761 | 0.28696 | 7 | 900 ft^2 Units | [45 empty] | 900
| B1044.061 |  | B1044.061 | Low rise reinforced concrete walls with boundary columns, less than 8" thick, height <15' | 11924.736 | 13460.736 | 16724.736 | LogNormal | 13893.0081 | 0.13623 | 3 | 16825.92 |  |  |  | 11441.6256 | 0.13623 | 7 | 144 ft^2 Units | 19920 | 22915.2 | 30710.4 | LogNormal | 24087.3041 | 0.1776 | 3 | 28644 |  |  |  | 19477.92 | 0.1776 | 7 | 144 ft^2 Units | [45 empty] | 9.288 | 10.4976 | 13.032 | LogNormal | 10.4976 | 0.28471 | 3 | 13.1205 |  |  |  | 8.9239 | 0.28471 | 7 | 144 ft^2 Units | 15.5232 | 17.856 | 23.9328 | LogNormal | 17.856 | 0.30666 | 3 | 22.3211 |  |  |  | 15.1769 | 0.30666 | 7 | 144 ft^2 Units | [45 empty] | 144
| B1044.062 |  | B1044.062 | Low rise reinforced concrete walls with boundary columns, less than 8" thick, height between 16'-24' | 32720 | 36520 | 44120 | LogNormal | 37488.0971 | 0.11972 | 3 | 45650 |  |  |  | 31042 | 0.11972 | 7 | 400 ft^2 Units | 55620 | 60340 | 83060 | LogNormal | 65275.0028 | 0.16913 | 3 | 75425 |  |  |  | 51289 | 0.16913 | 7 | 400 ft^2 Units | [45 empty] | 30.32 | 33.84 | 40.88 | LogNormal | 33.84 | 0.27719 | 3 | 42.2987 |  |  |  | 28.7648 | 0.27719 | 7 | 400 ft^2 Units | 51.52 | 55.92 | 76.96 | LogNormal | 55.92 | 0.30183 | 3 | 69.8958 |  |  |  | 47.5345 | 0.30183 | 7 | 400 ft^2 Units | [45 empty] | 400
| B1044.063 |  | B1044.063 | Low rise reinforced concrete walls with boundary columns, less than 8" thick, height between 24'-40' | 72209.8286 | 77609.8286 | 90209.8286 | LogNormal | 79658.6588 | 0.089115 | 3 | 97012.2857 |  |  |  | 65968.3543 | 0.089115 | 7 | 900 ft^2 Units | 100182.8571 | 118774.2857 | 149580 | LogNormal | 121135.1591 | 0.15955 | 3 | 148467.8571 |  |  |  | 100958.1429 | 0.15955 | 7 | 900 ft^2 Units | [45 empty] | 69.03 | 74.16 | 86.22 | LogNormal | 74.16 | 0.26541 | 3 | 92.7065 |  |  |  | 63.0321 | 0.26541 | 7 | 900 ft^2 Units | 95.76 | 113.49 | 143.01 | LogNormal | 113.49 | 0.29657 | 3 | 141.8736 |  |  |  | 96.4599 | 0.29657 | 7 | 900 ft^2 Units | [45 empty] | 900
| B1044.071 |  | B1044.071 | Low rise reinforced concrete walls with boundary columns, 8" to 16" thick, height <15' | 13785.6 | 15321.6 | 18585.6 | LogNormal | 15771.2701 | 0.11999 | 3 | 19152 |  |  |  | 13023.36 | 0.11999 | 7 | 144 ft^2 Units | 25728 | 30134.4 | 37708.8 | LogNormal | 30793.0473 | 0.15247 | 3 | 37668 |  |  |  | 25614.24 | 0.15247 | 7 | 144 ft^2 Units | [45 empty] | 10.7424 | 11.9376 | 14.4864 | LogNormal | 11.9376 | 0.2773 | 3 | 14.9231 |  |  |  | 10.1463 | 0.2773 | 7 | 144 ft^2 Units | 20.0592 | 23.4864 | 29.3904 | LogNormal | 23.4864 | 0.29282 | 3 | 29.3582 |  |  |  | 19.9633 | 0.29282 | 7 | 144 ft^2 Units | [45 empty] | 144
| B1044.072 |  | B1044.072 | Low rise reinforced concrete walls with boundary columns, 8" to 16" thick, height between 16'-24' | 37900 | 41700 | 49300 | LogNormal | 42705.1046 | 0.10507 | 3 | 52125 |  |  |  | 35445 | 0.10507 | 7 | 400 ft^2 Units | 69000 | 77640 | 100280 | LogNormal | 81243.9493 | 0.15265 | 3 | 97050 |  |  |  | 65994 | 0.15265 | 7 | 400 ft^2 Units | [45 empty] | 35.12 | 38.64 | 45.68 | LogNormal | 38.64 | 0.27118 | 3 | 48.2985 |  |  |  | 32.8449 | 0.27118 | 7 | 400 ft^2 Units | 63.92 | 71.92 | 92.92 | LogNormal | 71.92 | 0.29292 | 3 | 89.9028 |  |  |  | 61.1303 | 0.29292 | 7 | 400 ft^2 Units | [45 empty] | 400
| B1044.073 |  | B1044.073 | Low rise reinforced concrete walls with boundary columns, 8" to 16" thick, height between 24'-40' | 83854.2857 | 89254.2857 | 101854.2857 | LogNormal | 91349.0862 | 0.077642 | 3 | 111567.8571 |  |  |  | 75866.1429 | 0.077642 | 7 | 900 ft^2 Units | 124328.5714 | 151740 | 181851.4286 | Normal | 152639.9272 | 0.14703 | 3 | 189675 |  |  |  | 128979 | 0.14703 | 7 | 900 ft^2 Units | [45 empty] | 80.19 | 85.32 | 97.38 | LogNormal | 85.32 | 0.26178 | 3 | 106.6491 |  |  |  | 72.5225 | 0.26178 | 7 | 900 ft^2 Units | 118.8 | 145.08 | 173.79 | Normal | 145.08 | 0.29003 | 3 | 181.3414 |  |  |  | 123.3232 | 0.29003 | 7 | 900 ft^2 Units | [45 empty] | 900
| B1044.081 |  | B1044.081 | Low rise reinforced concrete walls with boundary columns, 17"-24" thick, height <15' | 16878.72 | 18414.72 | 21678.72 | LogNormal | 18885.5993 | 0.10014 | 3 | 23018.4 |  |  |  | 15652.512 | 0.10014 | 7 | 144 ft^2 Units | 29692.8 | 35539.2 | 42633.6 | LogNormal | 35565.5822 | 0.14124 | 3 | 44424 |  |  |  | 30208.32 | 0.14124 | 7 | 144 ft^2 Units | [45 empty] | 13.1616 | 14.3568 | 16.8912 | LogNormal | 14.3568 | 0.26931 | 3 | 17.945 |  |  |  | 12.2039 | 0.26931 | 7 | 144 ft^2 Units | 23.1408 | 27.7056 | 33.2352 | LogNormal | 27.7056 | 0.28714 | 3 | 34.6305 |  |  |  | 23.5506 | 0.28714 | 7 | 144 ft^2 Units | [45 empty] | 144
| B1044.082 |  | B1044.082 | Low rise reinforced concrete walls with boundary columns, 17"-24" thick, height between 16'-24' | 46500 | 50300 | 57900 | LogNormal | 51349.8412 | 0.087328 | 3 | 62875 |  |  |  | 42755 | 0.087328 | 7 | 400 ft^2 Units | 86580 | 99220 | 117860 | LogNormal | 100398.4421 | 0.12178 | 3 | 124025 |  |  |  | 84337 | 0.12178 | 7 | 400 ft^2 Units | [45 empty] | 43.08 | 46.6 | 53.64 | LogNormal | 46.6 | 0.26481 | 3 | 58.2504 |  |  |  | 39.6098 | 0.26481 | 7 | 400 ft^2 Units | 80.2 | 91.92 | 109.2 | LogNormal | 91.92 | 0.27808 | 3 | 114.9011 |  |  |  | 78.1313 | 0.27808 | 7 | 400 ft^2 Units | [45 empty] | 400
| B1044.083 |  | B1044.083 | Low rise reinforced concrete walls with boundary columns, 17"-24" thick, height between 24'-40' | 103196.5714 | 108596.5714 | 121196.5714 | LogNormal | 110745.9319 | 0.063963 | 3 | 135745.7143 |  |  |  | 92307.0857 | 0.063963 | 7 | 900 ft^2 Units | 156805.7143 | 193217.1429 | 225128.5714 | Normal | 191717.0445 | 0.13904 | 3 | 241521.4286 |  |  |  | 164234.5714 | 0.13904 | 7 | 900 ft^2 Units | [45 empty] | 98.64 | 103.77 | 115.83 | LogNormal | 103.77 | 0.25805 | 3 | 129.7214 |  |  |  | 88.1992 | 0.25805 | 7 | 900 ft^2 Units | 149.85 | 184.68 | 215.19 | Normal | 184.68 | 0.28606 | 3 | 230.8532 |  |  |  | 156.9761 | 0.28606 | 7 | 900 ft^2 Units | [45 empty] | 900
| B1044.091 |  | B1044.091 | Slender Concrete Wall, 12" thick, 12' high, 15' long | 4404.8 | 5656 | 9847.2 | LogNormal | 6203.029 | 0.34659 | 3 | 7070 |  |  |  | 4807.6 | 0.34659 | 7 | 144 ft^2 Units | 16441.28 | 21361.6 | 30101.92 | LogNormal | 21915.3523 | 0.24239 | 3 | 26702 |  |  |  | 18157.36 | 0.24239 | 7 | 144 ft^2 Units | 36596 | 40608 | 53832 | LogNormal | 43058.693 | 0.15963 | 3 | 50760 |  |  |  | 34516.8 | 0.15963 | 7 | 144 ft^2 Units | [30 empty] | 3.4272 | 4.4064 | 7.6752 | LogNormal | 4.4064 | 0.42735 | 3 | 5.5085 |  |  |  | 3.7451 | 0.42735 | 7 | 144 ft^2 Units | 12.816 | 16.6464 | 23.4576 | LogNormal | 16.6464 | 0.34821 | 3 | 20.8088 |  |  |  | 14.149 | 0.34821 | 7 | 144 ft^2 Units | 28.5264 | 31.6512 | 41.9616 | LogNormal | 31.6512 | 0.29662 | 3 | 39.5638 |  |  |  | 26.9036 | 0.29662 | 7 | 144 ft^2 Units | [30 empty] | 144
| B1044.092 |  | B1044.092 | Slender Concrete Wall, 12" thick, 12' high, 20' long | 4144.8 | 5256 | 8647.2 | LogNormal | 5695.7325 | 0.31238 | 3 | 6570 |  |  |  | 4467.6 | 0.31238 | 7 | 144 ft^2 Units | 13241.28 | 17121.6 | 23941.92 | LogNormal | 17550.4011 | 0.23715 | 3 | 21402 |  |  |  | 14553.36 | 0.23715 | 7 | 144 ft^2 Units | 35763 | 39222 | 50940 | LogNormal | 41477.0541 | 0.1459 | 3 | 49027.5 |  |  |  | 33338.7 | 0.1459 | 7 | 144 ft^2 Units | [30 empty] | 3.2256 | 4.0896 | 6.7392 | LogNormal | 4.0896 | 0.4001 | 3 | 5.1137 |  |  |  | 3.4751 | 0.4001 | 7 | 144 ft^2 Units | 10.3248 | 13.3488 | 18.6624 | LogNormal | 13.3488 | 0.34459 | 3 | 16.685 |  |  |  | 11.3471 | 0.34459 | 7 | 144 ft^2 Units | 27.8784 | 30.5712 | 39.7008 | LogNormal | 30.5712 | 0.28946 | 3 | 38.2137 |  |  |  | 25.9857 | 0.28946 | 7 | 144 ft^2 Units | [30 empty] | 144
| B1044.093 |  | B1044.093 | Slender Concrete Wall, 12" thick, 12' high, 30' long | 3884.8 | 4856 | 7447.2 | LogNormal | 5178.3253 | 0.27151 | 3 | 6070 |  |  |  | 4127.6 | 0.27151 | 7 | 144 ft^2 Units | 9081.28 | 11681.6 | 16341.92 | LogNormal | 11995.8912 | 0.23568 | 3 | 14602 |  |  |  | 9929.36 | 0.23568 | 7 | 144 ft^2 Units | 34930 | 37836 | 48048 | LogNormal | 39885.5845 | 0.13108 | 3 | 47295 |  |  |  | 32160.6 | 0.13108 | 7 | 144 ft^2 Units | [30 empty] | 3.024 | 3.7872 | 5.8032 | LogNormal | 3.7872 | 0.36908 | 3 | 4.7334 |  |  |  | 3.2195 | 0.36908 | 7 | 144 ft^2 Units | 7.0848 | 9.1008 | 12.744 | LogNormal | 9.1008 | 0.34358 | 3 | 11.377 |  |  |  | 7.7351 | 0.34358 | 7 | 144 ft^2 Units | 27.2304 | 29.4912 | 37.4544 | LogNormal | 29.4912 | 0.28228 | 3 | 36.8637 |  |  |  | 25.0677 | 0.28228 | 7 | 144 ft^2 Units | [30 empty] | 144
| B1044.101 |  | B1044.101 | Slender Concrete Wall, 18" thick, 12' high, 15' long | 6824 | 8680 | 13476 | LogNormal | 9236.9083 | 0.28343 | 3 | 10850 |  |  |  | 7378 | 0.28343 | 7 | 144 ft^2 Units | 20958.4 | 29984 | 36877.6 | Normal | 29273.0496 | 0.21217 | 3 | 37480 |  |  |  | 25486.4 | 0.21217 | 7 | 144 ft^2 Units | 40160 | 44568 | 58584 | LogNormal | 47125.6783 | 0.15575 | 3 | 55710 |  |  |  | 37882.8 | 0.15575 | 7 | 144 ft^2 Units | [30 empty] | 5.3136 | 6.768 | 10.4976 | LogNormal | 6.768 | 0.37793 | 3 | 8.4593 |  |  |  | 5.7532 | 0.37793 | 7 | 144 ft^2 Units | 16.3296 | 23.3712 | 28.7424 | Normal | 23.3712 | 0.3279 | 3 | 29.2137 |  |  |  | 19.8657 | 0.3279 | 7 | 144 ft^2 Units | 31.3056 | 34.7328 | 45.6624 | LogNormal | 34.7328 | 0.29455 | 3 | 43.417 |  |  |  | 29.5223 | 0.29455 | 7 | 144 ft^2 Units | [30 empty] | 144
| B1044.102 |  | B1044.102 | Slender Concrete Wall, 18" thick, 12' high, 20' long | 6564 | 8280 | 12276 | LogNormal | 8712.6877 | 0.25759 | 3 | 10350 |  |  |  | 7038 | 0.25759 | 7 | 144 ft^2 Units | 17294.4 | 24420 | 30021.6 | Normal | 23911.9987 | 0.20766 | 3 | 30525 |  |  |  | 20757 | 0.20766 | 7 | 144 ft^2 Units | 39327 | 43182 | 55692 | LogNormal | 45541.5645 | 0.14312 | 3 | 53977.5 |  |  |  | 36704.7 | 0.14312 | 7 | 144 ft^2 Units | [30 empty] | 5.112 | 6.4512 | 9.5616 | LogNormal | 6.4512 | 0.35896 | 3 | 8.0646 |  |  |  | 5.4832 | 0.35896 | 7 | 144 ft^2 Units | 13.4784 | 19.0368 | 23.4 | Normal | 19.0368 | 0.325 | 3 | 23.7951 |  |  |  | 16.1818 | 0.325 | 7 | 144 ft^2 Units | 30.6576 | 33.6528 | 43.4016 | LogNormal | 33.6528 | 0.28807 | 3 | 42.0669 |  |  |  | 28.6043 | 0.28807 | 7 | 144 ft^2 Units | [30 empty] | 144
| B1044.103 |  | B1044.103 | Slender Concrete Wall, 18" thick, 12' high, 30' long | 6304 | 7880 | 11076 | LogNormal | 8180.0352 | 0.22857 | 3 | 9850 |  |  |  | 6698 | 0.22857 | 7 | 144 ft^2 Units | 13630.4 | 18856 | 23165.6 | Normal | 18550.6572 | 0.20054 | 3 | 23570 |  |  |  | 16027.6 | 0.20054 | 7 | 144 ft^2 Units | 38548 | 41856 | 52872 | LogNormal | 44009.9488 | 0.12957 | 3 | 0 |  |  |  | 0 | 0.12957 | 7 | 144 ft^2 Units | [30 empty] | 4.9104 | 6.1488 | 8.6256 | LogNormal | 6.1488 | 0.33874 | 3 | 7.6842 |  |  |  | 5.2275 | 0.33874 | 7 | 144 ft^2 Units | 10.6272 | 14.7024 | 18.0576 | Normal | 14.7024 | 0.32049 | 3 | 18.3765 |  |  |  | 12.4979 | 0.32049 | 7 | 144 ft^2 Units | 30.0384 | 32.616 | 41.2128 | LogNormal | 32.616 | 0.28158 | 3 | 32.616 |  |  |  | 32.616 | 0.28158 | 7 | 144 ft^2 Units | [30 empty] | 144
| B1044.111 |  | B1044.111 | Slender Concrete Wall, 30" thick, 12' high, 15' long | 10280 | 13000 | 18660 | LogNormal | 13532.0845 | 0.24253 | 3 | 16250 |  |  |  | 11050 | 0.24253 | 7 | 144 ft^2 Units | 28344 | 43200 | 47956 | Normal | 39833.3146 | 0.19209 | 3 | 54000 |  |  |  | 36720 | 0.19209 | 7 | 144 ft^2 Units | 47396 | 52608 | 68232 | LogNormal | 55380.6294 | 0.14964 | 3 | 65760 |  |  |  | 44716.8 | 0.14964 | 7 | 144 ft^2 Units | [30 empty] | 8.0064 | 10.1376 | 14.544 | LogNormal | 10.1376 | 0.34831 | 3 | 12.6707 |  |  |  | 8.6177 | 0.34831 | 7 | 144 ft^2 Units | 22.0896 | 33.6672 | 37.3824 | Normal | 33.6672 | 0.31528 | 3 | 42.0848 |  |  |  | 28.6166 | 0.31528 | 7 | 144 ft^2 Units | 36.936 | 40.9968 | 53.1792 | LogNormal | 40.9968 | 0.29136 | 3 | 51.2476 |  |  |  | 34.8463 | 0.29136 | 7 | 144 ft^2 Units | [30 empty] | 144
| B1044.112 |  | B1044.112 | Slender Concrete Wall, 30" thick, 12' high, 20' long | 10020 | 12600 | 17460 | LogNormal | 12995.953 | 0.22373 | 3 | 15750 |  |  |  | 10710 | 0.22373 | 7 | 144 ft^2 Units | 23784 | 35520 | 39756 | Normal | 33019.9819 | 0.18872 | 3 | 44400 |  |  |  | 30192 | 0.18872 | 7 | 144 ft^2 Units | 46536 | 51192 | 65304 | LogNormal | 53761.8612 | 0.1388 | 3 | 63990 |  |  |  | 43513.2 | 0.1388 | 7 | 144 ft^2 Units | [30 empty] | 7.8048 | 9.8208 | 13.608 | LogNormal | 9.8208 | 0.33549 | 3 | 12.2759 |  |  |  | 8.3477 | 0.33549 | 7 | 144 ft^2 Units | 18.5328 | 27.6912 | 30.9888 | Normal | 27.6912 | 0.31323 | 3 | 34.6124 |  |  |  | 23.5385 | 0.31323 | 7 | 144 ft^2 Units | 36.2736 | 39.9024 | 50.904 | LogNormal | 39.9024 | 0.28595 | 3 | 49.8773 |  |  |  | 33.9175 | 0.28595 | 7 | 144 ft^2 Units | [30 empty] | 144
| B1044.113 |  | B1044.113 | Slender Concrete Wall, 30" thick, 12' high, 30' long | 9760 | 12200 | 16260 | LogNormal | 12453.3986 | 0.20342 | 3 | 15250 |  |  |  | 10370 | 0.20342 | 7 | 144 ft^2 Units | 19224 | 27840 | 31556 | Normal | 26206.6482 | 0.18359 | 3 | 34800 |  |  |  | 23664 | 0.18359 | 7 | 144 ft^2 Units | 45730 | 49836 | 62448 | LogNormal | 52196.8278 | 0.12729 | 3 | 62295 |  |  |  | 42360.6 | 0.12729 | 7 | 144 ft^2 Units | [30 empty] | 7.6032 | 9.504 | 12.672 | LogNormal | 9.504 | 0.3223 | 3 | 11.8812 |  |  |  | 8.0777 | 0.3223 | 7 | 144 ft^2 Units | 14.9904 | 21.7008 | 24.5952 | Normal | 21.7008 | 0.31017 | 3 | 27.1255 |  |  |  | 18.446 | 0.31017 | 7 | 144 ft^2 Units | 35.64 | 38.8368 | 48.672 | LogNormal | 38.8368 | 0.28054 | 3 | 48.5475 |  |  |  | 33.0104 | 0.28054 | 7 | 144 ft^2 Units | [30 empty] | 144
| B1049.001a |  | B1049.001a | Reinforced concrete flat slabs- columns without shear reinforcing 0<Vg/Vo<.2, no continuity reinf | 19300 | 36230 | 50900 | Normal | 35476.6482 | 0.34752 | 3 | 45287.5 |  |  |  | 30795.5 | 0.34752 | 7 | Each | 34300 | 49540 | 76700 | LogNormal | 50584.2443 | 0.32128 | 3 | 61925 |  |  |  | 42109 | 0.32128 | 7 | Each | [45 empty] | 16.4618 | 30.9021 | 43.4147 | Normal | 30.9021 | 0.4281 | 3 | 38.6276 |  |  |  | 26.2668 | 0.4281 | 7 | Each | 29.2559 | 42.2547 | 65.4206 | LogNormal | 42.2547 | 0.40709 | 3 | 52.8184 |  |  |  | 35.9165 | 0.40709 | 7 | Each | [45 empty] | 1
| B1049.001b |  | B1049.001b | Reinforced concrete flat slabs- columns without shear reinforcing 0<Vg/Vo<.2, with continuity reinf | 19300 | 36230 | 50900 | Normal | 35476.6482 | 0.34752 | 3 | 45287.5 |  |  |  | 30795.5 | 0.34752 | 7 | Each | 23300 | 40230 | 56900 | Normal | 40143.3111 | 0.32656 | 3 | 50287.5 |  |  |  | 34195.5 | 0.32656 | 7 | Each | [45 empty] | 16.4618 | 30.9021 | 43.4147 | Normal | 30.9021 | 0.4281 | 3 | 38.6276 |  |  |  | 26.2668 | 0.4281 | 7 | Each | 19.8735 | 34.3138 | 48.5324 | Normal | 34.3138 | 0.41127 | 3 | 42.8923 |  |  |  | 29.1667 | 0.41127 | 7 | Each | [45 empty] | 1
| B1049.002a |  | B1049.002a | Reinforced concrete flat slabs- columns without shear reinforcing .2<Vg/Vo<.4, no continuity reinf | 19300 | 36230 | 50900 | Normal | 35476.6482 | 0.34752 | 3 | 45287.5 |  |  |  | 30795.5 | 0.34752 | 7 | Each | 34300 | 49540 | 76700 | LogNormal | 50584.2443 | 0.32128 | 3 | 61925 |  |  |  | 42109 | 0.32128 | 7 | Each | [45 empty] | 16.4618 | 30.9021 | 43.4147 | Normal | 30.9021 | 0.4281 | 3 | 38.6276 |  |  |  | 26.2668 | 0.4281 | 7 | Each | 29.2559 | 42.2547 | 65.4206 | LogNormal | 42.2547 | 0.40709 | 3 | 52.8184 |  |  |  | 35.9165 | 0.40709 | 7 | Each | [45 empty] | 1
| B1049.002b |  | B1049.002b | Reinforced concrete flat slabs- columns without shear reinforcing .2<Vg/Vo<.4, with continuity reinf | 19300 | 36230 | 50900 | Normal | 35476.6482 | 0.34752 | 3 | 45287.5 |  |  |  | 30795.5 | 0.34752 | 7 | Each | 23300 | 40230 | 56900 | Normal | 40143.3111 | 0.32656 | 3 | 50287.5 |  |  |  | 34195.5 | 0.32656 | 7 | Each | [45 empty] | 16.4618 | 30.9021 | 43.4147 | Normal | 30.9021 | 0.4281 | 3 | 38.6276 |  |  |  | 26.2668 | 0.4281 | 7 | Each | 19.8735 | 34.3138 | 48.5324 | Normal | 34.3138 | 0.41127 | 3 | 42.8923 |  |  |  | 29.1667 | 0.41127 | 7 | Each | [45 empty] | 1
| B1049.003a |  | B1049.003a | Reinforced concrete flat slabs- columns without shear reinforcing .4<Vg/Vo<.6, no continuity reinf | 19900 | 36830 | 51500 | Normal | 36076.648 | 0.34174 | 3 | 46037.5 |  |  |  | 31305.5 | 0.34174 | 7 | Each | 34300 | 49540 | 76700 | LogNormal | 50584.2443 | 0.32128 | 3 | 61925 |  |  |  | 42109 | 0.32128 | 7 | Each | [45 empty] | 16.9735 | 31.4138 | 43.9265 | Normal | 31.4138 | 0.42342 | 3 | 39.2673 |  |  |  | 26.7017 | 0.42342 | 7 | Each | 29.2559 | 42.2547 | 65.4206 | LogNormal | 42.2547 | 0.40709 | 3 | 52.8184 |  |  |  | 35.9165 | 0.40709 | 7 | Each | [45 empty] | 1
| B1049.003b |  | B1049.003b | Reinforced concrete flat slabs- columns without shear reinforcing .4<Vg/Vo<.6, with continuity reinf | 19900 | 36830 | 51500 | Normal | 36076.648 | 0.34174 | 3 | 46037.5 |  |  |  | 31305.5 | 0.34174 | 7 | Each | 23900 | 40830 | 57500 | Normal | 40743.3127 | 0.32175 | 3 | 51037.5 |  |  |  | 34705.5 | 0.32175 | 7 | Each | [45 empty] | 16.9735 | 31.4138 | 43.9265 | Normal | 31.4138 | 0.42342 | 3 | 39.2673 |  |  |  | 26.7017 | 0.42342 | 7 | Each | 20.3853 | 34.8256 | 49.0441 | Normal | 34.8256 | 0.40746 | 3 | 43.532 |  |  |  | 29.6018 | 0.40746 | 7 | Each | [45 empty] | 1
| B1049.011 |  | B1049.011 | Reinforced concrete flat slabs- columns with shear reinforcing 0.2<Vg/Vo<0.4 | 20500 | 37430 | 52100 | Normal | 36676.6475 | 0.33615 | 3 | 46787.5 |  |  |  | 31815.5 | 0.33615 | 7 | Each | 24500 | 41430 | 58100 | Normal | 41343.3135 | 0.31708 | 3 | 51787.5 |  |  |  | 35215.5 | 0.31708 | 7 | Each | [45 empty] | 17.4853 | 31.9256 | 44.4382 | Normal | 31.9256 | 0.41892 | 3 | 39.907 |  |  |  | 27.1368 | 0.41892 | 7 | Each | 20.8971 | 35.3374 | 49.5559 | Normal | 35.3374 | 0.40378 | 3 | 44.1717 |  |  |  | 30.0368 | 0.40378 | 7 | Each | [45 empty] | 1
| B1049.012 |  | B1049.012 | Reinforced concrete flat slabs- columns with shear reinforcing 0.4<Vg/Vo<.6 | 21100 | 38030 | 52700 | Normal | 37276.6476 | 0.33074 | 3 | 47537.5 |  |  |  | 32325.5 | 0.33074 | 7 | Each | 25100 | 42030 | 58700 | Normal | 41943.3078 | 0.31254 | 3 | 52537.5 |  |  |  | 35725.5 | 0.31254 | 7 | Each | [45 empty] | 17.9971 | 32.4374 | 44.95 | Normal | 32.4374 | 0.41459 | 3 | 40.5467 |  |  |  | 27.5718 | 0.41459 | 7 | Each | 21.4088 | 35.8491 | 50.0676 | Normal | 35.8491 | 0.40023 | 3 | 44.8114 |  |  |  | 30.4717 | 0.40023 | 7 | Each | [45 empty] | 1
| B1049.021a |  | B1049.021a | Post-tensioned concrete flat slabs- columns without shear reinforcing 0.2<Vg/Vo<.0.4, no continuity reinf | 18700 | 35630 | 50300 | Normal | 34876.6483 | 0.3535 | 3 | 44537.5 |  |  |  | 30285.5 | 0.3535 | 7 | Each | 34300 | 49540 | 76700 | LogNormal | 50584.2443 | 0.32128 | 3 | 61925 |  |  |  | 42109 | 0.32128 | 7 | Each | [45 empty] | 15.95 | 30.3903 | 42.9029 | Normal | 30.3903 | 0.43297 | 3 | 37.9879 |  |  |  | 25.8318 | 0.43297 | 7 | Each | 29.2559 | 42.2547 | 65.4206 | LogNormal | 42.2547 | 0.40709 | 3 | 52.8184 |  |  |  | 35.9165 | 0.40709 | 7 | Each | [45 empty] | 1
| B1049.021b |  | B1049.021b | Post-tensioned concrete flat slabs- columns without shear reinforcing 0.2<Vg/Vo<.0.4, with continuity reinf | 18700 | 35630 | 50300 | Normal | 34876.6483 | 0.3535 | 3 | 44537.5 |  |  |  | 30285.5 | 0.3535 | 7 | Each | 22700 | 39630 | 56300 | Normal | 39543.3132 | 0.33151 | 3 | 49537.5 |  |  |  | 33685.5 | 0.33151 | 7 | Each | [45 empty] | 15.95 | 30.3903 | 42.9029 | Normal | 30.3903 | 0.43297 | 3 | 37.9879 |  |  |  | 25.8318 | 0.43297 | 7 | Each | 19.3618 | 33.8021 | 48.0206 | Normal | 33.8021 | 0.41521 | 3 | 42.2526 |  |  |  | 28.7318 | 0.41521 | 7 | Each | [45 empty] | 1
| B1049.022a |  | B1049.022a | Post-tensioned concrete flat slabs- columns without shear reinforcing 0.4<Vg/Vo<.0.6, no continuity reinf | 19300 | 36230 | 50900 | Normal | 35476.6482 | 0.34752 | 3 | 45287.5 |  |  |  | 30795.5 | 0.34752 | 7 | Each | 34300 | 49540 | 76700 | LogNormal | 50584.2443 | 0.32128 | 3 | 61925 |  |  |  | 42109 | 0.32128 | 7 | Each | [45 empty] | 16.4618 | 30.9021 | 43.4147 | Normal | 30.9021 | 0.4281 | 3 | 38.6276 |  |  |  | 26.2668 | 0.4281 | 7 | Each | 29.2559 | 42.2547 | 65.4206 | LogNormal | 42.2547 | 0.40709 | 3 | 52.8184 |  |  |  | 35.9165 | 0.40709 | 7 | Each | [45 empty] | 1
| B1049.022b |  | B1049.022b | Post-tensioned concrete flat slabs- columns without shear reinforcing 0.4<Vg/Vo<.0.6, with continuity reinf | 19300 | 36230 | 50900 | Normal | 35476.6482 | 0.34752 | 3 | 43476 |  |  |  | 28984 | 0.34752 | 7 | Each | 23300 | 40230 | 56900 | Normal | 40143.3111 | 0.32656 | 3 | 48276 |  |  |  | 32184 | 0.32656 | 7 | Each | [45 empty] | 16.4618 | 30.9021 | 43.4147 | Normal | 30.9021 | 0.4281 | 3 | 37.0825 |  |  |  | 24.7217 | 0.4281 | 7 | Each | 19.8735 | 34.3138 | 48.5324 | Normal | 34.3138 | 0.41127 | 3 | 41.1766 |  |  |  | 27.451 | 0.41127 | 7 | Each | [45 empty] | 1
| B1049.031 |  | B1049.031 | Post-tensioned concrete flat slabs- columns with shear reinforcing 0<Vg/Vo<.0.4 | 19500 | 36430 | 51100 | Normal | 35676.6482 | 0.34557 | 3 | 43716 |  |  |  | 29144 | 0.34557 | 7 | Each | 23500 | 40430 | 57100 | Normal | 40343.3338 | 0.32494 | 3 | 48516 |  |  |  | 32344 | 0.32494 | 7 | Each | [45 empty] | 16.6324 | 31.0726 | 43.5853 | Normal | 31.0726 | 0.42652 | 3 | 37.2871 |  |  |  | 24.8581 | 0.42652 | 7 | Each | 20.0441 | 34.4844 | 48.7029 | Normal | 34.4844 | 0.40998 | 3 | 41.3813 |  |  |  | 27.5875 | 0.40998 | 7 | Each | [45 empty] | 1
| B1049.032 |  | B1049.032 | Post-tensioned concrete flat slabs- columns with shear reinforcing 0.4<Vg/Vo<.0.6 | 20100 | 37030 | 51700 | Normal | 36276.6479 | 0.33986 | 3 | 44436 |  |  |  | 29624 | 0.33986 | 7 | Each | 24100 | 41030 | 57700 | Normal | 40943.3125 | 0.32018 | 3 | 49236 |  |  |  | 32824 | 0.32018 | 7 | Each | [45 empty] | 17.1441 | 31.5844 | 44.0971 | Normal | 31.5844 | 0.4219 | 3 | 37.9013 |  |  |  | 25.2675 | 0.4219 | 7 | Each | 20.5559 | 34.9962 | 49.2147 | Normal | 34.9962 | 0.40622 | 3 | 41.9954 |  |  |  | 27.997 | 0.40622 | 7 | Each | [45 empty] | 1
| B1049.041a |  | B1049.041a | Reinforced concrete flat slabs drop panel or drop capital- columns without shear reinforcing 0<Vg/Vo<0.4, no continuity reinf | 19300 | 36230 | 50900 | Normal | 35476.6482 | 0.34752 | 3 | 43476 |  |  |  | 28984 | 0.34752 | 7 | Each | 34300 | 49540 | 76700 | LogNormal | 50584.2443 | 0.32128 | 3 | 59448 |  |  |  | 39632 | 0.32128 | 7 | Each | [45 empty] | 16.4618 | 30.9021 | 43.4147 | Normal | 30.9021 | 0.4281 | 3 | 37.0825 |  |  |  | 24.7217 | 0.4281 | 7 | Each | 29.2559 | 42.2547 | 65.4206 | LogNormal | 42.2547 | 0.40709 | 3 | 50.7056 |  |  |  | 33.8038 | 0.40709 | 7 | Each | [45 empty] | 1
| B1049.041b |  | B1049.041b | Reinforced concrete flat slabs drop panel or drop capital- columns without shear reinforcing 0<Vg/Vo<0.4, with continuity reinf | 19300 | 36230 | 50900 | Normal | 35476.6482 | 0.34752 | 3 | 43476 |  |  |  | 28984 | 0.34752 | 7 | Each | 23300 | 40230 | 56900 | Normal | 40143.3111 | 0.32656 | 3 | 48276 |  |  |  | 32184 | 0.32656 | 7 | Each | [45 empty] | 16.4618 | 30.9021 | 43.4147 | Normal | 30.9021 | 0.4281 | 3 | 37.0825 |  |  |  | 24.7217 | 0.4281 | 7 | Each | 19.8735 | 34.3138 | 48.5324 | Normal | 34.3138 | 0.41127 | 3 | 41.1766 |  |  |  | 27.451 | 0.41127 | 7 | Each | [45 empty] | 1
| B1049.042a |  | B1049.042a | Reinforced concrete flat slabs drop panel or drop capital- columns without shear reinforcing 0.4<Vg/Vo<0.6, no continuity reinf | 19900 | 36830 | 51500 | Normal | 36076.648 | 0.34174 | 3 | 44196 |  |  |  | 29464 | 0.34174 | 7 | Each | 34300 | 49540 | 76700 | LogNormal | 50584.2443 | 0.32128 | 3 | 59448 |  |  |  | 39632 | 0.32128 | 7 | Each | [45 empty] | 16.9735 | 31.4138 | 43.9265 | Normal | 31.4138 | 0.42342 | 3 | 37.6966 |  |  |  | 25.131 | 0.42342 | 7 | Each | 29.2559 | 42.2547 | 65.4206 | LogNormal | 42.2547 | 0.40709 | 3 | 50.7056 |  |  |  | 33.8038 | 0.40709 | 7 | Each | [45 empty] | 1
| B1049.042b |  | B1049.042b | Reinforced concrete flat slabs drop panel or drop capital- columns without shear reinforcing 0.4<Vg/Vo<0.6, with continuity reinf | 19900 | 36830 | 51500 | Normal | 36076.648 | 0.34174 | 3 | 44196 |  |  |  | 29464 | 0.34174 | 7 | Each | 23900 | 40830 | 57500 | Normal | 40743.3127 | 0.32175 | 3 | 48996 |  |  |  | 32664 | 0.32175 | 7 | Each | [45 empty] | 16.9735 | 31.4138 | 43.9265 | Normal | 31.4138 | 0.42342 | 3 | 37.6966 |  |  |  | 25.131 | 0.42342 | 7 | Each | 20.3853 | 34.8256 | 49.0441 | Normal | 34.8256 | 0.40746 | 3 | 41.7907 |  |  |  | 27.8605 | 0.40746 | 7 | Each | [45 empty] | 1
| B1042.001a |  | B1042.001a | Concrete link beam, diagonally reinforced, aspect ratio between 1.0 and 2.0, beam < 16" wide and depth < 30" | 9856 | 12906 | 26156 | LogNormal | 14632.0453 | 0.43843 | 5 | 15487.2 |  |  |  | 10324.8 | 0.43843 | 20 | Each | 13850 | 28440 | 39250 | Normal | 27179.9982 | 0.3646 | 5 | 34128 |  |  |  | 22752 | 0.3646 | 20 | Each | 22300 | 44390 | 59700 | Normal | 42129.8331 | 0.34635 | 5 | 53268 |  |  |  | 35512 | 0.34635 | 20 | Each | [30 empty] | 8.4066 | 11.0081 | 22.3095 | LogNormal | 11.0081 | 0.5047 | 5 | 13.2097 |  |  |  | 8.8065 | 0.5047 | 20 | Each | 11.8132 | 24.2576 | 33.4779 | Normal | 24.2576 | 0.44208 | 5 | 29.1091 |  |  |  | 19.4061 | 0.44208 | 20 | Each | 19.0206 | 37.8621 | 50.9206 | Normal | 37.8621 | 0.42715 | 5 | 45.4345 |  |  |  | 30.2897 | 0.42715 | 20 | Each | [30 empty] | 1
| B1042.001b |  | B1042.001b | Concrete link beam, diagonally reinforced, aspect ratio between 2.0 and 4.0, beam < 16" wide and depth < 30" | 8128 | 10578 | 24428 | LogNormal | 12373.7731 | 0.51577 | 5 | 12693.6 |  |  |  | 8462.4 | 0.51577 | 20 | Each | 13850 | 27840 | 39250 | Normal | 26979.9772 | 0.3673 | 5 | 33408 |  |  |  | 22272 | 0.3673 | 20 | Each | 20080 | 41570 | 58980 | Normal | 40209.9798 | 0.37744 | 5 | 49884 |  |  |  | 33256 | 0.37744 | 20 | Each | [30 empty] | 6.9327 | 9.0224 | 20.8356 | LogNormal | 9.0224 | 0.57317 | 5 | 10.8269 |  |  |  | 7.2179 | 0.57317 | 20 | Each | 11.8132 | 23.7459 | 33.4779 | Normal | 23.7459 | 0.44431 | 5 | 28.4951 |  |  |  | 18.9967 | 0.44431 | 20 | Each | 17.1271 | 35.4568 | 50.3065 | Normal | 35.4568 | 0.45273 | 5 | 42.5482 |  |  |  | 28.3654 | 0.45273 | 20 | Each | [30 empty] | 1
| B1042.002a |  | B1042.002a | Concrete link beam, conventionally reinforced, aspect ratio between 1.0 and 2.0, beam < 16" wide and depth < 30" | 9856 | 12906 | 26156 | LogNormal | 14632.0453 | 0.43843 | 5 | 15487.2 |  |  |  | 10324.8 | 0.43843 | 20 | Each | 13850 | 28440 | 39250 | Normal | 27179.9982 | 0.3646 | 5 | 34128 |  |  |  | 22752 | 0.3646 | 20 | Each | 22300 | 44390 | 59700 | Normal | 42129.8331 | 0.34635 | 5 | 53268 |  |  |  | 35512 | 0.34635 | 20 | Each | [30 empty] | 8.4066 | 11.0081 | 22.3095 | LogNormal | 11.0081 | 0.5047 | 5 | 13.2097 |  |  |  | 8.8065 | 0.5047 | 20 | Each | 11.8132 | 24.2576 | 33.4779 | Normal | 24.2576 | 0.44208 | 5 | 29.1091 |  |  |  | 19.4061 | 0.44208 | 20 | Each | 19.0206 | 37.8621 | 50.9206 | Normal | 37.8621 | 0.42715 | 5 | 45.4345 |  |  |  | 30.2897 | 0.42715 | 20 | Each | [30 empty] | 1
| B1042.002b |  | B1042.002b | Concrete link beam, conventionally reinforced, aspect ratio between 2.0 and 4.0, beam < 16" wide and depth < 30" | 8128 | 10578 | 24428 | LogNormal | 12373.7731 | 0.51577 | 5 | 12693.6 |  |  |  | 8462.4 | 0.51577 | 20 | Each | 13850 | 27840 | 39250 | Normal | 26979.9772 | 0.3673 | 5 | 33408 |  |  |  | 22272 | 0.3673 | 20 | Each | 20080 | 41570 | 58980 | Normal | 40209.9798 | 0.37744 | 5 | 49884 |  |  |  | 33256 | 0.37744 | 20 | Each | [30 empty] | 6.9327 | 9.0224 | 20.8356 | LogNormal | 9.0224 | 0.57317 | 5 | 10.8269 |  |  |  | 7.2179 | 0.57317 | 20 | Each | 11.8132 | 23.7459 | 33.4779 | Normal | 23.7459 | 0.44431 | 5 | 28.4951 |  |  |  | 18.9967 | 0.44431 | 20 | Each | 17.1271 | 35.4568 | 50.3065 | Normal | 35.4568 | 0.45273 | 5 | 42.5482 |  |  |  | 28.3654 | 0.45273 | 20 | Each | [30 empty] | 1
| B1042.011a |  | B1042.011a | Concrete link beam, diagonally reinforced, aspect ratio between 1.0 and 2.0, beam > 16" wide and depth < 30" | 9856 | 12906 | 26156 | LogNormal | 14632.0453 | 0.43843 | 5 | 15487.2 |  |  |  | 10324.8 | 0.43843 | 20 | Each | 14850 | 29440 | 40250 | Normal | 28179.9853 | 0.35166 | 5 | 35328 |  |  |  | 23552 | 0.35166 | 20 | Each | 23300 | 45390 | 60700 | Normal | 43129.6838 | 0.33833 | 5 | 54468 |  |  |  | 36312 | 0.33833 | 20 | Each | [30 empty] | 8.4066 | 11.0081 | 22.3095 | LogNormal | 11.0081 | 0.5047 | 5 | 13.2097 |  |  |  | 8.8065 | 0.5047 | 20 | Each | 12.6662 | 25.1106 | 34.3309 | Normal | 25.1106 | 0.43147 | 5 | 30.1327 |  |  |  | 20.0885 | 0.43147 | 20 | Each | 19.8735 | 38.715 | 51.7735 | Normal | 38.715 | 0.42067 | 5 | 46.458 |  |  |  | 30.972 | 0.42067 | 20 | Each | [30 empty] | 1
| B1042.011b |  | B1042.011b | Concrete link beam, diagonally reinforced, aspect ratio between 2.0 and 4.0, beam > 16" wide and depth < 30" | 8128 | 10578 | 24428 | LogNormal | 12373.7731 | 0.51577 | 5 | 12693.6 |  |  |  | 8462.4 | 0.51577 | 20 | Each | 14850 | 28840 | 40250 | Normal | 27979.8916 | 0.35418 | 5 | 34608 |  |  |  | 23072 | 0.35418 | 20 | Each | 21080 | 42570 | 59980 | Normal | 41209.9429 | 0.36828 | 5 | 51084 |  |  |  | 34056 | 0.36828 | 20 | Each | [30 empty] | 6.9327 | 9.0224 | 20.8356 | LogNormal | 9.0224 | 0.57317 | 5 | 10.8269 |  |  |  | 7.2179 | 0.57317 | 20 | Each | 12.6662 | 24.5988 | 34.3309 | Normal | 24.5988 | 0.43352 | 5 | 29.5186 |  |  |  | 19.679 | 0.43352 | 20 | Each | 17.98 | 36.3097 | 51.1594 | Normal | 36.3097 | 0.44512 | 5 | 43.5716 |  |  |  | 29.0478 | 0.44512 | 20 | Each | [30 empty] | 1
| B1042.012a |  | B1042.012a | Concrete link beam, conventionally reinforced, aspect ratio between 1.0 and 2.0, beam > 16" wide and depth < 30" | 9856 | 12906 | 26156 | LogNormal | 14632.0453 | 0.43843 | 5 | 15487.2 |  |  |  | 10324.8 | 0.43843 | 20 | Each | 14850 | 29440 | 40250 | Normal | 28179.9853 | 0.35166 | 5 | 35328 |  |  |  | 23552 | 0.35166 | 20 | Each | 23300 | 45390 | 60700 | Normal | 43129.6838 | 0.33833 | 5 | 54468 |  |  |  | 36312 | 0.33833 | 20 | Each | [30 empty] | 8.4066 | 11.0081 | 22.3095 | LogNormal | 11.0081 | 0.5047 | 5 | 13.2097 |  |  |  | 8.8065 | 0.5047 | 20 | Each | 12.6662 | 25.1106 | 34.3309 | Normal | 25.1106 | 0.43147 | 5 | 30.1327 |  |  |  | 20.0885 | 0.43147 | 20 | Each | 19.8735 | 38.715 | 51.7735 | Normal | 38.715 | 0.42067 | 5 | 46.458 |  |  |  | 30.972 | 0.42067 | 20 | Each | [30 empty] | 1
| B1042.012b |  | B1042.012b | Concrete link beam, conventionally reinforced, aspect ratio between 2.0 and 4.0, beam > 16" wide and depth < 30" | 8128 | 10578 | 24428 | LogNormal | 12373.7731 | 0.51577 | 5 | 12693.6 |  |  |  | 8462.4 | 0.51577 | 20 | Each | 14850 | 28840 | 40250 | Normal | 27979.8916 | 0.35418 | 5 | 34608 |  |  |  | 23072 | 0.35418 | 20 | Each | 21080 | 42570 | 59980 | Normal | 41209.9429 | 0.36828 | 5 | 51084 |  |  |  | 34056 | 0.36828 | 20 | Each | [30 empty] | 6.9327 | 9.0224 | 20.8356 | LogNormal | 9.0224 | 0.57317 | 5 | 10.8269 |  |  |  | 7.2179 | 0.57317 | 20 | Each | 12.6662 | 24.5988 | 34.3309 | Normal | 24.5988 | 0.43352 | 5 | 29.5186 |  |  |  | 19.679 | 0.43352 | 20 | Each | 17.98 | 36.3097 | 51.1594 | Normal | 36.3097 | 0.44512 | 5 | 43.5716 |  |  |  | 29.0478 | 0.44512 | 20 | Each | [30 empty] | 1
| B1042.021a |  | B1042.021a | Concrete link beam, diagonally reinforced, aspect ratio between 1.0 and 2.0, beam > 24" wide and depth < 30" | 9856 | 12906 | 26156 | LogNormal | 14632.0453 | 0.43843 | 5 | 15487.2 |  |  |  | 10324.8 | 0.43843 | 20 | Each | 14850 | 29440 | 40250 | Normal | 28179.9853 | 0.35166 | 5 | 35328 |  |  |  | 23552 | 0.35166 | 20 | Each | 23300 | 46390 | 60700 | Normal | 43463.3406 | 0.33572 | 5 | 55668 |  |  |  | 37112 | 0.33572 | 20 | Each | [30 empty] | 8.4066 | 11.0081 | 22.3095 | LogNormal | 11.0081 | 0.5047 | 5 | 13.2097 |  |  |  | 8.8065 | 0.5047 | 20 | Each | 12.6662 | 25.1106 | 34.3309 | Normal | 25.1106 | 0.43147 | 5 | 30.1327 |  |  |  | 20.0885 | 0.43147 | 20 | Each | 19.8735 | 39.5679 | 51.7735 | Normal | 39.5679 | 0.41858 | 5 | 47.4815 |  |  |  | 31.6543 | 0.41858 | 20 | Each | [30 empty] | 1
| B1042.021b |  | B1042.021b | Concrete link beam, diagonally reinforced, aspect ratio between 2.0 and 4.0, beam > 24" wide and depth < 30" | 8128 | 10578 | 24428 | LogNormal | 12373.7731 | 0.51577 | 5 | 12693.6 |  |  |  | 8462.4 | 0.51577 | 20 | Each | 14850 | 28840 | 40250 | Normal | 27979.8916 | 0.35418 | 5 | 34608 |  |  |  | 23072 | 0.35418 | 20 | Each | 21080 | 43570 | 59980 | Normal | 41543.332 | 0.36533 | 5 | 52284 |  |  |  | 34856 | 0.36533 | 20 | Each | [30 empty] | 6.9327 | 9.0224 | 20.8356 | LogNormal | 9.0224 | 0.57317 | 5 | 10.8269 |  |  |  | 7.2179 | 0.57317 | 20 | Each | 12.6662 | 24.5988 | 34.3309 | Normal | 24.5988 | 0.43352 | 5 | 29.5186 |  |  |  | 19.679 | 0.43352 | 20 | Each | 17.98 | 37.1626 | 51.1594 | Normal | 37.1626 | 0.44268 | 5 | 44.5951 |  |  |  | 29.7301 | 0.44268 | 20 | Each | [30 empty] | 1
| B1042.022a |  | B1042.022a | Concrete link beam, conventionally reinforced, aspect ratio between 1.0 and 2.0, beam > 24" wide and depth < 30" | 9856 | 12906 | 26156 | LogNormal | 14632.0453 | 0.43843 | 5 | 15487.2 |  |  |  | 10324.8 | 0.43843 | 20 | Each | 14850 | 29440 | 40250 | Normal | 28179.9853 | 0.35166 | 5 | 35328 |  |  |  | 23552 | 0.35166 | 20 | Each | 23300 | 46390 | 60700 | Normal | 43463.3406 | 0.33572 | 5 | 55668 |  |  |  | 37112 | 0.33572 | 20 | Each | [30 empty] | 8.4066 | 11.0081 | 22.3095 | LogNormal | 11.0081 | 0.5047 | 5 | 13.2097 |  |  |  | 8.8065 | 0.5047 | 20 | Each | 12.6662 | 25.1106 | 34.3309 | Normal | 25.1106 | 0.43147 | 5 | 30.1327 |  |  |  | 20.0885 | 0.43147 | 20 | Each | 19.8735 | 39.5679 | 51.7735 | Normal | 39.5679 | 0.41858 | 5 | 47.4815 |  |  |  | 31.6543 | 0.41858 | 20 | Each | [30 empty] | 1
| B1042.022b |  | B1042.022b | Concrete link beam, conventionally reinforced, aspect ratio between 2.0 and 4.0, beam > 24" wide and depth < 30" | 8128 | 10578 | 24428 | LogNormal | 12373.7731 | 0.51577 | 5 | 12693.6 |  |  |  | 8462.4 | 0.51577 | 20 | Each | 14850 | 28840 | 40250 | Normal | 27979.8916 | 0.35418 | 5 | 34608 |  |  |  | 23072 | 0.35418 | 20 | Each | 21080 | 43570 | 59980 | Normal | 41543.332 | 0.36533 | 5 | 52284 |  |  |  | 34856 | 0.36533 | 20 | Each | [30 empty] | 6.9327 | 9.0224 | 20.8356 | LogNormal | 9.0224 | 0.57317 | 5 | 10.8269 |  |  |  | 7.2179 | 0.57317 | 20 | Each | 12.6662 | 24.5988 | 34.3309 | Normal | 24.5988 | 0.43352 | 5 | 29.5186 |  |  |  | 19.679 | 0.43352 | 20 | Each | 17.98 | 37.1626 | 51.1594 | Normal | 37.1626 | 0.44268 | 5 | 44.5951 |  |  |  | 29.7301 | 0.44268 | 20 | Each | [30 empty] | 1
| B1051.001 |  | B1051.001 | Ordinary reinforced masonry walls with partially grouted cells, shear dominated, 4" to 6"' thick, up to 12 foot tall | 3650 | 4200 | 4783.3333 | Normal | 4211.1118 | 0.105 | 2 | 5040 |  |  |  | 3360 | 0.105 | 30 | 100 ft^2 Units | 4650 | 6000 | 6750 | Normal | 5799.9739 | 0.14126 | 2 | 7200 |  |  |  | 4800 | 0.14126 | 30 | 100 ft^2 Units | [45 empty] | 2.84 | 3.27 | 3.73 | Normal | 3.27 | 0.27116 | 2 | 3.9247 |  |  |  | 2.6153 | 0.27116 | 30 | 100 ft^2 Units | 3.62 | 4.68 | 5.26 | Normal | 4.68 | 0.28715 | 2 | 5.6153 |  |  |  | 3.7447 | 0.28715 | 30 | 100 ft^2 Units | [45 empty] | 100
| B1051.002 |  | B1051.002 | Ordinary reinforced masonry walls with partially grouted cells, shear dominated, 4" to 6"' thick, greater than 12 foot tall | 7375 | 8200 | 9075 | LogNormal | 8187.3936 | 0.080803 | 1 | 9840 |  |  |  | 6560 | 0.080803 | 14 | 225 ft^2 Units | 9600 | 12375 | 13500 | Normal | 11824.8385 | 0.12867 | 1 | 14850 |  |  |  | 9900 | 0.12867 | 14 | 225 ft^2 Units | [45 empty] | 6.3 | 6.9975 | 7.74 | LogNormal | 6.9975 | 0.26273 | 1 | 8.3963 |  |  |  | 5.5987 | 0.26273 | 14 | 225 ft^2 Units | 8.19 | 10.5525 | 11.52 | Normal | 10.5525 | 0.28117 | 1 | 12.6635 |  |  |  | 8.4415 | 0.28117 | 14 | 225 ft^2 Units | [45 empty] | 225
| B1051.003 |  | B1051.003 | Ordinary reinforced masonry walls with partially grouted cells, 4" to 6" thick, flexure dominated up to 12' tall | 366.6667 | 600 | 933.3333 | LogNormal | 591.3197 | 0.35842 | 2 | 720 |  |  |  | 480 | 0.35842 | 30 | 100 ft^2 Units | 3650 | 4200 | 4783.3333 | Normal | 4211.1098 | 0.105 | 2 | 5040 |  |  |  | 3360 | 0.105 | 30 | 100 ft^2 Units | 4650 | 6000 | 6750 | Normal | 5799.9739 | 0.14126 | 2 | 7200 |  |  |  | 4800 | 0.14126 | 30 | 100 ft^2 Units | [30 empty] | 0.29 | 0.47 | 0.73 | LogNormal | 0.47 | 0.437 | 2 | 0.56353 |  |  |  | 0.37647 | 0.437 | 30 | 100 ft^2 Units | 2.84 | 3.27 | 3.73 | Normal | 3.27 | 0.27116 | 2 | 3.9247 |  |  |  | 2.6153 | 0.27116 | 30 | 100 ft^2 Units | 3.62 | 4.68 | 5.26 | Normal | 4.68 | 0.28715 | 2 | 5.6153 |  |  |  | 3.7447 | 0.28715 | 30 | 100 ft^2 Units | [30 empty] | 100
| B1051.004 |  | B1051.004 | Ordinary reinforced masonry walls with partially grouted cells, 4" to 6" thick, flexure dominated greater than 12' tall | 825 | 1350 | 2100 | LogNormal | 1330.4693 | 0.35842 | 1 | 1620 |  |  |  | 1080 | 0.35842 | 14 | 225 ft^2 Units | 7375 | 8200 | 9075 | LogNormal | 8187.3936 | 0.080803 | 1 | 9840 |  |  |  | 6560 | 0.080803 | 14 | 225 ft^2 Units | 9600 | 12375 | 13500 | Normal | 11824.8385 | 0.12867 | 1 | 14850 |  |  |  | 9900 | 0.12867 | 14 | 225 ft^2 Units | [30 empty] | 0.6975 | 1.1475 | 1.8 | LogNormal | 1.1475 | 0.437 | 1 | 1.3778 |  |  |  | 0.91721 | 0.437 | 14 | 225 ft^2 Units | 6.3 | 6.9975 | 7.74 | LogNormal | 6.9975 | 0.26273 | 1 | 8.3963 |  |  |  | 5.5987 | 0.26273 | 14 | 225 ft^2 Units | 8.19 | 10.5525 | 11.52 | Normal | 10.5525 | 0.28117 | 1 | 12.6635 |  |  |  | 8.4415 | 0.28117 | 14 | 225 ft^2 Units | [30 empty] | 225
| B1051.011 |  | B1051.011 | Ordinary reinforced masonry walls with partially grouted cells, shear dominated, 8" to 12"' thick, up to 12 foot tall | 3800 | 4350 | 4933.3333 | Normal | 4361.1109 | 0.10139 | 2 | 5220 |  |  |  | 3480 | 0.10139 | 30 | 100 ft^2 Units | 5783.3333 | 7633.3333 | 8383.3333 | Normal | 7266.5833 | 0.1396 | 2 | 9160 |  |  |  | 6106.6667 | 0.1396 | 30 | 100 ft^2 Units | [45 empty] | 2.96 | 3.39 | 3.85 | Normal | 3.39 | 0.26978 | 2 | 4.0681 |  |  |  | 2.7119 | 0.26978 | 30 | 100 ft^2 Units | 4.51 | 5.95 | 6.53 | Normal | 5.95 | 0.28634 | 2 | 7.1399 |  |  |  | 4.7601 | 0.28634 | 30 | 100 ft^2 Units | [45 empty] | 100
| B1051.012 |  | B1051.012 | Ordinary reinforced masonry walls with partially grouted cells, shear dominated, 8" to 12"' thick, greater than 12 foot tall | 7712.5 | 8537.5 | 9412.5 | LogNormal | 8526.0453 | 0.077612 | 1 | 10245 |  |  |  | 6830 | 0.077612 | 14 | 225 ft^2 Units | 11900 | 15800 | 16675 | Normal | 14791.5267 | 0.12595 | 1 | 18960 |  |  |  | 12640 | 0.12595 | 14 | 225 ft^2 Units | [45 empty] | 6.57 | 7.29 | 8.0325 | LogNormal | 7.29 | 0.26177 | 1 | 8.7464 |  |  |  | 5.8336 | 0.26177 | 14 | 225 ft^2 Units | 10.1475 | 13.4775 | 14.22 | Normal | 13.4775 | 0.27993 | 1 | 16.1728 |  |  |  | 10.7822 | 0.27993 | 14 | 225 ft^2 Units | [45 empty] | 225
| B1051.013 |  | B1051.013 | Ordinary reinforced masonry walls with partially grouted cells, 8" to 12" thick, flexure dominated up to 12' tall | 366.6667 | 600 | 933.3333 | LogNormal | 591.3197 | 0.35842 | 2 | 720 |  |  |  | 480 | 0.35842 | 30 | 100 ft^2 Units | 3800 | 4350 | 4933.3333 | Normal | 4361.1108 | 0.10139 | 2 | 5220 |  |  |  | 3480 | 0.10139 | 30 | 100 ft^2 Units | 5783.3333 | 7633.3333 | 8383.3333 | Normal | 7266.5833 | 0.1396 | 2 | 9160 |  |  |  | 6106.6667 | 0.1396 | 30 | 100 ft^2 Units | [30 empty] | 0.29 | 0.47 | 0.73 | LogNormal | 0.47 | 0.437 | 2 | 0.56353 |  |  |  | 0.37647 | 0.437 | 30 | 100 ft^2 Units | 2.96 | 3.39 | 3.85 | Normal | 3.39 | 0.26978 | 2 | 4.0681 |  |  |  | 2.7119 | 0.26978 | 30 | 100 ft^2 Units | 4.51 | 5.95 | 6.53 | Normal | 5.95 | 0.28634 | 2 | 7.1399 |  |  |  | 4.7601 | 0.28634 | 30 | 100 ft^2 Units | [30 empty] | 100
| B1051.014 |  | B1051.014 | Ordinary reinforced masonry walls with partially grouted cells, 8" to 12" thick, flexure dominated greater than 12' tall | 825 | 1350 | 2100 | LogNormal | 1330.4693 | 0.35842 | 1 | 1620 |  |  |  | 1080 | 0.35842 | 14 | 225 ft^2 Units | 7712.5 | 8537.5 | 9412.5 | LogNormal | 8526.0453 | 0.077612 | 1 | 10245 |  |  |  | 6830 | 0.077612 | 14 | 225 ft^2 Units | 11900 | 15800 | 16675 | Normal | 14791.5267 | 0.12595 | 1 | 18960 |  |  |  | 12640 | 0.12595 | 14 | 225 ft^2 Units | [30 empty] | 0.6975 | 1.1475 | 1.8 | LogNormal | 1.1475 | 0.437 | 1 | 1.3778 |  |  |  | 0.91721 | 0.437 | 14 | 225 ft^2 Units | 6.57 | 7.29 | 8.0325 | LogNormal | 7.29 | 0.26177 | 1 | 8.7464 |  |  |  | 5.8336 | 0.26177 | 14 | 225 ft^2 Units | 10.1475 | 13.4775 | 14.22 | Normal | 13.4775 | 0.27993 | 1 | 16.1728 |  |  |  | 10.7822 | 0.27993 | 14 | 225 ft^2 Units | [30 empty] | 225
| B1051.021 |  | B1051.021 | Ordinary reinforced masonry walls with partially grouted cells, shear dominated, 16" thick, up to 12 foot tall | 3950 | 4500 | 5083.3333 | Normal | 4511.1105 | 0.098018 | 2 | 5850 |  |  |  | 3150 | 0.098018 | 30 | 100 ft^2 Units | 6616.6667 | 8466.6667 | 9216.6667 | Normal | 8099.9819 | 0.12523 | 2 | 10160 |  |  |  | 6350 | 0.12523 | 30 | 100 ft^2 Units | [45 empty] | 3.08 | 3.51 | 3.96 | Normal | 3.51 | 0.26853 | 2 | 4.5622 |  |  |  | 2.4578 | 0.26853 | 30 | 100 ft^2 Units | 5.16 | 6.6 | 7.18 | Normal | 6.6 | 0.27961 | 2 | 7.9198 |  |  |  | 4.9502 | 0.27961 | 30 | 100 ft^2 Units | [45 empty] | 100
| B1051.022 |  | B1051.022 | Ordinary reinforced masonry walls with partially grouted cells, shear dominated,16"' thick, greater than 12 foot tall | 7800 | 8625 | 9500 | LogNormal | 8613.8267 | 0.076825 | 1 | 11212.5 |  |  |  | 6037.5 | 0.076825 | 14 | 225 ft^2 Units | 13525 | 17425 | 18300 | Normal | 16416.6498 | 0.11348 | 1 | 20910 |  |  |  | 13068.75 | 0.11348 | 14 | 225 ft^2 Units | [45 empty] | 6.66 | 7.3575 | 8.1 | LogNormal | 7.3575 | 0.26154 | 1 | 9.5645 |  |  |  | 5.1505 | 0.26154 | 14 | 225 ft^2 Units | 11.5425 | 14.8725 | 15.615 | Normal | 14.8725 | 0.27455 | 1 | 17.845 |  |  |  | 11.1569 | 0.27455 | 14 | 225 ft^2 Units | [45 empty] | 225
| B1051.023 |  | B1051.023 | Ordinary reinforced masonry walls with partially grouted cells, 16" thick, flexure dominated up to 12' tall | 366.6667 | 600 | 933.3333 | LogNormal | 591.3197 | 0.35842 | 2 | 780 |  |  |  | 420 | 0.35842 | 30 | 100 ft^2 Units | 3950 | 4500 | 5083.3333 | Normal | 4511.1111 | 0.098018 | 2 | 5400 |  |  |  | 3375 | 0.098018 | 30 | 100 ft^2 Units | 6616.6667 | 8466.6667 | 9216.6667 | Normal | 8099.9819 | 0.12523 | 2 | 10160 |  |  |  | 6350 | 0.12523 | 30 | 100 ft^2 Units | [30 empty] | 0.29 | 0.47 | 0.73 | LogNormal | 0.47 | 0.437 | 2 | 0.61029 |  |  |  | 0.32971 | 0.437 | 30 | 100 ft^2 Units | 3.08 | 3.51 | 3.96 | Normal | 3.51 | 0.26853 | 2 | 4.2115 |  |  |  | 2.6332 | 0.26853 | 30 | 100 ft^2 Units | 5.16 | 6.6 | 7.18 | Normal | 6.6 | 0.27961 | 2 | 7.9198 |  |  |  | 4.9502 | 0.27961 | 30 | 100 ft^2 Units | [30 empty] | 100
| B1051.024 |  | B1051.024 | Ordinary reinforced masonry walls with partially grouted cells, 16" thick, flexure dominated greater than 12' tall | 825 | 1350 | 2100 | LogNormal | 1330.4693 | 0.35842 | 1 | 1755 |  |  |  | 945 | 0.35842 | 14 | 225 ft^2 Units | 7800 | 8625 | 9500 | LogNormal | 8613.8267 | 0.076825 | 1 | 10350 |  |  |  | 6468.75 | 0.076825 | 14 | 225 ft^2 Units | 13525 | 17425 | 18300 | Normal | 16416.6498 | 0.11348 | 1 | 20910 |  |  |  | 13068.75 | 0.11348 | 14 | 225 ft^2 Units | [30 empty] | 0.6975 | 1.1475 | 1.8 | LogNormal | 1.1475 | 0.437 | 1 | 1.4929 |  |  |  | 0.80206 | 0.437 | 14 | 225 ft^2 Units | 6.66 | 7.3575 | 8.1 | LogNormal | 7.3575 | 0.26154 | 1 | 8.8288 |  |  |  | 5.5183 | 0.26154 | 14 | 225 ft^2 Units | 11.5425 | 14.8725 | 15.615 | Normal | 14.8725 | 0.27455 | 1 | 17.845 |  |  |  | 11.1569 | 0.27455 | 14 | 225 ft^2 Units | [30 empty] | 225
| B1052.001 |  | B1052.001 | Special reinforced masonry walls with fully grouted cells, 8" or 12" thick, shear dominated, up t o12' tall | 3400 | 3950 | 4533.3333 | Normal | 3961.1123 | 0.11163 | 2 | 5135 |  |  |  | 2765 | 0.11163 | 30 | 100 ft^2 Units | 5983.3333 | 7833.3333 | 8416.6667 | Normal | 7411.1056 | 0.1281 | 2 | 9400 |  |  |  | 5875 | 0.1281 | 30 | 100 ft^2 Units | [45 empty] | 2.65 | 3.08 | 3.53 | Normal | 3.08 | 0.27379 | 2 | 4.0036 |  |  |  | 2.1564 | 0.27379 | 30 | 100 ft^2 Units | 4.66 | 6.11 | 6.56 | Normal | 6.11 | 0.28091 | 2 | 7.3311 |  |  |  | 4.5837 | 0.28091 | 30 | 100 ft^2 Units | [45 empty] | 100
| B1052.002 |  | B1052.002 | Special reinforced masonry walls with fully grouted cells, 8" or 12" thick, shear dominated, greater than 12' tall | 6812.5 | 7637.5 | 8512.5 | LogNormal | 7622.7593 | 0.086747 | 1 | 9928.75 |  |  |  | 5346.25 | 0.086747 | 14 | 225 ft^2 Units | 12350 | 16250 | 17125 | Normal | 15241.66 | 0.12223 | 1 | 19500 |  |  |  | 12187.5 | 0.12223 | 14 | 225 ft^2 Units | [45 empty] | 5.805 | 6.525 | 7.2675 | LogNormal | 6.525 | 0.26462 | 1 | 8.4793 |  |  |  | 4.5707 | 0.26462 | 14 | 225 ft^2 Units | 10.53 | 13.86 | 14.6025 | Normal | 13.86 | 0.27828 | 1 | 16.6321 |  |  |  | 10.3949 | 0.27828 | 14 | 225 ft^2 Units | [45 empty] | 225
| B1052.003 |  | B1052.003 | Special reinforced masonry walls with fully grouted cells, 8" to 12" thick, flexure dominated up to 12' tall | 366.6667 | 600 | 933.3333 | LogNormal | 591.3197 | 0.35842 | 2 | 900 |  |  |  | 480 | 0.35842 | 30 | 100 ft^2 Units | 3400 | 3950 | 4533.3333 | Normal | 3961.1096 | 0.11163 | 2 | 5925 |  |  |  | 3357.5 | 0.11163 | 30 | 100 ft^2 Units | 5983.3333 | 7833.3333 | 8416.6667 | Normal | 7411.1056 | 0.1281 | 2 | 11750 |  |  |  | 6658.3333 | 0.1281 | 30 | 100 ft^2 Units | [30 empty] | 0.29 | 0.47 | 0.73 | LogNormal | 0.47 | 0.437 | 2 | 0.70382 |  |  |  | 0.37647 | 0.437 | 30 | 100 ft^2 Units | 2.65 | 3.08 | 3.53 | Normal | 3.08 | 0.27379 | 2 | 4.6193 |  |  |  | 2.6182 | 0.27379 | 30 | 100 ft^2 Units | 4.66 | 6.11 | 6.56 | Normal | 6.11 | 0.28091 | 2 | 9.1627 |  |  |  | 5.1942 | 0.28091 | 30 | 100 ft^2 Units | [30 empty] | 100
| B1052.004 |  | B1052.004 | Special reinforced masonry walls with fully grouted cells, 8" to 12" thick, flexure dominated greater than 12' tall | 825 | 1350 | 2100 | LogNormal | 1330.4693 | 0.35842 | 1 | 2025 |  |  |  | 1080 | 0.35842 | 14 | 225 ft^2 Units | 6812.5 | 7637.5 | 8512.5 | LogNormal | 7622.7593 | 0.086747 | 1 | 11456.25 |  |  |  | 6491.875 | 0.086747 | 14 | 225 ft^2 Units | 12350 | 16250 | 17125 | Normal | 15241.66 | 0.12223 | 1 | 24375 |  |  |  | 13812.5 | 0.12223 | 14 | 225 ft^2 Units | [30 empty] | 0.6975 | 1.1475 | 1.8 | LogNormal | 1.1475 | 0.437 | 1 | 1.7232 |  |  |  | 0.91721 | 0.437 | 14 | 225 ft^2 Units | 5.805 | 6.525 | 7.2675 | LogNormal | 6.525 | 0.26462 | 1 | 9.7822 |  |  |  | 5.5478 | 0.26462 | 14 | 225 ft^2 Units | 10.53 | 13.86 | 14.6025 | Normal | 13.86 | 0.27828 | 1 | 20.7901 |  |  |  | 11.781 | 0.27828 | 14 | 225 ft^2 Units | [30 empty] | 225
| B1052.011 |  | B1052.011 | Special reinforced masonry walls with fully grouted cells, 16" thick, shear dominated, up to 12' tall | 3550 | 4100 | 4683.3333 | Normal | 4111.1118 | 0.10755 | 2 | 6150 |  |  |  | 3280 | 0.10755 | 30 | 100 ft^2 Units | 6916.6667 | 8766.6667 | 9350 | Normal | 8344.4458 | 0.11377 | 2 | 13150 |  |  |  | 7451.6667 | 0.11377 | 30 | 100 ft^2 Units | [45 empty] | 2.77 | 3.2 | 3.65 | Normal | 3.2 | 0.27215 | 2 | 4.7978 |  |  |  | 2.5609 | 0.27215 | 30 | 100 ft^2 Units | 5.39 | 6.83 | 7.29 | Normal | 6.83 | 0.27467 | 2 | 10.2464 |  |  |  | 5.8051 | 0.27467 | 30 | 100 ft^2 Units | [45 empty] | 100
| B1052.012 |  | B1052.012 | Special reinforced masonry walls with fully grouted cells, 16" thick, shear dominated, greater than 12' tall | 7150 | 7975 | 8850 | LogNormal | 7961.5746 | 0.08308 | 1 | 11962.5 |  |  |  | 6380 | 0.08308 | 14 | 225 ft^2 Units | 14200 | 18100 | 18975 | Normal | 17091.7654 | 0.10899 | 1 | 27150 |  |  |  | 15385 | 0.10899 | 14 | 225 ft^2 Units | [45 empty] | 6.0975 | 6.795 | 7.5375 | LogNormal | 6.795 | 0.26344 | 1 | 10.1961 |  |  |  | 5.4346 | 0.26344 | 14 | 225 ft^2 Units | 12.105 | 15.435 | 16.1775 | Normal | 15.435 | 0.27272 | 1 | 23.1541 |  |  |  | 13.1193 | 0.27272 | 14 | 225 ft^2 Units | [45 empty] | 225
| B1052.013 |  | B1052.013 | Special reinforced masonry walls with fully grouted cells, 16" thick, flexure dominated up to 12' tall | 366.6667 | 600 | 933.3333 | LogNormal | 591.3197 | 0.35842 | 2 | 900 |  |  |  | 480 | 0.35842 | 30 | 100 ft^2 Units | 3550 | 4100 | 4683.3333 | Normal | 4111.1119 | 0.10756 | 2 | 6150 |  |  |  | 3485 | 0.10756 | 30 | 100 ft^2 Units | 6916.6667 | 8766.6667 | 9350 | Normal | 8344.4458 | 0.11377 | 2 | 13150 |  |  |  | 7451.6667 | 0.11377 | 30 | 100 ft^2 Units | [30 empty] | 0.29 | 0.47 | 0.73 | LogNormal | 0.47 | 0.437 | 2 | 0.70382 |  |  |  | 0.37647 | 0.437 | 30 | 100 ft^2 Units | 2.77 | 3.2 | 3.65 | Normal | 3.2 | 0.27215 | 2 | 4.7978 |  |  |  | 2.7207 | 0.27215 | 30 | 100 ft^2 Units | 5.39 | 6.83 | 7.29 | Normal | 6.83 | 0.27467 | 2 | 10.2464 |  |  |  | 5.8051 | 0.27467 | 30 | 100 ft^2 Units | [30 empty] | 100
| B1052.014 |  | B1052.014 | Special reinforced masonry walls with fully grouted cells, 16" thick, flexure dominated greater than 12' tall | 825 | 1350 | 2100 | LogNormal | 1330.4693 | 0.35842 | 1 | 2025 |  |  |  | 1080 | 0.35842 | 14 | 225 ft^2 Units | 7150 | 7975 | 8850 | LogNormal | 7961.5746 | 0.08308 | 1 | 11962.5 |  |  |  | 6778.75 | 0.08308 | 14 | 225 ft^2 Units | 14200 | 18100 | 18975 | Normal | 17091.7654 | 0.10899 | 1 | 27150 |  |  |  | 15385 | 0.10899 | 14 | 225 ft^2 Units | [30 empty] | 0.6975 | 1.1475 | 1.8 | LogNormal | 1.1475 | 0.437 | 1 | 1.7232 |  |  |  | 0.91721 | 0.437 | 14 | 225 ft^2 Units | 6.0975 | 6.795 | 7.5375 | LogNormal | 6.795 | 0.26344 | 1 | 10.1961 |  |  |  | 5.7747 | 0.26344 | 14 | 225 ft^2 Units | 12.105 | 15.435 | 16.1775 | Normal | 15.435 | 0.27272 | 1 | 23.1541 |  |  |  | 13.1193 | 0.27272 | 14 | 225 ft^2 Units | [30 empty] | 225
| B1061.001a |  | B1061.001a | Cold formed steel walls with wood structural panel sheathing, interior - gypsum board | 2100 | 3050 | 4666.6667 | LogNormal | 3098.1237 | 0.31697 | 2 | 4575 |  |  |  | 2440 | 0.31697 | 30 | 100 ft^2 Units | 2000 | 3500 | 5683.3333 | LogNormal | 3428.0432 | 0.39744 | 2 | 5250 |  |  |  | 2975 | 0.39744 | 30 | 100 ft^2 Units | 3466.6667 | 4500 | 4650 | Normal | 4205.5307 | 0.10978 | 2 | 6750 |  |  |  | 3825 | 0.10978 | 30 | 100 ft^2 Units | [30 empty] | 2.04 | 2.96 | 4.53 | LogNormal | 2.96 | 0.40369 | 2 | 4.4401 |  |  |  | 2.3679 | 0.40369 | 30 | 100 ft^2 Units | 1.94 | 3.4 | 5.52 | LogNormal | 3.4 | 0.46953 | 2 | 5.0985 |  |  |  | 2.8904 | 0.46953 | 30 | 100 ft^2 Units | 3.36 | 4.37 | 4.51 | Normal | 4.37 | 0.27304 | 2 | 6.5538 |  |  |  | 3.7149 | 0.27304 | 30 | 100 ft^2 Units | [30 empty] | 100
| B1061.001b |  | B1061.001b | Cold formed steel walls with wood structural panel sheathing, exterior - stucco one side | 1758.3333 | 2191.6667 | 2975 | LogNormal | 2252.332 | 0.21105 | 2 | 3287.5 |  |  |  | 1753.3333 | 0.21105 | 30 | 100 ft^2 Units | 3408.3333 | 3825 | 6058.3333 | LogNormal | 4274.0968 | 0.25096 | 2 | 5737.5 |  |  |  | 3251.25 | 0.25096 | 30 | 100 ft^2 Units | 4591.6667 | 5375 | 5958.3333 | Normal | 5308.3306 | 0.10045 | 2 | 8062.5 |  |  |  | 4568.75 | 0.10045 | 30 | 100 ft^2 Units | [30 empty] | 1.71 | 2.13 | 2.89 | LogNormal | 2.13 | 0.32717 | 2 | 3.1936 |  |  |  | 1.7046 | 0.32717 | 30 | 100 ft^2 Units | 3.31 | 3.71 | 5.88 | LogNormal | 3.71 | 0.35424 | 2 | 5.5663 |  |  |  | 3.1531 | 0.35424 | 30 | 100 ft^2 Units | 4.46 | 5.22 | 5.78 | Normal | 5.22 | 0.26942 | 2 | 7.8285 |  |  |  | 4.4375 | 0.26942 | 30 | 100 ft^2 Units | [30 empty] | 100
| B1061.011a |  | B1061.011a | Cold formed steel walls with flat strap X-bracing, interior - gypsum board | 2325 | 3116.6667 | 4283.3333 | LogNormal | 3141.1303 | 0.24037 | 2 | 4051.6667 |  |  |  | 2493.3333 | 0.24037 | 6 | 100 ft^2 Units | 3258.3333 | 3775 | 4191.6667 | Normal | 3741.6648 | 0.097321 | 2 | 4530 |  |  |  | 3208.75 | 0.097321 | 6 | 100 ft^2 Units | [45 empty] | 2.26 | 3.03 | 4.16 | LogNormal | 3.03 | 0.34681 | 2 | 3.9375 |  |  |  | 2.425 | 0.34681 | 6 | 100 ft^2 Units | 3.16 | 3.66 | 4.07 | Normal | 3.66 | 0.26827 | 2 | 4.3928 |  |  |  | 3.1104 | 0.26827 | 6 | 100 ft^2 Units | [45 empty] | 100
| B1061.011b |  | B1061.011b | Cold formed steel walls with flat strap X-bracing, exterior - stucco one side | 2783.3333 | 3075 | 4441.6667 | LogNormal | 3357.07 | 0.19902 | 3 | 3997.5 |  |  |  | 2460 | 0.19902 | 8 | 100 ft^2 Units | 4633.3333 | 4916.6667 | 6350 | LogNormal | 5248.8852 | 0.13115 | 3 | 5900 |  |  |  | 4179.1667 | 0.13115 | 8 | 100 ft^2 Units | [45 empty] | 2.7 | 2.98 | 4.31 | LogNormal | 2.98 | 0.31954 | 3 | 3.8754 |  |  |  | 2.3831 | 0.31954 | 8 | 100 ft^2 Units | 4.5 | 4.77 | 6.16 | LogNormal | 4.77 | 0.28231 | 3 | 5.7244 |  |  |  | 4.0542 | 0.28231 | 8 | 100 ft^2 Units | [45 empty] | 100
| B1061.021a |  | B1061.021a | Cold formed steel walls with 22 or 31 mil steel sheathing, interior - gypsum board | 2100 | 3050 | 4666.6667 | LogNormal | 3098.1237 | 0.31697 | 4 | 3965 |  |  |  | 2440 | 0.31697 | 11 | 100 ft^2 Units | 2450 | 4150 | 6133.3333 | Normal | 4244.455 | 0.33857 | 4 | 4980 |  |  |  | 3527.5 | 0.33857 | 11 | 100 ft^2 Units | [45 empty] | 2.04 | 2.96 | 4.53 | LogNormal | 2.96 | 0.40369 | 4 | 3.8481 |  |  |  | 2.3679 | 0.40369 | 11 | 100 ft^2 Units | 2.38 | 4.03 | 5.95 | Normal | 4.03 | 0.42087 | 4 | 4.8356 |  |  |  | 3.4258 | 0.42087 | 11 | 100 ft^2 Units | [45 empty] | 100
| B1061.021b |  | B1061.021b | Cold formed steel walls with 22 or 31 mil steel sheathing, exterior - stucco one side | 1891.6667 | 2308.3333 | 3658.3333 | LogNormal | 2506.2097 | 0.28026 | 2 | 3000.8333 |  |  |  | 1846.6667 | 0.28026 | 6 | 100 ft^2 Units | 4091.6667 | 4775 | 6225 | LogNormal | 4950.6944 | 0.16982 | 2 | 5730 |  |  |  | 4058.75 | 0.16982 | 6 | 100 ft^2 Units | [45 empty] | 1.84 | 2.24 | 3.55 | LogNormal | 2.24 | 0.37556 | 2 | 2.9121 |  |  |  | 1.7919 | 0.37556 | 6 | 100 ft^2 Units | 3.97 | 4.63 | 6.04 | LogNormal | 4.63 | 0.30222 | 2 | 5.5569 |  |  |  | 3.9348 | 0.30222 | 6 | 100 ft^2 Units | [45 empty] | 100
| B1071.001 |  | B1071.001 | Light framed wood walls with structural panel sheathing, gypsum wallboard no hold-downs | 1375 | 1641.6667 | 2191.6667 | LogNormal | 1702.1648 | 0.18873 | 3 | 2134.1667 |  |  |  | 1313.3333 | 0.18873 | 8 | 100 ft^2 Units | 1708.3333 | 2141.6667 | 2925 | LogNormal | 2201.0716 | 0.21585 | 3 | 2570 |  |  |  | 1820.4167 | 0.21585 | 8 | 100 ft^2 Units | 5191.6667 | 5375 | 6308.3333 | LogNormal | 5605.3301 | 0.079218 | 3 | 6450 |  |  |  | 4568.75 | 0.079218 | 8 | 100 ft^2 Units | [30 empty] | 1.33 | 1.59 | 2.13 | LogNormal | 1.59 | 0.31324 | 3 | 2.068 |  |  |  | 1.2713 | 0.31324 | 8 | 100 ft^2 Units | 1.66 | 2.08 | 2.84 | LogNormal | 2.08 | 0.33029 | 3 | 2.4957 |  |  |  | 1.7682 | 0.33029 | 8 | 100 ft^2 Units | 5.04 | 5.22 | 6.12 | LogNormal | 5.22 | 0.26225 | 3 | 6.2634 |  |  |  | 4.4375 | 0.26225 | 8 | 100 ft^2 Units | [30 empty] | 100
| B1071.012 |  | B1071.012 | Light framed wood walls with structural panel sheathing, stucco, hold-downs | 1766.6667 | 2300 | 3333.3333 | LogNormal | 2378.6919 | 0.25663 | 2 | 2990 |  |  |  | 1840 | 0.25663 | 6 | 100 ft^2 Units | 1666.6667 | 2750 | 4350 | LogNormal | 2717.0542 | 0.36907 | 2 | 3300 |  |  |  | 2337.5 | 0.36907 | 6 | 100 ft^2 Units | 3466.6667 | 4500 | 4650 | Normal | 4205.5307 | 0.10978 | 2 | 5400 |  |  |  | 3825 | 0.10978 | 6 | 100 ft^2 Units | [30 empty] | 1.71 | 2.23 | 3.24 | LogNormal | 2.23 | 0.35828 | 2 | 2.8997 |  |  |  | 1.7835 | 0.35828 | 6 | 100 ft^2 Units | 1.62 | 2.67 | 4.22 | LogNormal | 2.67 | 0.44577 | 2 | 3.2038 |  |  |  | 2.2696 | 0.44577 | 6 | 100 ft^2 Units | 3.36 | 4.37 | 4.51 | Normal | 4.37 | 0.27304 | 2 | 5.2435 |  |  |  | 3.7149 | 0.27304 | 6 | 100 ft^2 Units | [30 empty] | 100
| B1071.011 |  | B1071.011 | Light framed wood walls with structural panel sheathing, stucco no hold-downs | 1766.6667 | 2300 | 3333.3333 | LogNormal | 2378.6919 | 0.25663 | 2 | 2990 |  |  |  | 1840 | 0.25663 | 6 | 100 ft^2 Units | 1666.6667 | 2750 | 4350 | LogNormal | 2717.0542 | 0.36907 | 2 | 3300 |  |  |  | 2337.5 | 0.36907 | 6 | 100 ft^2 Units | 3466.6667 | 4500 | 4650 | Normal | 4205.5307 | 0.10978 | 2 | 5400 |  |  |  | 3825 | 0.10978 | 6 | 100 ft^2 Units | [30 empty] | 1.71 | 2.23 | 3.24 | LogNormal | 2.23 | 0.35828 | 2 | 2.8997 |  |  |  | 1.7835 | 0.35828 | 6 | 100 ft^2 Units | 1.62 | 2.67 | 4.22 | LogNormal | 2.67 | 0.44577 | 2 | 3.2038 |  |  |  | 2.2696 | 0.44577 | 6 | 100 ft^2 Units | 3.36 | 4.37 | 4.51 | Normal | 4.37 | 0.27304 | 2 | 5.2435 |  |  |  | 3.7149 | 0.27304 | 6 | 100 ft^2 Units | [30 empty] | 100
| B1071.002 |  | B1071.002 | Light framed wood walls with structural panel sheathing, gypsum wallboard and hold-downs | 1375 | 1641.6667 | 2191.6667 | LogNormal | 1702.1648 | 0.18873 | 3 | 2134.1667 |  |  |  | 1313.3333 | 0.18873 | 8 | 100 ft^2 Units | 1708.3333 | 2141.6667 | 2925 | LogNormal | 2201.0716 | 0.21585 | 3 | 2570 |  |  |  | 1820.4167 | 0.21585 | 8 | 100 ft^2 Units | 5191.6667 | 5375 | 6308.3333 | LogNormal | 5605.3301 | 0.079218 | 3 | 6450 |  |  |  | 4568.75 | 0.079218 | 8 | 100 ft^2 Units | [30 empty] | 1.33 | 1.59 | 2.13 | LogNormal | 1.59 | 0.31324 | 3 | 2.068 |  |  |  | 1.2713 | 0.31324 | 8 | 100 ft^2 Units | 1.66 | 2.08 | 2.84 | LogNormal | 2.08 | 0.33029 | 3 | 2.4957 |  |  |  | 1.7682 | 0.33029 | 8 | 100 ft^2 Units | 5.04 | 5.22 | 6.12 | LogNormal | 5.22 | 0.26225 | 3 | 6.2634 |  |  |  | 4.4375 | 0.26225 | 8 | 100 ft^2 Units | [30 empty] | 100
| B1071.031 |  | B1071.031 | Wood walls with diagonal let-in bracing | 4011.8056 | 4741.6667 | 5274.3056 | Normal | 4675.9236 | 0.10534 | 4 | 6164.1667 |  |  |  | 3793.3333 | 0.10534 | 11 | 100 ft^2 Units | [60 empty] | 3.89 | 4.6 | 5.12 | Normal | 4.6 | 0.27129 | 4 | 5.9807 |  |  |  | 3.6796 | 0.27129 | 11 | 100 ft^2 Units | [60 empty] | 100
| B1071.041 |  | B1071.041 | Exterior Wall - Type: Gypsum with wood studs, Full Height, Fixed Below, Fixed Above | 700 | 2170 | 3000 | Normal | 1956.6655 | 0.45861 | 1 | 4340 |  |  |  | 1302 | 0.45861 | 10 | Each (13'x100' Panel) | 2050 | 5550 | 8900 | Normal | 5499.9816 | 0.48592 | 1 | 11100 |  |  |  | 3330 | 0.48592 | 10 | Each (13'x100' Panel) | 18000 | 18800 | 22800 | LogNormal | 19762.5099 | 0.096878 | 1 | 37600 |  |  |  | 11280 | 0.096878 | 10 | Each (13'x100' Panel) | [30 empty] | 0.52 | 1.69 | 2.34 | Normal | 1.5167 | 0.52233 | 1 | 3.3813 |  |  |  | 1.0135 | 0.52233 | 10 | Each (13'x100' Panel) | 1.56 | 4.29 | 6.89 | Normal | 4.2467 | 0.54646 | 1 | 8.6157 |  |  |  | 2.5597 | 0.54646 | 10 | Each (13'x100' Panel) | 14.04 | 14.69 | 17.81 | LogNormal | 15.4311 | 0.26811 | 1 | 29.3429 |  |  |  | 8.8288 | 0.26811 | 10 | Each (13'x100' Panel) | [30 empty] | 1300
| B2011.001a |  | B2011.001a | Exterior Wall - Cold formed steel walls with wood structural panel sheathing, interior - gypsum board | 2100 | 3050 | 4666.6667 | LogNormal | 3098.1237 | 0.31697 | 6 | 3965 |  |  |  | 2440 | 0.31697 | 30 | 100 ft^2 Units | 2000 | 3500 | 5683.3333 | LogNormal | 3428.0432 | 0.39744 | 6 | 4200 |  |  |  | 2975 | 0.39744 | 30 | 100 ft^2 Units | 3466.6667 | 4500 | 4650 | Normal | 4205.5307 | 0.10978 | 6 | 5400 |  |  |  | 3825 | 0.10978 | 30 | 100 ft^2 Units | [30 empty] | 1.64 | 2.38 | 3.64 | LogNormal | 2.38 | 0.40369 | 6 | 3.0932 |  |  |  | 1.9046 | 0.40369 | 30 | 100 ft^2 Units | 1.56 | 2.73 | 4.43 | LogNormal | 2.73 | 0.46953 | 6 | 3.2756 |  |  |  | 2.3208 | 0.46953 | 30 | 100 ft^2 Units | 2.7 | 3.51 | 3.62 | Normal | 3.51 | 0.27304 | 6 | 4.2115 |  |  |  | 2.9839 | 0.27304 | 30 | 100 ft^2 Units | [30 empty] | 100
| B2011.001b |  | B2011.001b | Exterior Wall - Cold formed steel walls with wood structural panel sheathing, exterior - stucco one side | 1758.3333 | 2191.6667 | 2975 | LogNormal | 2252.332 | 0.21105 | 6 | 2849.1667 |  |  |  | 1753.3333 | 0.21105 | 30 | 100 ft^2 Units | 3408.3333 | 3825 | 6058.3333 | LogNormal | 4274.0968 | 0.25096 | 6 | 4590 |  |  |  | 3251.25 | 0.25096 | 30 | 100 ft^2 Units | 4591.6667 | 5375 | 5958.3333 | Normal | 5308.3306 | 0.10045 | 6 | 6450 |  |  |  | 4568.75 | 0.10045 | 30 | 100 ft^2 Units | [30 empty] | 1.37 | 1.71 | 2.32 | LogNormal | 1.71 | 0.32717 | 6 | 2.2225 |  |  |  | 1.3684 | 0.32717 | 30 | 100 ft^2 Units | 2.66 | 2.98 | 4.72 | LogNormal | 2.98 | 0.35424 | 6 | 3.5762 |  |  |  | 2.5328 | 0.35424 | 30 | 100 ft^2 Units | 3.58 | 4.19 | 4.64 | Normal | 4.19 | 0.26942 | 6 | 5.0279 |  |  |  | 3.5616 | 0.26942 | 30 | 100 ft^2 Units | [30 empty] | 100
| B2011.011a |  | B2011.011a | Exterior Wall - Cold formed steel walls with flat strap X-bracing, interior - gypsum board | 2325 | 3116.6667 | 4283.3333 | LogNormal | 3141.1303 | 0.24037 | 2 | 4051.6667 |  |  |  | 2493.3333 | 0.24037 | 6 | 100 ft^2 Units | 3258.3333 | 3775 | 4191.6667 | Normal | 3741.6648 | 0.097321 | 2 | 4530 |  |  |  | 3208.75 | 0.097321 | 6 | 100 ft^2 Units | [45 empty] | 1.81 | 2.43 | 3.34 | LogNormal | 2.43 | 0.34681 | 2 | 3.1587 |  |  |  | 1.9442 | 0.34681 | 6 | 100 ft^2 Units | 2.54 | 2.94 | 3.27 | Normal | 2.94 | 0.26827 | 2 | 3.5285 |  |  |  | 2.4987 | 0.26827 | 6 | 100 ft^2 Units | [45 empty] | 100
| B2011.011b |  | B2011.011b | Exterior Wall - Cold formed steel walls with flat strap X-bracing, exterior - stucco one side | 2783.3333 | 3075 | 4441.6667 | LogNormal | 3357.07 | 0.19902 | 3 | 3997.5 |  |  |  | 2460 | 0.19902 | 8 | 100 ft^2 Units | 4633.3333 | 4916.6667 | 6350 | LogNormal | 5248.8852 | 0.13115 | 3 | 5900 |  |  |  | 4179.1667 | 0.13115 | 8 | 100 ft^2 Units | [45 empty] | 2.17 | 2.4 | 3.46 | LogNormal | 2.4 | 0.31954 | 3 | 3.119 |  |  |  | 1.9207 | 0.31954 | 8 | 100 ft^2 Units | 3.61 | 3.83 | 4.95 | LogNormal | 3.83 | 0.28231 | 3 | 4.5964 |  |  |  | 3.2552 | 0.28231 | 8 | 100 ft^2 Units | [45 empty] | 100
| B2011.021a |  | B2011.021a | Exterior Wall - Cold formed steel walls with 22 or 31 mil steel sheathing, interior - gypsum board | 2100 | 3050 | 4666.6667 | LogNormal | 3098.1237 | 0.31697 | 4 | 3965 |  |  |  | 2440 | 0.31697 | 11 | 100 ft^2 Units | 2450 | 4150 | 6133.3333 | Normal | 4244.455 | 0.33857 | 4 | 4980 |  |  |  | 3527.5 | 0.33857 | 11 | 100 ft^2 Units | [45 empty] | 1.64 | 2.38 | 3.64 | LogNormal | 2.38 | 0.40369 | 4 | 3.0932 |  |  |  | 1.9046 | 0.40369 | 11 | 100 ft^2 Units | 1.91 | 3.23 | 4.78 | Normal | 3.23 | 0.42087 | 4 | 3.8769 |  |  |  | 2.7448 | 0.42087 | 11 | 100 ft^2 Units | [45 empty] | 100
| B2011.021b |  | B2011.021b | Exterior Wall - Cold formed steel walls with 22 or 31 mil steel sheathing, exterior - stucco one side | 1891.6667 | 2308.3333 | 3658.3333 | LogNormal | 2506.2097 | 0.28026 | 2 | 3000.8333 |  |  |  | 1846.6667 | 0.28026 | 6 | 100 ft^2 Units | 4091.6667 | 4775 | 6225 | LogNormal | 4950.6944 | 0.16982 | 2 | 5730 |  |  |  | 4058.75 | 0.16982 | 6 | 100 ft^2 Units | [45 empty] | 1.47 | 1.8 | 2.85 | LogNormal | 1.8 | 0.37556 | 2 | 2.3397 |  |  |  | 1.4402 | 0.37556 | 6 | 100 ft^2 Units | 3.19 | 3.72 | 4.85 | LogNormal | 3.72 | 0.30222 | 2 | 4.4643 |  |  |  | 3.1617 | 0.30222 | 6 | 100 ft^2 Units | [45 empty] | 100
| B2011.101 |  | B2011.101 | Exterior Wall - Light framed wood walls with structural panel sheathing, gypsum wallboard no hold-downs | 1766.6667 | 2300 | 3333.3333 | LogNormal | 2378.6919 | 0.25663 | 3 | 2990 |  |  |  | 1840 | 0.25663 | 8 | 100 ft^2 Units | 1666.6667 | 2750 | 4350 | LogNormal | 2717.0542 | 0.36907 | 3 | 3300 |  |  |  | 2337.5 | 0.36907 | 8 | 100 ft^2 Units | 3466.6667 | 4500 | 4650 | Normal | 4205.5307 | 0.10978 | 3 | 5400 |  |  |  | 3825 | 0.10978 | 8 | 100 ft^2 Units | [30 empty] | 1.38 | 1.79 | 2.6 | LogNormal | 1.79 | 0.35828 | 3 | 2.3278 |  |  |  | 1.4315 | 0.35828 | 8 | 100 ft^2 Units | 1.3 | 2.14 | 3.39 | LogNormal | 2.14 | 0.44577 | 3 | 2.5687 |  |  |  | 1.8185 | 0.44577 | 8 | 100 ft^2 Units | 2.7 | 3.51 | 3.62 | Normal | 3.51 | 0.27304 | 3 | 4.2115 |  |  |  | 2.9839 | 0.27304 | 8 | 100 ft^2 Units | [30 empty] | 100
| B2011.102 |  | B2011.102 | Exterior Wall - Light framed wood walls with structural panel sheathing, stucco, hold-downs | 1375 | 1641.6667 | 2191.6667 | LogNormal | 1702.1648 | 0.18873 | 4 | 2134.1667 |  |  |  | 1313.3333 | 0.18873 | 11 | 100 ft^2 Units | 1708.3333 | 2141.6667 | 2925 | LogNormal | 2201.0716 | 0.21585 | 4 | 2570 |  |  |  | 1820.4167 | 0.21585 | 11 | 100 ft^2 Units | 4266.6667 | 4800 | 5700 | LogNormal | 4886.4349 | 0.11505 | 4 | 5760 |  |  |  | 4080 | 0.11505 | 11 | 100 ft^2 Units | [30 empty] | 1.07 | 1.28 | 1.71 | LogNormal | 1.28 | 0.31324 | 4 | 1.6639 |  |  |  | 1.0241 | 0.31324 | 11 | 100 ft^2 Units | 1.33 | 1.67 | 2.28 | LogNormal | 1.67 | 0.33029 | 4 | 2.0038 |  |  |  | 1.4196 | 0.33029 | 11 | 100 ft^2 Units | 3.33 | 3.74 | 4.44 | LogNormal | 3.74 | 0.2752 | 4 | 4.4882 |  |  |  | 3.1788 | 0.2752 | 11 | 100 ft^2 Units | [30 empty] | 100
| B2011.111 |  | B2011.111 | Exterior Wall - Light framed wood walls with structural panel sheathing, stucco no hold-downs | 1766.6667 | 2300 | 3333.3333 | LogNormal | 2378.6919 | 0.25663 | 2 | 2990 |  |  |  | 1840 | 0.25663 | 6 | 100 ft^2 Units | 1666.6667 | 2750 | 4350 | LogNormal | 2717.0542 | 0.36907 | 2 | 3300 |  |  |  | 2337.5 | 0.36907 | 6 | 100 ft^2 Units | 3466.6667 | 4500 | 4650 | Normal | 4205.5307 | 0.10978 | 2 | 5400 |  |  |  | 3825 | 0.10978 | 6 | 100 ft^2 Units | [30 empty] | 1.38 | 1.79 | 2.6 | LogNormal | 1.79 | 0.35828 | 2 | 2.3278 |  |  |  | 1.4315 | 0.35828 | 6 | 100 ft^2 Units | 1.3 | 2.14 | 3.39 | LogNormal | 2.14 | 0.44577 | 2 | 2.5687 |  |  |  | 1.8185 | 0.44577 | 6 | 100 ft^2 Units | 2.7 | 3.51 | 3.62 | Normal | 3.51 | 0.27304 | 2 | 4.2115 |  |  |  | 2.9839 | 0.27304 | 6 | 100 ft^2 Units | [30 empty] | 100
| B2011.121 |  | B2011.121 | Exterior Wall - Light framed wood walls with structural panel sheathing, gypsum wallboard and hold-downs | 1375 | 1641.6667 | 2191.6667 | LogNormal | 1702.1648 | 0.18873 | 3 | 2134.1667 |  |  |  | 1313.3333 | 0.18873 | 8 | 100 ft^2 Units | 1708.3333 | 2141.6667 | 2925 | LogNormal | 2201.0716 | 0.21585 | 3 | 2570 |  |  |  | 1820.4167 | 0.21585 | 8 | 100 ft^2 Units | 5191.6667 | 5375 | 6308.3333 | LogNormal | 5605.3301 | 0.079218 | 3 | 6450 |  |  |  | 4568.75 | 0.079218 | 8 | 100 ft^2 Units | [30 empty] | 1.07 | 1.28 | 1.71 | LogNormal | 1.28 | 0.31324 | 3 | 1.6639 |  |  |  | 1.0241 | 0.31324 | 8 | 100 ft^2 Units | 1.33 | 1.67 | 2.28 | LogNormal | 1.67 | 0.33029 | 3 | 2.0038 |  |  |  | 1.4196 | 0.33029 | 8 | 100 ft^2 Units | 4.05 | 4.19 | 4.92 | LogNormal | 4.19 | 0.26225 | 3 | 5.0279 |  |  |  | 3.5616 | 0.26225 | 8 | 100 ft^2 Units | [30 empty] | 100
| B2011.131 |  | B2011.131 | Exterior Wall - Wood walls with diagonal let-in bracing | 4011.8056 | 4741.6667 | 5274.3056 | Normal | 4675.9236 | 0.10534 | 4 | 6164.1667 |  |  |  | 3793.3333 | 0.10534 | 11 | 100 ft^2 Units | [60 empty] | 3.13 | 3.7 | 4.11 | Normal | 3.7 | 0.27129 | 4 | 4.8087 |  |  |  | 2.9609 | 0.27129 | 11 | 100 ft^2 Units | [60 empty] | 100
| B2011.201a |  | B2011.201a | Precast Concrete Panels 4.5 inches thick - in plane deformation | 8332 | 12671 | 14183 | Normal | 11728.6662 | 0.19463 | 2 | 16472.3 |  |  |  | 10136.8 | 0.19463 | 8 | 390 ft^2 Units | 41660 | 63355 | 70915 | Normal | 58643.3045 | 0.19463 | 2 | 82361.5 |  |  |  | 50684 | 0.19463 | 8 | 390 ft^2 Units | [45 empty] | 1.2246 | 1.8642 | 2.0826 | Normal | 1.7238 | 0.31683 | 2 | 2.4232 |  |  |  | 1.4915 | 0.31683 | 8 | 390 ft^2 Units | 6.123 | 9.321 | 10.413 | Normal | 8.619 | 0.31683 | 2 | 12.1161 |  |  |  | 7.4576 | 0.31683 | 8 | 390 ft^2 Units | [45 empty] | 390
| B2011.201b |  | B2011.201b | Precast Concrete Panels 4.5 inches thick - out of plane deformation | 41660 | 63355 | 70915 | Normal | 58643.3117 | 0.19463 | 2 | 82361.5 |  |  |  | 50684 | 0.19463 | 8 | 390 ft^2 Units | [60 empty] | 6.123 | 9.321 | 10.413 | Normal | 9.321 | 0.31683 | 2 | 12.1161 |  |  |  | 7.4576 | 0.31683 | 8 | 390 ft^2 Units | [60 empty] | 390
| B2022.001 |  | B2022.001 | Curtain Walls - Generic Midrise Stick-Built Curtain wall, Config: Monolithic, Lamination: Unknown, Glass Type: Unknown, Details: Aspect ratio = 6:5, Other details Unknown | 1370 | 1370 | 2000 | LogNormal | 1554.814 | 0.1668 | 20 | 2055 |  |  |  | 1096 | 0.1668 | 100 | Each (5'x6' Panel) | 1370 | 1370 | 2000 | LogNormal | 1554.814 | 0.1668 | 20 | 2055 |  |  |  | 1096 | 0.1668 | 100 | Each (5'x6' Panel) | [45 empty] | 0.603 | 0.603 | 0.882 | LogNormal | 0.603 | 0.30054 | 20 | 0.90521 |  |  |  | 0.48212 | 0.30054 | 100 | Each (5'x6' Panel) | 0.603 | 0.603 | 0.882 | LogNormal | 0.603 | 0.30054 | 20 | 0.90521 |  |  |  | 0.48212 | 0.30054 | 100 | Each (5'x6' Panel) | [45 empty] | 30
| B2022.002 |  | B2022.002 | Curtain Walls - Generic Midrise Stick-Built Curtain wall, Config: Insulating Glass Units (dual pane), Lamination: Unknown, Glass Type: Unknown, Details: Aspect ratio = 6:5, Other details Unknown | 1970 | 1970 | 2600 | LogNormal | 2162.6019 | 0.1185 | 20 | 2955 |  |  |  | 1576 | 0.1185 | 100 | Each (5'x6' Panel) | 1970 | 1970 | 2600 | LogNormal | 2162.6019 | 0.1185 | 20 | 2955 |  |  |  | 1576 | 0.1185 | 100 | Each (5'x6' Panel) | [45 empty] | 0.87 | 0.87 | 1.146 | LogNormal | 0.87 | 0.27666 | 20 | 1.3046 |  |  |  | 0.69618 | 0.27666 | 100 | Each (5'x6' Panel) | 0.87 | 0.87 | 1.146 | LogNormal | 0.87 | 0.27666 | 20 | 1.3046 |  |  |  | 0.69618 | 0.27666 | 100 | Each (5'x6' Panel) | [45 empty] | 30
| B2022.011 |  | B2022.011 | Midrise stick-built curtain wall, Config: Asymmetric insulating glass units (dual-pane, unequal-thickness IGU), Lamination: Laminated, Glass Type: Annealed, Details: 1/4 in. (6 mm) inner AN / 1/2 in. (13 mm) outer AN LAM (0.030 PVB) IGU; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 6:5 sealant = dry | 1370 | 1370 | 2000 | LogNormal | 1554.814 | 0.1668 | 20 | 2055 |  |  |  | 1096 | 0.1668 | 100 | Each (5'x6' Panel) | 1970 | 1970 | 2600 | LogNormal | 2162.6019 | 0.1185 | 20 | 2955 |  |  |  | 1576 | 0.1185 | 100 | Each (5'x6' Panel) | 1970 | 1970 | 2600 | LogNormal | 2162.6019 | 0.1185 | 20 | 2364 |  |  |  | 1674.5 | 0.1185 | 100 | Each (5'x6' Panel) | [30 empty] | 0.603 | 0.603 | 0.882 | LogNormal | 0.603 | 0.30054 | 20 | 0.90521 |  |  |  | 0.48212 | 0.30054 | 100 | Each (5'x6' Panel) | 0.87 | 0.87 | 1.146 | LogNormal | 0.87 | 0.27666 | 20 | 1.3046 |  |  |  | 0.69618 | 0.27666 | 100 | Each (5'x6' Panel) | 0.87 | 0.87 | 1.146 | LogNormal | 0.87 | 0.27666 | 20 | 1.0438 |  |  |  | 0.73963 | 0.27666 | 100 | Each (5'x6' Panel) | [30 empty] | 30
| B2022.021 |  | B2022.021 | Midrise stick-built curtain wall, Config: Monolithic, Lamination: Laminated, Glass Type: Annealed, Details: 1/4 in. (6 mm) AN LAM (0.030 PVB); glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 6:5 sealant = dry | 1970 | 1970 | 2600 | LogNormal | 2162.6019 | 0.1185 | 20 | 2955 |  |  |  | 1576 | 0.1185 | 100 | Each (5'x6' Panel) | 1970 | 1970 | 2600 | LogNormal | 2162.6019 | 0.1185 | 20 | 2955 |  |  |  | 1576 | 0.1185 | 100 | Each (5'x6' Panel) | [45 empty] | 0.87 | 0.87 | 1.146 | LogNormal | 0.87 | 0.27666 | 20 | 1.3046 |  |  |  | 0.69618 | 0.27666 | 100 | Each (5'x6' Panel) | 0.87 | 0.87 | 1.146 | LogNormal | 0.87 | 0.27666 | 20 | 1.3046 |  |  |  | 0.69618 | 0.27666 | 100 | Each (5'x6' Panel) | [45 empty] | 30
| B2022.022 |  | B2022.022 | Midrise stick-built curtain wall, Config: Monolithic, Lamination: Laminated, Glass Type: Annealed, Details: 1/4 in. (6 mm) AN laminated, 2-sided SSG, Center Panel; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 6:5 sealant = wet | 1370 | 1370 | 2000 | LogNormal | 1554.814 | 0.1668 | 20 | 2055 |  |  |  | 1096 | 0.1668 | 100 | Each (5'x6' Panel) | 1370 | 1370 | 2000 | LogNormal | 1554.814 | 0.1668 | 20 | 2055 |  |  |  | 1096 | 0.1668 | 100 | Each (5'x6' Panel) | [45 empty] | 0.603 | 0.603 | 0.882 | LogNormal | 0.603 | 0.30054 | 20 | 0.90521 |  |  |  | 0.48212 | 0.30054 | 100 | Each (5'x6' Panel) | 0.603 | 0.603 | 0.882 | LogNormal | 0.603 | 0.30054 | 20 | 0.90521 |  |  |  | 0.48212 | 0.30054 | 100 | Each (5'x6' Panel) | [45 empty] | 30
| B2022.023 |  | B2022.023 | Midrise stick-built curtain wall, Config: Monolithic, Lamination: Laminated, Glass Type: Annealed, Details: 1/4 in. (6 mm) AN laminated, 2-sided SSG, Outside Panel; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 6:5 sealant = wet | 1370 | 1370 | 2000 | LogNormal | 1554.814 | 0.1668 | 20 | 2055 |  |  |  | 1096 | 0.1668 | 100 | Each (5'x6' Panel) | 1370 | 1370 | 2000 | LogNormal | 1554.814 | 0.1668 | 20 | 2055 |  |  |  | 1096 | 0.1668 | 100 | Each (5'x6' Panel) | [45 empty] | 0.603 | 0.603 | 0.882 | LogNormal | 0.603 | 0.30054 | 20 | 0.90521 |  |  |  | 0.48212 | 0.30054 | 100 | Each (5'x6' Panel) | 0.603 | 0.603 | 0.882 | LogNormal | 0.603 | 0.30054 | 20 | 0.90521 |  |  |  | 0.48212 | 0.30054 | 100 | Each (5'x6' Panel) | [45 empty] | 30
| B2022.031 |  | B2022.031 | Midrise stick-built curtain wall, Config: Monolithic, Lamination: Not laminated, Glass Type: Annealed, Details: 1/4 in. (6 mm) AN monolithic; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 6:5 sealant = dry | 1370 | 1370 | 2000 | LogNormal | 1554.814 | 0.1668 | 20 | 2055 |  |  |  | 1096 | 0.1668 | 100 | Each (5'x6' Panel) | 1370 | 1370 | 2000 | LogNormal | 1554.814 | 0.1668 | 20 | 2055 |  |  |  | 1096 | 0.1668 | 100 | Each (5'x6' Panel) | [45 empty] | 0.603 | 0.603 | 0.882 | LogNormal | 0.603 | 0.30054 | 20 | 0.90521 |  |  |  | 0.48212 | 0.30054 | 100 | Each (5'x6' Panel) | 0.603 | 0.603 | 0.882 | LogNormal | 0.603 | 0.30054 | 20 | 0.90521 |  |  |  | 0.48212 | 0.30054 | 100 | Each (5'x6' Panel) | [45 empty] | 30
| B2022.032 |  | B2022.032 | Midrise stick-built curtain wall, Config: Monolithic, Lamination: Not laminated, Glass Type: Annealed, Details: 1/4 in. (6 mm) AN monolithic; glass-frame clearance = 0 in. (0 mm); aspect ratio = 6:5 sealant = dry | 1370 | 1370 | 2000 | LogNormal | 1554.814 | 0.1668 | 20 | 2055 |  |  |  | 1096 | 0.1668 | 100 | Each (5'x6' Panel) | 1370 | 1370 | 2000 | LogNormal | 1554.814 | 0.1668 | 20 | 2055 |  |  |  | 1096 | 0.1668 | 100 | Each (5'x6' Panel) | [45 empty] | 0.603 | 0.603 | 0.882 | LogNormal | 0.603 | 0.30054 | 20 | 0.90521 |  |  |  | 0.48212 | 0.30054 | 100 | Each (5'x6' Panel) | 0.603 | 0.603 | 0.882 | LogNormal | 0.603 | 0.30054 | 20 | 0.90521 |  |  |  | 0.48212 | 0.30054 | 100 | Each (5'x6' Panel) | [45 empty] | 30
| B2022.033 |  | B2022.033 | Midrise stick-built curtain wall, Config: Monolithic, Lamination: Not laminated, Glass Type: Annealed, Details: 1/4 in. (6 mm) AN monolithic; glass-frame clearance = 0.13 in. (3 mm); aspect ratio = 6:5 sealant = dry | 1970 | 1970 | 2600 | LogNormal | 2162.6019 | 0.1185 | 20 | 2955 |  |  |  | 1576 | 0.1185 | 100 | Each (5'x6' Panel) | 1970 | 1970 | 2600 | LogNormal | 2162.6019 | 0.1185 | 20 | 2955 |  |  |  | 1576 | 0.1185 | 100 | Each (5'x6' Panel) | [45 empty] | 0.87 | 0.87 | 1.146 | LogNormal | 0.87 | 0.27666 | 20 | 1.3046 |  |  |  | 0.69618 | 0.27666 | 100 | Each (5'x6' Panel) | 0.87 | 0.87 | 1.146 | LogNormal | 0.87 | 0.27666 | 20 | 1.3046 |  |  |  | 0.69618 | 0.27666 | 100 | Each (5'x6' Panel) | [45 empty] | 30
| B2022.034 |  | B2022.034 | Midrise stick-built curtain wall, Config: Monolithic, Lamination: Not laminated, Glass Type: Annealed, Details: 1/4 in. (6 mm) AN monolithic; glass-frame clearance = 0.25 in. (6 mm); aspect ratio = 6:5 sealant = dry | 1970 | 1970 | 2600 | LogNormal | 2162.6019 | 0.1185 | 20 | 2955 |  |  |  | 1576 | 0.1185 | 100 | Each (5'x6' Panel) | 1970 | 1970 | 2600 | LogNormal | 2162.6019 | 0.1185 | 20 | 2955 |  |  |  | 1576 | 0.1185 | 100 | Each (5'x6' Panel) | [45 empty] | 0.87 | 0.87 | 1.146 | LogNormal | 0.87 | 0.27666 | 20 | 1.3046 |  |  |  | 0.69618 | 0.27666 | 100 | Each (5'x6' Panel) | 0.87 | 0.87 | 1.146 | LogNormal | 0.87 | 0.27666 | 20 | 1.3046 |  |  |  | 0.69618 | 0.27666 | 100 | Each (5'x6' Panel) | [45 empty] | 30
| B2022.035 |  | B2022.035 | Midrise stick-built curtain wall, Config: Monolithic, Lamination: Not laminated, Glass Type: Annealed, Details: 1/4 in. (6 mm) AN monolithic; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 2:1 sealant = dry | 3152 | 3152 | 4160 | LogNormal | 3460.1608 | 0.1185 | 13 | 4728 |  |  |  | 2521.6 | 0.1185 | 63 | Each (4'x8' Panel) | 3152 | 3152 | 4160 | LogNormal | 3460.1608 | 0.1185 | 13 | 4728 |  |  |  | 2521.6 | 0.1185 | 63 | Each (4'x8' Panel) | [45 empty] | 1.392 | 1.392 | 1.8336 | LogNormal | 1.392 | 0.27666 | 13 | 2.0873 |  |  |  | 1.1139 | 0.27666 | 63 | Each (4'x8' Panel) | 1.392 | 1.392 | 1.8336 | LogNormal | 1.392 | 0.27666 | 13 | 2.0873 |  |  |  | 1.1139 | 0.27666 | 63 | Each (4'x8' Panel) | [45 empty] | 48
| B2022.036 |  | B2022.036 | Midrise stick-built curtain wall, Config: Monolithic, Lamination: Not laminated, Glass Type: Annealed, Details: 1/4 in. (6 mm) AN monolithic; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 1:2 sealant = dry | 3152 | 3152 | 4160 | LogNormal | 3460.1608 | 0.1185 | 13 | 4728 |  |  |  | 2521.6 | 0.1185 | 63 | Each (4'x8' Panel) | 3152 | 3152 | 4160 | LogNormal | 3460.1608 | 0.1185 | 13 | 4728 |  |  |  | 2521.6 | 0.1185 | 63 | Each (4'x8' Panel) | [45 empty] | 1.392 | 1.392 | 1.8336 | LogNormal | 1.392 | 0.27666 | 13 | 2.0873 |  |  |  | 1.1139 | 0.27666 | 63 | Each (4'x8' Panel) | 1.392 | 1.392 | 1.8336 | LogNormal | 1.392 | 0.27666 | 13 | 2.0873 |  |  |  | 1.1139 | 0.27666 | 63 | Each (4'x8' Panel) | [45 empty] | 48
| B2022.037 |  | B2022.037 | Midrise stick-built curtain wall, Config: Monolithic, Lamination: Not laminated, Glass Type: Annealed, Details: 1/4 in. (6 mm) AN monolithic, 2-sided SSG, Center Panel; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 6:5 sealant = wet | 1970 | 1970 | 2600 | LogNormal | 2162.6019 | 0.1185 | 20 | 2955 |  |  |  | 1576 | 0.1185 | 100 | Each (5'x6' Panel) | 1970 | 1970 | 2600 | LogNormal | 2162.6019 | 0.1185 | 20 | 2955 |  |  |  | 1576 | 0.1185 | 100 | Each (5'x6' Panel) | [45 empty] | 0.87 | 0.87 | 1.146 | LogNormal | 0.87 | 0.27666 | 20 | 1.3046 |  |  |  | 0.69618 | 0.27666 | 100 | Each (5'x6' Panel) | 0.87 | 0.87 | 1.146 | LogNormal | 0.87 | 0.27666 | 20 | 1.3046 |  |  |  | 0.69618 | 0.27666 | 100 | Each (5'x6' Panel) | [45 empty] | 30
| B2022.038 |  | B2022.038 | Midrise stick-built curtain wall, Config: Monolithic, Lamination: Not laminated, Glass Type: Annealed, Details: 1/4 in. (6 mm) AN monolithic, 2-sided SSG, Outside Panel; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 6:5 sealant = wet | 1970 | 1970 | 2600 | LogNormal | 2162.6019 | 0.1185 | 20 | 2955 |  |  |  | 1576 | 0.1185 | 100 | Each (5'x6' Panel) | 1970 | 1970 | 2600 | LogNormal | 2162.6019 | 0.1185 | 20 | 2955 |  |  |  | 1576 | 0.1185 | 100 | Each (5'x6' Panel) | [45 empty] | 0.87 | 0.87 | 1.146 | LogNormal | 0.87 | 0.27666 | 20 | 1.3046 |  |  |  | 0.69618 | 0.27666 | 100 | Each (5'x6' Panel) | 0.87 | 0.87 | 1.146 | LogNormal | 0.87 | 0.27666 | 20 | 1.3046 |  |  |  | 0.69618 | 0.27666 | 100 | Each (5'x6' Panel) | [45 empty] | 30
| B2022.039 |  | B2022.039 | Midrise stick-built curtain wall, Config: Monolithic, Lamination: Not laminated, Glass Type: Annealed, Details: 1/4 in. (6 mm) AN monolithic; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 6:5 sealant = dry | 1970 | 1970 | 2600 | LogNormal | 2162.6019 | 0.1185 | 20 | 2955 |  |  |  | 1576 | 0.1185 | 100 | Each (5'x6' Panel) | 1970 | 1970 | 2600 | LogNormal | 2162.6019 | 0.1185 | 20 | 2955 |  |  |  | 1576 | 0.1185 | 100 | Each (5'x6' Panel) | [45 empty] | 0.87 | 0.87 | 1.146 | LogNormal | 0.87 | 0.27666 | 20 | 1.3046 |  |  |  | 0.69618 | 0.27666 | 100 | Each (5'x6' Panel) | 0.87 | 0.87 | 1.146 | LogNormal | 0.87 | 0.27666 | 20 | 1.3046 |  |  |  | 0.69618 | 0.27666 | 100 | Each (5'x6' Panel) | [45 empty] | 30
| B2022.040 |  | B2022.040 | Midrise stick-built curtain wall, Config: Monolithic, Lamination: Not laminated, Glass Type: Annealed, Details: 1/4 in. (6 mm) AN monolithic; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 2:1 sealant = dry | 1970 | 1970 | 2600 | LogNormal | 2162.6019 | 0.1185 | 20 | 2955 |  |  |  | 1576 | 0.1185 | 100 | Each (5'x6' Panel) | 1970 | 1970 | 2600 | LogNormal | 2162.6019 | 0.1185 | 20 | 2955 |  |  |  | 1576 | 0.1185 | 100 | Each (5'x6' Panel) | [45 empty] | 0.87 | 0.87 | 1.146 | LogNormal | 0.87 | 0.27666 | 20 | 1.3046 |  |  |  | 0.69618 | 0.27666 | 100 | Each (5'x6' Panel) | 0.87 | 0.87 | 1.146 | LogNormal | 0.87 | 0.27666 | 20 | 1.3046 |  |  |  | 0.69618 | 0.27666 | 100 | Each (5'x6' Panel) | [45 empty] | 30
| B2022.041 |  | B2022.041 | Midrise stick-built curtain wall, Config: Monolithic, Lamination: Not laminated, Glass Type: Annealed, Details: 1/4 in. (6 mm) AN monolithic; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 1:2 sealant = dry | 1970 | 1970 | 2600 | LogNormal | 2162.6019 | 0.1185 | 20 | 2955 |  |  |  | 1576 | 0.1185 | 100 | Each (5'x6' Panel) | 1970 | 1970 | 2600 | LogNormal | 2162.6019 | 0.1185 | 20 | 2955 |  |  |  | 1576 | 0.1185 | 100 | Each (5'x6' Panel) | [45 empty] | 0.87 | 0.87 | 1.146 | LogNormal | 0.87 | 0.27666 | 20 | 1.3046 |  |  |  | 0.69618 | 0.27666 | 100 | Each (5'x6' Panel) | 0.87 | 0.87 | 1.146 | LogNormal | 0.87 | 0.27666 | 20 | 1.3046 |  |  |  | 0.69618 | 0.27666 | 100 | Each (5'x6' Panel) | [45 empty] | 30
| B2022.051 |  | B2022.051 | Midrise stick-built curtain wall, Config: Monolithic, Lamination: Not laminated, Glass Type: Full tempered, Details: 1/4 in. (6 mm) FT monolithic, 2-sided SSG, Center Panel; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 6:5 sealant = wet | 1970 | 1970 | 2600 | LogNormal | 2162.6019 | 0.1185 | 20 | 2955 |  |  |  | 1576 | 0.1185 | 100 | Each (5'x6' Panel) | 1970 | 1970 | 2600 | LogNormal | 2162.6019 | 0.1185 | 20 | 2955 |  |  |  | 1576 | 0.1185 | 100 | Each (5'x6' Panel) | [45 empty] | 0.87 | 0.87 | 1.146 | LogNormal | 0.87 | 0.27666 | 20 | 1.3046 |  |  |  | 0.69618 | 0.27666 | 100 | Each (5'x6' Panel) | 0.87 | 0.87 | 1.146 | LogNormal | 0.87 | 0.27666 | 20 | 1.3046 |  |  |  | 0.69618 | 0.27666 | 100 | Each (5'x6' Panel) | [45 empty] | 30
| B2022.052 |  | B2022.052 | Midrise stick-built curtain wall, Config: Monolithic, Lamination: Not laminated, Glass Type: Full tempered, Details: 1/4 in. (6 mm) FT monolithic, 2-sided SSG, Outside Panel; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 6:5 sealant = wet | 1970 | 1970 | 2600 | LogNormal | 2162.6019 | 0.1185 | 20 | 2955 |  |  |  | 1576 | 0.1185 | 100 | Each (5'x6' Panel) | 1970 | 1970 | 2600 | LogNormal | 2162.6019 | 0.1185 | 20 | 2955 |  |  |  | 1576 | 0.1185 | 100 | Each (5'x6' Panel) | [45 empty] | 0.87 | 0.87 | 1.146 | LogNormal | 0.87 | 0.27666 | 20 | 1.3046 |  |  |  | 0.69618 | 0.27666 | 100 | Each (5'x6' Panel) | 0.87 | 0.87 | 1.146 | LogNormal | 0.87 | 0.27666 | 20 | 1.3046 |  |  |  | 0.69618 | 0.27666 | 100 | Each (5'x6' Panel) | [45 empty] | 30
| B2022.053 |  | B2022.053 | Midrise stick-built curtain wall, Config: Monolithic, Lamination: Not laminated, Glass Type: Full tempered, Details: 1/4 in. (6 mm) FT monolithic, Seamed Edge; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 6:5 sealant = dry | 1970 | 1970 | 2600 | LogNormal | 2162.6019 | 0.1185 | 20 | 2955 |  |  |  | 1576 | 0.1185 | 100 | Each (5'x6' Panel) | 1970 | 1970 | 2600 | LogNormal | 2162.6019 | 0.1185 | 20 | 2955 |  |  |  | 1576 | 0.1185 | 100 | Each (5'x6' Panel) | [45 empty] | 0.87 | 0.87 | 1.146 | LogNormal | 0.87 | 0.27666 | 20 | 1.3046 |  |  |  | 0.69618 | 0.27666 | 100 | Each (5'x6' Panel) | 0.87 | 0.87 | 1.146 | LogNormal | 0.87 | 0.27666 | 20 | 1.3046 |  |  |  | 0.69618 | 0.27666 | 100 | Each (5'x6' Panel) | [45 empty] | 30
| B2022.054 |  | B2022.054 | Midrise stick-built curtain wall, Config: Monolithic, Lamination: Not laminated, Glass Type: Full tempered, Details: 1/4 in. (6 mm) FT monolithic, Polished Edge; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 6:5 sealant = dry | 1970 | 1970 | 2600 | LogNormal | 2162.6019 | 0.1185 | 20 | 2955 |  |  |  | 1576 | 0.1185 | 100 | Each (5'x6' Panel) | 1970 | 1970 | 2600 | LogNormal | 2162.6019 | 0.1185 | 20 | 2955 |  |  |  | 1576 | 0.1185 | 100 | Each (5'x6' Panel) | [45 empty] | 0.87 | 0.87 | 1.146 | LogNormal | 0.87 | 0.27666 | 20 | 1.3046 |  |  |  | 0.69618 | 0.27666 | 100 | Each (5'x6' Panel) | 0.87 | 0.87 | 1.146 | LogNormal | 0.87 | 0.27666 | 20 | 1.3046 |  |  |  | 0.69618 | 0.27666 | 100 | Each (5'x6' Panel) | [45 empty] | 30
| B2022.061 |  | B2022.061 | Midrise stick-built curtain wall, Config: Monolithic, Lamination: Not laminated, Glass Type: Heat strengthened, Details: 1/4 in. (6 mm) HS monolithic; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 6:5 sealant = dry | 1970 | 1970 | 2600 | LogNormal | 2162.6019 | 0.1185 | 20 | 2955 |  |  |  | 1576 | 0.1185 | 100 | Each (5'x6' Panel) | 1970 | 1970 | 2600 | LogNormal | 2162.6019 | 0.1185 | 20 | 2955 |  |  |  | 1576 | 0.1185 | 100 | Each (5'x6' Panel) | [45 empty] | 0.87 | 0.87 | 1.146 | LogNormal | 0.87 | 0.27666 | 20 | 1.3046 |  |  |  | 0.69618 | 0.27666 | 100 | Each (5'x6' Panel) | 0.87 | 0.87 | 1.146 | LogNormal | 0.87 | 0.27666 | 20 | 1.3046 |  |  |  | 0.69618 | 0.27666 | 100 | Each (5'x6' Panel) | [45 empty] | 30
| B2022.071 |  | B2022.071 | Midrise stick-built curtain wall, Config: Symmetric insulating glass units (dual-pane, equal-thickness IGU), Lamination: Laminated, Glass Type: Annealed, Details: 1/4 in. (6 mm) inner AN / 1/4 in. (6 mm) outer AN LAM (0.030 PVB) IGU; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 6:5 sealant = dry | 1370 | 1370 | 2000 | LogNormal | 1554.814 | 0.1668 | 20 | 2055 |  |  |  | 1096 | 0.1668 | 100 | Each (5'x6' Panel) | 1970 | 1970 | 2600 | LogNormal | 2162.6019 | 0.1185 | 20 | 2955 |  |  |  | 1576 | 0.1185 | 100 | Each (5'x6' Panel) | 1970 | 1970 | 2600 | LogNormal | 2162.6019 | 0.1185 | 20 | 2364 |  |  |  | 1674.5 | 0.1185 | 100 | Each (5'x6' Panel) | [30 empty] | 0.603 | 0.603 | 0.882 | LogNormal | 0.603 | 0.30054 | 20 | 0.90521 |  |  |  | 0.48212 | 0.30054 | 100 | Each (5'x6' Panel) | 0.87 | 0.87 | 1.146 | LogNormal | 0.87 | 0.27666 | 20 | 1.3046 |  |  |  | 0.69618 | 0.27666 | 100 | Each (5'x6' Panel) | 0.87 | 0.87 | 1.146 | LogNormal | 0.87 | 0.27666 | 20 | 1.0438 |  |  |  | 0.73963 | 0.27666 | 100 | Each (5'x6' Panel) | [30 empty] | 30
| B2022.072 |  | B2022.072 | Midrise stick-built curtain wall, Config: Symmetric insulating glass units (dual-pane, equal-thickness IGU), Lamination: Laminated, Glass Type: Annealed, Details: 1/4 in. (6 mm) inner AN / 1/4 in. (6 mm) outer AN LAM (0.060 PVB) IGU; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 6:5 sealant = dry | 1370 | 1370 | 2000 | LogNormal | 1554.814 | 0.1668 | 20 | 2055 |  |  |  | 1096 | 0.1668 | 100 | Each (5'x6' Panel) | 1970 | 1970 | 2600 | LogNormal | 2162.6019 | 0.1185 | 20 | 2955 |  |  |  | 1576 | 0.1185 | 100 | Each (5'x6' Panel) | 1970 | 1970 | 2600 | LogNormal | 2162.6019 | 0.1185 | 20 | 2364 |  |  |  | 1674.5 | 0.1185 | 100 | Each (5'x6' Panel) | [30 empty] | 0.603 | 0.603 | 0.882 | LogNormal | 0.603 | 0.30054 | 20 | 0.90521 |  |  |  | 0.48212 | 0.30054 | 100 | Each (5'x6' Panel) | 0.87 | 0.87 | 1.146 | LogNormal | 0.87 | 0.27666 | 20 | 1.3046 |  |  |  | 0.69618 | 0.27666 | 100 | Each (5'x6' Panel) | 0.87 | 0.87 | 1.146 | LogNormal | 0.87 | 0.27666 | 20 | 1.0438 |  |  |  | 0.73963 | 0.27666 | 100 | Each (5'x6' Panel) | [30 empty] | 30
| B2022.081 |  | B2022.081 | Midrise stick-built curtain wall, Config: Symmetric insulating glass units (dual-pane, equal-thickness IGU), Lamination: Not laminated, Glass Type: Annealed, Details: 1 in. (25 mm) AN insulating glass unit (IGU) [1/4 in. (6 mm) inner and outer panes]; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 6:5 sealant = dry | 1970 | 1970 | 2600 | LogNormal | 2162.6019 | 0.1185 | 20 | 2955 |  |  |  | 1576 | 0.1185 | 100 | Each (5'x6' Panel) | 1970 | 1970 | 2600 | LogNormal | 2162.6019 | 0.1185 | 20 | 2955 |  |  |  | 1576 | 0.1185 | 100 | Each (5'x6' Panel) | [45 empty] | 0.87 | 0.87 | 1.146 | LogNormal | 0.87 | 0.27666 | 20 | 1.3046 |  |  |  | 0.69618 | 0.27666 | 100 | Each (5'x6' Panel) | 0.87 | 0.87 | 1.146 | LogNormal | 0.87 | 0.27666 | 20 | 1.3046 |  |  |  | 0.69618 | 0.27666 | 100 | Each (5'x6' Panel) | [45 empty] | 30
| B2022.082 |  | B2022.082 | Midrise stick-built curtain wall, Config: Symmetric insulating glass units (dual-pane, equal-thickness IGU), Lamination: Not laminated, Glass Type: Annealed, Details: 1 in. (25 mm) AN IGU [1/4 in. (6 mm) inner and outer panes]; glass-frame clearance = 0.25 in. (6 mm); aspect ratio = 6:5 sealant = dry | 1970 | 1970 | 2600 | LogNormal | 2162.6019 | 0.1185 | 20 | 2955 |  |  |  | 1576 | 0.1185 | 100 | Each (5'x6' Panel) | 1970 | 1970 | 2600 | LogNormal | 2162.6019 | 0.1185 | 20 | 2955 |  |  |  | 1576 | 0.1185 | 100 | Each (5'x6' Panel) | [45 empty] | 0.87 | 0.87 | 1.146 | LogNormal | 0.87 | 0.27666 | 20 | 1.3046 |  |  |  | 0.69618 | 0.27666 | 100 | Each (5'x6' Panel) | 0.87 | 0.87 | 1.146 | LogNormal | 0.87 | 0.27666 | 20 | 1.3046 |  |  |  | 0.69618 | 0.27666 | 100 | Each (5'x6' Panel) | [45 empty] | 30
| B2022.083 |  | B2022.083 | Midrise stick-built curtain wall, Config: Symmetric insulating glass units (dual-pane, equal-thickness IGU), Lamination: Not laminated, Glass Type: Annealed, Details: 1 in. (25 mm) AN IGU [1/4 in. (6 mm) inner and outer panes], 2-sided SSG, Center Panel; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 6:5 sealant = wet | 1370 | 1370 | 2000 | LogNormal | 1554.814 | 0.1668 | 20 | 2055 |  |  |  | 1096 | 0.1668 | 100 | Each (5'x6' Panel) | 1970 | 1970 | 2600 | LogNormal | 2162.6019 | 0.1185 | 20 | 2955 |  |  |  | 1576 | 0.1185 | 100 | Each (5'x6' Panel) | 1970 | 1970 | 2600 | LogNormal | 2162.6019 | 0.1185 | 20 | 2364 |  |  |  | 1674.5 | 0.1185 | 100 | Each (5'x6' Panel) | [30 empty] | 0.603 | 0.603 | 0.882 | LogNormal | 0.603 | 0.30054 | 20 | 0.90521 |  |  |  | 0.48212 | 0.30054 | 100 | Each (5'x6' Panel) | 0.87 | 0.87 | 1.146 | LogNormal | 0.87 | 0.27666 | 20 | 1.3046 |  |  |  | 0.69618 | 0.27666 | 100 | Each (5'x6' Panel) | 0.87 | 0.87 | 1.146 | LogNormal | 0.87 | 0.27666 | 20 | 1.0438 |  |  |  | 0.73963 | 0.27666 | 100 | Each (5'x6' Panel) | [30 empty] | 30
| B2022.084 |  | B2022.084 | Midrise stick-built curtain wall, Config: Symmetric insulating glass units (dual-pane, equal-thickness IGU), Lamination: Not laminated, Glass Type: Annealed, Details: 1 in. (25 mm) AN IGU [1/4 in. (6 mm) inner and outer panes], 2-sided SSG, Outside Panel; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 6:5 sealant = wet | 1370 | 1370 | 2000 | LogNormal | 1554.814 | 0.1668 | 20 | 2055 |  |  |  | 1096 | 0.1668 | 100 | Each (5'x6' Panel) | 1970 | 1970 | 2600 | LogNormal | 2162.6019 | 0.1185 | 20 | 2955 |  |  |  | 1576 | 0.1185 | 100 | Each (5'x6' Panel) | 1970 | 1970 | 2600 | LogNormal | 2162.6019 | 0.1185 | 20 | 2364 |  |  |  | 1674.5 | 0.1185 | 100 | Each (5'x6' Panel) | [30 empty] | 0.603 | 0.603 | 0.882 | LogNormal | 0.603 | 0.30054 | 20 | 0.90521 |  |  |  | 0.48212 | 0.30054 | 100 | Each (5'x6' Panel) | 0.87 | 0.87 | 1.146 | LogNormal | 0.87 | 0.27666 | 20 | 1.3046 |  |  |  | 0.69618 | 0.27666 | 100 | Each (5'x6' Panel) | 0.87 | 0.87 | 1.146 | LogNormal | 0.87 | 0.27666 | 20 | 1.0438 |  |  |  | 0.73963 | 0.27666 | 100 | Each (5'x6' Panel) | [30 empty] | 30
| B2022.091 |  | B2022.091 | Midrise stick-built curtain wall, Config: Symmetric insulating glass units (dual-pane, equal-thickness IGU), Lamination: Not laminated, Glass Type: Full tempered, Details: 1 in. (25 mm) FT IGU [1/4 in. (6 mm) inner and outer panes]; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 6:5 sealant = dry | 1370 | 1370 | 2000 | LogNormal | 1554.814 | 0.1668 | 20 | 2055 |  |  |  | 1096 | 0.1668 | 100 | Each (5'x6' Panel) | 1970 | 1970 | 2600 | LogNormal | 2162.6019 | 0.1185 | 20 | 2955 |  |  |  | 1576 | 0.1185 | 100 | Each (5'x6' Panel) | 1970 | 1970 | 2600 | LogNormal | 2162.6019 | 0.1185 | 20 | 2364 |  |  |  | 1674.5 | 0.1185 | 100 | Each (5'x6' Panel) | [30 empty] | 0.603 | 0.603 | 0.882 | LogNormal | 0.603 | 0.30054 | 20 | 0.90521 |  |  |  | 0.48212 | 0.30054 | 100 | Each (5'x6' Panel) | 0.87 | 0.87 | 1.146 | LogNormal | 0.87 | 0.27666 | 20 | 1.3046 |  |  |  | 0.69618 | 0.27666 | 100 | Each (5'x6' Panel) | 0.87 | 0.87 | 1.146 | LogNormal | 0.87 | 0.27666 | 20 | 1.0438 |  |  |  | 0.73963 | 0.27666 | 100 | Each (5'x6' Panel) | [30 empty] | 30
| B2022.101 |  | B2022.101 | Midrise stick-built curtain wall, Config: Symmetric insulating glass units (dual-pane, equal-thickness IGU), Lamination: Not laminated, Glass Type: Heat strengthened, Details: 1 in. (25 mm) HS IGU [1/4 in. (6 mm) inner and outer panes]; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 6:5 sealant = dry | 1370 | 1370 | 2000 | LogNormal | 1554.814 | 0.1668 | 20 | 2055 |  |  |  | 1096 | 0.1668 | 100 | Each (5'x6' Panel) | 1970 | 1970 | 2600 | LogNormal | 2162.6019 | 0.1185 | 20 | 2955 |  |  |  | 1576 | 0.1185 | 100 | Each (5'x6' Panel) | 1970 | 1970 | 2600 | LogNormal | 2162.6019 | 0.1185 | 20 | 2364 |  |  |  | 1674.5 | 0.1185 | 100 | Each (5'x6' Panel) | [30 empty] | 0.603 | 0.603 | 0.882 | LogNormal | 0.603 | 0.30054 | 20 | 0.90521 |  |  |  | 0.48212 | 0.30054 | 100 | Each (5'x6' Panel) | 0.87 | 0.87 | 1.146 | LogNormal | 0.87 | 0.27666 | 20 | 1.3046 |  |  |  | 0.69618 | 0.27666 | 100 | Each (5'x6' Panel) | 0.87 | 0.87 | 1.146 | LogNormal | 0.87 | 0.27666 | 20 | 1.0438 |  |  |  | 0.73963 | 0.27666 | 100 | Each (5'x6' Panel) | [30 empty] | 30
| B2022.201 |  | B2022.201 | Curtain Walls - Unitized curtain wall (also generic unitized curtain wall), Config: Symmetric insulating glass units (dual-pane, equal-thickness IGU), Lamination: Not laminated, Glass Type: Full tempered, Details: 1-1/4 in. (32 mm) FT IGU [1/4 in. (6 mm) inner and outer panes], 4-sided SSG, VHBTM SGTTM; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = Varies sealant = wet | 1370 | 1370 | 2000 | LogNormal | 1554.814 | 0.1668 | 20 | 2055 |  |  |  | 1096 | 0.1668 | 100 | Each (5'x6' Panel) | 1970 | 1970 | 2600 | LogNormal | 2162.6019 | 0.1185 | 20 | 2955 |  |  |  | 1576 | 0.1185 | 100 | Each (5'x6' Panel) | 1970 | 1970 | 2600 | LogNormal | 2162.6019 | 0.1185 | 20 | 2364 |  |  |  | 1674.5 | 0.1185 | 100 | Each (5'x6' Panel) | [30 empty] | 0.603 | 0.603 | 0.882 | LogNormal | 0.603 | 0.30054 | 20 | 0.90521 |  |  |  | 0.48212 | 0.30054 | 100 | Each (5'x6' Panel) | 0.87 | 0.87 | 1.146 | LogNormal | 0.87 | 0.27666 | 20 | 1.3046 |  |  |  | 0.69618 | 0.27666 | 100 | Each (5'x6' Panel) | 0.87 | 0.87 | 1.146 | LogNormal | 0.87 | 0.27666 | 20 | 1.0438 |  |  |  | 0.73963 | 0.27666 | 100 | Each (5'x6' Panel) | [30 empty] | 30
| B2023.001 |  | B2023.001 | Generic Storefront, Config: Monolithic, Lamination: Unknown, Glass Type: Unknown, Details: Aspect ratio = 6:5, Other details Unknown | 770 | 770 | 1400 | LogNormal | 935.1717 | 0.28211 | 44 | 924 |  |  |  | 539 | 0.28211 | 434 | Each (5'x6' Panel) | 1370 | 1370 | 2000 | LogNormal | 1554.814 | 0.1668 | 44 | 0 |  |  |  | 0 | 0.1668 | 434 | Each (5'x6' Panel) | 1370 | 1370 | 2000 | LogNormal | 1554.814 | 0.1668 | 44 | 0 |  |  |  | 0 | 0.1668 | 434 | Each (5'x6' Panel) | [30 empty] | 0.57 | 0.57 | 1.02 | LogNormal | 0.57 | 0.37694 | 44 | 0.68324 |  |  |  | 0.40015 | 0.37694 | 434 | Each (5'x6' Panel) | 1.02 | 1.02 | 1.47 | LogNormal | 1.02 | 0.30054 | 44 | 1.02 |  |  |  | 1.02 | 0.30054 | 434 | Each (5'x6' Panel) | 1.02 | 1.02 | 1.47 | LogNormal | 1.02 | 0.30054 | 44 | 1.02 |  |  |  | 1.02 | 0.30054 | 434 | Each (5'x6' Panel) | [30 empty] | 30
| B2023.002 |  | B2023.002 | Generic Storefront, Config: IGU, Lamination: Unknown, Glass Type: Unknown, Details: Aspect ratio = 6:5, Other details Unknown | 770 | 770 | 1400 | LogNormal | 935.1717 | 0.28211 | 44 | 924 |  |  |  | 539 | 0.28211 | 434 | Each (5'x6' Panel) | 1370 | 1370 | 2000 | LogNormal | 1554.814 | 0.1668 | 44 | 0 |  |  |  | 0 | 0.1668 | 434 | Each (5'x6' Panel) | 1370 | 1370 | 2000 | LogNormal | 1554.814 | 0.1668 | 44 | 0 |  |  |  | 0 | 0.1668 | 434 | Each (5'x6' Panel) | [30 empty] | 0.57 | 0.57 | 1.02 | LogNormal | 0.57 | 0.37694 | 44 | 0.68324 |  |  |  | 0.40015 | 0.37694 | 434 | Each (5'x6' Panel) | 1.02 | 1.02 | 1.47 | LogNormal | 1.02 | 0.30054 | 44 | 1.02 |  |  |  | 1.02 | 0.30054 | 434 | Each (5'x6' Panel) | 1.02 | 1.02 | 1.47 | LogNormal | 1.02 | 0.30054 | 44 | 1.02 |  |  |  | 1.02 | 0.30054 | 434 | Each (5'x6' Panel) | [30 empty] | 30
| B2023.011 |  | B2023.011 | Storefront, Config: Monolithic, Lamination: Laminated, Glass Type: Annealed, Details: 1/4 in. (6 mm) AN LAM (0.030 PVB); glass-frame clearance = 0.41 in. (10 mm); aspect ratio = 6:5 sealant = dry | 770 | 770 | 1400 | LogNormal | 935.1717 | 0.28211 | 44 | 924 |  |  |  | 539 | 0.28211 | 434 | Each (5'x6' Panel) | 1370 | 1370 | 2000 | LogNormal | 1554.814 | 0.1668 | 44 | 0 |  |  |  | 0 | 0.1668 | 434 | Each (5'x6' Panel) | 1370 | 1370 | 2000 | LogNormal | 1554.814 | 0.1668 | 44 | 0 |  |  |  | 0 | 0.1668 | 434 | Each (5'x6' Panel) | [30 empty] | 0.57 | 0.57 | 1.02 | LogNormal | 0.57 | 0.37694 | 44 | 0.68324 |  |  |  | 0.40015 | 0.37694 | 434 | Each (5'x6' Panel) | 1.02 | 1.02 | 1.47 | LogNormal | 1.02 | 0.30054 | 44 | 1.02 |  |  |  | 1.02 | 0.30054 | 434 | Each (5'x6' Panel) | 1.02 | 1.02 | 1.47 | LogNormal | 1.02 | 0.30054 | 44 | 1.02 |  |  |  | 1.02 | 0.30054 | 434 | Each (5'x6' Panel) | [30 empty] | 30
| B2023.021 |  | B2023.021 | Storefront, Config: Monolithic, Lamination: Not laminated, Glass Type: Annealed, Details: 1/4 in. (6 mm) AN monolithic; glass-frame clearance = 0.41 in. (10 mm); aspect ratio = 6:5 sealant = dry | 770 | 770 | 1400 | LogNormal | 935.1717 | 0.28211 | 44 | 924 |  |  |  | 539 | 0.28211 | 434 | Each (5'x6' Panel) | 1370 | 1370 | 2000 | LogNormal | 1554.814 | 0.1668 | 44 | 0 |  |  |  | 0 | 0.1668 | 434 | Each (5'x6' Panel) | 1370 | 1370 | 2000 | LogNormal | 1554.814 | 0.1668 | 44 | 0 |  |  |  | 0 | 0.1668 | 434 | Each (5'x6' Panel) | [30 empty] | 0.57 | 0.57 | 1.02 | LogNormal | 0.57 | 0.37694 | 44 | 0.68324 |  |  |  | 0.40015 | 0.37694 | 434 | Each (5'x6' Panel) | 1.02 | 1.02 | 1.47 | LogNormal | 1.02 | 0.30054 | 44 | 1.02 |  |  |  | 1.02 | 0.30054 | 434 | Each (5'x6' Panel) | 1.02 | 1.02 | 1.47 | LogNormal | 1.02 | 0.30054 | 44 | 1.02 |  |  |  | 1.02 | 0.30054 | 434 | Each (5'x6' Panel) | [30 empty] | 30
| B2023.031 |  | B2023.031 | Storefront, Config: Monolithic, Lamination: Not laminated, Glass Type: Full tempered, Details: 3/8 in. (10 mm) FT monolithic, Planar Specimen; glass-frame clearance = 0.5 in. (13 mm); aspect ratio = 1.93:1 sealant = wet | 1370 | 1370 | 2000 | LogNormal | 1554.814 | 0.1668 | 20 | 2055 |  |  |  | 1096 | 0.1668 | 100 | Each (5'x6' Panel) | 1370 | 1370 | 2000 | LogNormal | 1554.814 | 0.1668 | 20 | 2055 |  |  |  | 1096 | 0.1668 | 100 | Each (5'x6' Panel) | [45 empty] | 0.603 | 0.603 | 0.882 | LogNormal | 0.68477 | 0.30054 | 20 | 0.90521 |  |  |  | 0.48212 | 0.30054 | 100 | Each (5'x6' Panel) | 0.603 | 0.603 | 0.882 | LogNormal | 0.68477 | 0.30054 | 20 | 0.90521 |  |  |  | 0.48212 | 0.30054 | 100 | Each (5'x6' Panel) | [45 empty] | 30
| B2023.032 |  | B2023.032 | Storefront, Config: Monolithic, Lamination: Not laminated, Glass Type: Full tempered, Details: 3/8 in. (10 mm) FT monolithic, Corner Cond. Specimen, in-plane; glass-frame clearance = 0.5 in. (13 mm); aspect ratio = 1.93:1 sealant = wet | 1370 | 1370 | 2000 | LogNormal | 1554.814 | 0.1668 | 20 | 2055 |  |  |  | 1096 | 0.1668 | 100 | Each (5'x6' Panel) | 1370 | 1370 | 2000 | LogNormal | 1554.814 | 0.1668 | 20 | 2055 |  |  |  | 1096 | 0.1668 | 100 | Each (5'x6' Panel) | [45 empty] | 0.603 | 0.603 | 0.882 | LogNormal | 0.68477 | 0.30054 | 20 | 0.90521 |  |  |  | 0.48212 | 0.30054 | 100 | Each (5'x6' Panel) | 0.603 | 0.603 | 0.882 | LogNormal | 0.68477 | 0.30054 | 20 | 0.90521 |  |  |  | 0.48212 | 0.30054 | 100 | Each (5'x6' Panel) | [45 empty] | 30
| B2023.033 |  | B2023.033 | Storefront, Config: Monolithic, Lamination: Not laminated, Glass Type: Full tempered, Details: 3/8 in. (10 mm) FT monolithic, Corner Cond. Specimen, combined; glass-frame clearance = 0.5 in. (13 mm); aspect ratio = 1.93:1 sealant = wet | 1370 | 1370 | 2000 | LogNormal | 1554.814 | 0.1668 | 20 | 2055 |  |  |  | 1096 | 0.1668 | 100 | Each (5'x6' Panel) | 1370 | 1370 | 2000 | LogNormal | 1554.814 | 0.1668 | 20 | 2055 |  |  |  | 1096 | 0.1668 | 100 | Each (5'x6' Panel) | [45 empty] | 0.603 | 0.603 | 0.882 | LogNormal | 0.68477 | 0.30054 | 20 | 0.90521 |  |  |  | 0.48212 | 0.30054 | 100 | Each (5'x6' Panel) | 0.603 | 0.603 | 0.882 | LogNormal | 0.68477 | 0.30054 | 20 | 0.90521 |  |  |  | 0.48212 | 0.30054 | 100 | Each (5'x6' Panel) | [45 empty] | 30
| B2023.034 |  | B2023.034 | Storefront, Config: Monolithic, Lamination: Not laminated, Glass Type: Full tempered, Details: 3/8 in. (10 mm) FT monolithic, Corner Cond. Specimen, Short side; glass-frame clearance = 0.5 in. (13 mm); aspect ratio = 2.72:1 sealant = wet | 1370 | 1370 | 2000 | LogNormal | 1554.814 | 0.1668 | 20 | 2055 |  |  |  | 1096 | 0.1668 | 100 | Each (5'x6' Panel) | 1370 | 1370 | 2000 | LogNormal | 1554.814 | 0.1668 | 20 | 2055 |  |  |  | 1096 | 0.1668 | 100 | Each (5'x6' Panel) | [45 empty] | 0.603 | 0.603 | 0.882 | LogNormal | 0.68477 | 0.30054 | 20 | 0.90521 |  |  |  | 0.48212 | 0.30054 | 100 | Each (5'x6' Panel) | 0.603 | 0.603 | 0.882 | LogNormal | 0.68477 | 0.30054 | 20 | 0.90521 |  |  |  | 0.48212 | 0.30054 | 100 | Each (5'x6' Panel) | [45 empty] | 30
| B2023.041 |  | B2023.041 | Storefront, Config: Symmetric insulating glass units (dual-pane, equal-thickness IGU), Lamination: Not laminated, Glass Type: Annealed, Details: 1 in. (25 mm) AN IGU; glass-frame clearance = 0.59 in. (15 mm); aspect ratio = 6:5 sealant = dry | 770 | 770 | 1400 | LogNormal | 935.1717 | 0.28211 | 44 | 924 |  |  |  | 539 | 0.28211 | 434 | Each (5'x6' Panel) | 1370 | 1370 | 2000 | LogNormal | 1554.814 | 0.1668 | 44 | 0 |  |  |  | 0 | 0.1668 | 434 | Each (5'x6' Panel) | 1370 | 1370 | 2000 | LogNormal | 1554.814 | 0.1668 | 44 | 0 |  |  |  | 0 | 0.1668 | 434 | Each (5'x6' Panel) | [30 empty] | 0.57 | 0.57 | 1.02 | LogNormal | 0.68908 | 0.37694 | 44 | 0.68324 |  |  |  | 0.40015 | 0.37694 | 434 | Each (5'x6' Panel) | 1.02 | 1.02 | 1.47 | LogNormal | 1.1528 | 0.30054 | 44 | 1.02 |  |  |  | 1.02 | 0.30054 | 434 | Each (5'x6' Panel) | 1.02 | 1.02 | 1.47 | LogNormal | 1.1528 | 0.30054 | 44 | 1.02 |  |  |  | 1.02 | 0.30054 | 434 | Each (5'x6' Panel) | [30 empty] | 30
| B2023.051 |  | B2023.051 | Storefront, Config: Symmetric insulating glass units (dual-pane, equal-thickness IGU), Lamination: Not laminated, Glass Type: Full tempered, Details: 1 in. (25 mm) FT IGU [1/4 in. (6 mm) inner and outer panes], Planar Specimen; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 1.89:1 sealant = dry | 1970 | 1970 | 2600 | LogNormal | 2162.6019 | 0.1185 | 20 | 2955 |  |  |  | 1576 | 0.1185 | 100 | Each (5'x6' Panel) | 1970 | 1970 | 2600 | LogNormal | 2162.6019 | 0.1185 | 20 | 2955 |  |  |  | 1576 | 0.1185 | 100 | Each (5'x6' Panel) | [45 empty] | 0.87 | 0.87 | 1.146 | LogNormal | 0.95444 | 0.27666 | 20 | 1.3046 |  |  |  | 0.69618 | 0.27666 | 100 | Each (5'x6' Panel) | 0.87 | 0.87 | 1.146 | LogNormal | 0.95444 | 0.27666 | 20 | 1.3046 |  |  |  | 0.69618 | 0.27666 | 100 | Each (5'x6' Panel) | [45 empty] | 30
| B2023.052 |  | B2023.052 | Storefront, Config: Symmetric insulating glass units (dual-pane, equal-thickness IGU), Lamination: Not laminated, Glass Type: Full tempered, Details: 1 in. (25 mm) FT IGU [1/4 in. (6 mm) inner and outer panes], Corner Cond. Specimen, in-plane; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 1.89:1 sealant = dry | 1970 | 1970 | 2600 | LogNormal | 2162.6019 | 0.1185 | 20 | 2955 |  |  |  | 1576 | 0.1185 | 100 | Each (5'x6' Panel) | 1970 | 1970 | 2600 | LogNormal | 2162.6019 | 0.1185 | 20 | 2955 |  |  |  | 1576 | 0.1185 | 100 | Each (5'x6' Panel) | [45 empty] | 0.87 | 0.87 | 1.146 | LogNormal | 0.95444 | 0.27666 | 20 | 1.3046 |  |  |  | 0.69618 | 0.27666 | 100 | Each (5'x6' Panel) | 0.87 | 0.87 | 1.146 | LogNormal | 0.95444 | 0.27666 | 20 | 1.3046 |  |  |  | 0.69618 | 0.27666 | 100 | Each (5'x6' Panel) | [45 empty] | 30
| B2023.053 |  | B2023.053 | Storefront, Config: Symmetric insulating glass units (dual-pane, equal-thickness IGU), Lamination: Not laminated, Glass Type: Full tempered, Details: 1 in. (25 mm) FT IGU [1/4 in. (6 mm) inner and outer panes], Corner Cond. Specimen, combined; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 1.89:1 sealant = dry | 1970 | 1970 | 2600 | LogNormal | 2162.6019 | 0.1185 | 20 | 2955 |  |  |  | 1576 | 0.1185 | 100 | Each (5'x6' Panel) | 1970 | 1970 | 2600 | LogNormal | 2162.6019 | 0.1185 | 20 | 2955 |  |  |  | 1576 | 0.1185 | 100 | Each (5'x6' Panel) | [45 empty] | 0.87 | 0.87 | 1.146 | LogNormal | 0.95444 | 0.27666 | 20 | 1.3046 |  |  |  | 0.69618 | 0.27666 | 100 | Each (5'x6' Panel) | 0.87 | 0.87 | 1.146 | LogNormal | 0.95444 | 0.27666 | 20 | 1.3046 |  |  |  | 0.69618 | 0.27666 | 100 | Each (5'x6' Panel) | [45 empty] | 30
| B2023.054 |  | B2023.054 | Storefront, Config: Symmetric insulating glass units (dual-pane, equal-thickness IGU), Lamination: Not laminated, Glass Type: Full tempered, Details: 1 in. (25 mm) FT IGU [1/4 in. (6 mm) inner and outer panes], Corner Cond. Specimen, Short side; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 2.83:1 sealant = dry | 1970 | 1970 | 2600 | LogNormal | 2162.6019 | 0.1185 | 20 | 2955 |  |  |  | 1576 | 0.1185 | 100 | Each (5'x6' Panel) | 1970 | 1970 | 2600 | LogNormal | 2162.6019 | 0.1185 | 20 | 2955 |  |  |  | 1576 | 0.1185 | 100 | Each (5'x6' Panel) | [45 empty] | 0.87 | 0.87 | 1.146 | LogNormal | 0.95444 | 0.27666 | 20 | 1.3046 |  |  |  | 0.69618 | 0.27666 | 100 | Each (5'x6' Panel) | 0.87 | 0.87 | 1.146 | LogNormal | 0.95444 | 0.27666 | 20 | 1.3046 |  |  |  | 0.69618 | 0.27666 | 100 | Each (5'x6' Panel) | [45 empty] | 30
| B2023.055 |  | B2023.055 | Storefront, Config: Symmetric insulating glass units (dual-pane, equal-thickness IGU), Lamination: Not laminated, Glass Type: Full tempered, Details: 1 in. (25 mm) FT IGU [1/4 in. (6 mm) inner and outer panes], Planar Specimen; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 1.88:1 sealant = dry | 1970 | 1970 | 2600 | LogNormal | 2162.6019 | 0.1185 | 20 | 2955 |  |  |  | 1576 | 0.1185 | 100 | Each (5'x6' Panel) | 1970 | 1970 | 2600 | LogNormal | 2162.6019 | 0.1185 | 20 | 2955 |  |  |  | 1576 | 0.1185 | 100 | Each (5'x6' Panel) | [45 empty] | 0.87 | 0.87 | 1.146 | LogNormal | 0.95444 | 0.27666 | 20 | 1.3046 |  |  |  | 0.69618 | 0.27666 | 100 | Each (5'x6' Panel) | 0.87 | 0.87 | 1.146 | LogNormal | 0.95444 | 0.27666 | 20 | 1.3046 |  |  |  | 0.69618 | 0.27666 | 100 | Each (5'x6' Panel) | [45 empty] | 30
| B2023.056 |  | B2023.056 | Storefront, Config: Symmetric insulating glass units (dual-pane, equal-thickness IGU), Lamination: Not laminated, Glass Type: Full tempered, Details: 1 in. (25 mm) FT IGU [1/4 in. (6 mm) inner and outer panes], Corner Cond. Specimen, in-plane; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 1.88:1 sealant = dry | 1970 | 1970 | 2600 | LogNormal | 2162.6019 | 0.1185 | 20 | 2955 |  |  |  | 1576 | 0.1185 | 100 | Each (5'x6' Panel) | 1970 | 1970 | 2600 | LogNormal | 2162.6019 | 0.1185 | 20 | 2955 |  |  |  | 1576 | 0.1185 | 100 | Each (5'x6' Panel) | [45 empty] | 0.87 | 0.87 | 1.146 | LogNormal | 0.95444 | 0.27666 | 20 | 1.3046 |  |  |  | 0.69618 | 0.27666 | 100 | Each (5'x6' Panel) | 0.87 | 0.87 | 1.146 | LogNormal | 0.95444 | 0.27666 | 20 | 1.3046 |  |  |  | 0.69618 | 0.27666 | 100 | Each (5'x6' Panel) | [45 empty] | 30
| B2023.057 |  | B2023.057 | Storefront, Config: Symmetric insulating glass units (dual-pane, equal-thickness IGU), Lamination: Not laminated, Glass Type: Full tempered, Details: 1 in. (25 mm) FT IGU [1/4 in. (6 mm) inner and outer panes], Corner Cond. Specimen, combined; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 1.88:1 sealant = dry | 1970 | 1970 | 2600 | LogNormal | 2162.6019 | 0.1185 | 20 | 2955 |  |  |  | 1576 | 0.1185 | 100 | Each (5'x6' Panel) | 1970 | 1970 | 2600 | LogNormal | 2162.6019 | 0.1185 | 20 | 2955 |  |  |  | 1576 | 0.1185 | 100 | Each (5'x6' Panel) | [45 empty] | 0.87 | 0.87 | 1.146 | LogNormal | 0.95444 | 0.27666 | 20 | 1.3046 |  |  |  | 0.69618 | 0.27666 | 100 | Each (5'x6' Panel) | 0.87 | 0.87 | 1.146 | LogNormal | 0.95444 | 0.27666 | 20 | 1.3046 |  |  |  | 0.69618 | 0.27666 | 100 | Each (5'x6' Panel) | [45 empty] | 30
| B2023.058 |  | B2023.058 | Storefront, Config: Symmetric insulating glass units (dual-pane, equal-thickness IGU), Lamination: Not laminated, Glass Type: Full tempered, Details: 1 in. (25 mm) FT IGU [1/4 in. (6 mm) inner and outer panes], Corner Cond. Specimen, Short side; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 2.82:1 sealant = dry | 1970 | 1970 | 2600 | LogNormal | 2162.6019 | 0.1185 | 20 | 2955 |  |  |  | 1576 | 0.1185 | 100 | Each (5'x6' Panel) | 1970 | 1970 | 2600 | LogNormal | 2162.6019 | 0.1185 | 20 | 2955 |  |  |  | 1576 | 0.1185 | 100 | Each (5'x6' Panel) | [45 empty] | 0.87 | 0.87 | 1.146 | LogNormal | 0.95444 | 0.27666 | 20 | 1.3046 |  |  |  | 0.69618 | 0.27666 | 100 | Each (5'x6' Panel) | 0.87 | 0.87 | 1.146 | LogNormal | 0.95444 | 0.27666 | 20 | 1.3046 |  |  |  | 0.69618 | 0.27666 | 100 | Each (5'x6' Panel) | [45 empty] | 30
| B3011.011 |  | B3011.011 | Concrete tile roof, tiles secured and compliant with UBC94 | 400 | 700 | 1565 | LogNormal | 742.9669 | 0.57618 | 13 | 840 |  |  |  | 490 | 0.57618 | 130 | 100 ft^2 Units | 1150 | 1480 | 2390 | LogNormal | 1587.3204 | 0.30743 | 13 | 2220 |  |  |  | 1184 | 0.30743 | 130 | 100 ft^2 Units | [45 empty] | 0.4 | 0.8 | 1.7 | LogNormal | 0.8 | 0.62808 | 13 | 0.95441 |  |  |  | 0.56838 | 0.62808 | 130 | 100 ft^2 Units | 1.3 | 1.6 | 2.6 | LogNormal | 1.6 | 0.39625 | 13 | 2.4162 |  |  |  | 1.2735 | 0.39625 | 130 | 100 ft^2 Units | [45 empty] | 100
| B3011.012 |  | B3011.012 | Clay tile roof, tiles secured and compliant with UBC94 | 625 | 1025 | 2000 | LogNormal | 1073.5571 | 0.48035 | 5 | 1332.5 |  |  |  | 820 | 0.48035 | 50 | 100 ft^2 Units | 1350 | 2000 | 3350 | LogNormal | 2072.9371 | 0.36923 | 5 | 3000 |  |  |  | 1600 | 0.36923 | 50 | 100 ft^2 Units | [45 empty] | 0.69 | 1.13 | 2.21 | LogNormal | 1.13 | 0.54151 | 5 | 1.4692 |  |  |  | 0.9039 | 0.54151 | 50 | 100 ft^2 Units | 1.49 | 2.21 | 3.69 | LogNormal | 2.21 | 0.44591 | 5 | 3.3129 |  |  |  | 1.7688 | 0.44591 | 50 | 100 ft^2 Units | [45 empty] | 100
| B3011.013 |  | B3011.013 | Concrete tile roof, unsecured tiles | 325 | 625 | 1490 | LogNormal | 655.9027 | 0.63667 | 1 | 812.5 |  |  |  | 500 | 0.63667 | 10 | 100 ft^2 Units | 700 | 1030 | 1940 | LogNormal | 1104.2289 | 0.43109 | 1 | 1545 |  |  |  | 824 | 0.43109 | 10 | 100 ft^2 Units | [45 empty] | 0.36 | 0.69 | 1.64 | LogNormal | 0.69 | 0.68399 | 1 | 0.8968 |  |  |  | 0.55213 | 0.68399 | 10 | 100 ft^2 Units | 0.77 | 1.14 | 2.14 | LogNormal | 1.14 | 0.49834 | 1 | 1.708 |  |  |  | 0.91279 | 0.49834 | 10 | 100 ft^2 Units | [45 empty] | 100
| B3011.014 |  | B3011.014 | Clay tile roof, unsecured tiles | 550 | 950 | 1925 | LogNormal | 989.7183 | 0.51493 | 1 | 1235 |  |  |  | 760 | 0.51493 | 10 | 100 ft^2 Units | 900 | 1550 | 2900 | LogNormal | 1584.4806 | 0.46911 | 1 | 2325 |  |  |  | 1240 | 0.46911 | 10 | 100 ft^2 Units | [45 empty] | 0.61 | 1.05 | 2.12 | LogNormal | 1.05 | 0.57241 | 1 | 1.3643 |  |  |  | 0.84044 | 0.57241 | 10 | 100 ft^2 Units | 0.99 | 1.71 | 3.2 | LogNormal | 1.71 | 0.53157 | 1 | 2.5648 |  |  |  | 1.3681 | 0.53157 | 10 | 100 ft^2 Units | [45 empty] | 100
| B3031.001a |  | B3031.001a | Masonry Chimney - unreinforced, non industrial, above roof 5 ft, replace with masonry | 6370 | 7225 | 9085 | LogNormal | 7474.3117 | 0.14332 | 1 | 9392.5 |  |  |  | 5780 | 0.14332 | 5 | Each | 6370 | 7225 | 9085 | LogNormal | 7474.3117 | 0.14332 | 1 | 10837.5 |  |  |  | 5780 | 0.14332 | 5 | Each | [45 empty] | 7.0257 | 7.9688 | 10.0202 | LogNormal | 7.9688 | 0.28817 | 1 | 10.3594 |  |  |  | 6.375 | 0.28817 | 5 | Each | 7.0257 | 7.9688 | 10.0202 | LogNormal | 7.9688 | 0.28817 | 1 | 11.9532 |  |  |  | 6.375 | 0.28817 | 5 | Each | [45 empty] | 1
| B3031.001b |  | B3031.001b | Masonry Chimney - unreinforced, non industrial, above roof 10 ft, replace with masonry | 9515 | 11200 | 14580 | LogNormal | 11573.43 | 0.17215 | 1 | 14560 |  |  |  | 8960 | 0.17215 | 5 | Each | 9515 | 11200 | 14580 | LogNormal | 11573.43 | 0.17215 | 1 | 16800 |  |  |  | 8960 | 0.17215 | 5 | Each | [45 empty] | 10.4945 | 12.3529 | 16.0809 | LogNormal | 12.3529 | 0.30354 | 1 | 16.0588 |  |  |  | 9.8823 | 0.30354 | 5 | Each | 10.4945 | 12.3529 | 16.0809 | LogNormal | 12.3529 | 0.30354 | 1 | 18.5294 |  |  |  | 9.8823 | 0.30354 | 5 | Each | [45 empty] | 1
| B3031.001c |  | B3031.001c | Masonry Chimney - unreinforced, non industrial, above roof 15 ft, replace with masonry | 12660 | 15175 | 20075 | LogNormal | 15667.7021 | 0.18583 | 1 | 19727.5 |  |  |  | 12140 | 0.18583 | 5 | Each | 12660 | 15175 | 20075 | LogNormal | 15667.7021 | 0.18583 | 1 | 22762.5 |  |  |  | 12140 | 0.18583 | 5 | Each | [45 empty] | 13.9632 | 16.7371 | 22.1415 | LogNormal | 16.7371 | 0.3115 | 1 | 21.7582 |  |  |  | 13.3897 | 0.3115 | 5 | Each | 13.9632 | 16.7371 | 22.1415 | LogNormal | 16.7371 | 0.3115 | 1 | 25.1057 |  |  |  | 13.3897 | 0.3115 | 5 | Each | [45 empty] | 1
| B3031.002a |  | B3031.002a | Masonry Chimney - unreinforced, non industrial, above roof 5 ft, replace with framing | 4495 | 6525 | 8105 | Normal | 6374.9895 | 0.22093 | 1 | 9787.5 |  |  |  | 5220 | 0.22093 | 5 | Each | 4495 | 6525 | 8105 | Normal | 6374.9947 | 0.22094 | 1 | 9787.5 |  |  |  | 5220 | 0.22094 | 5 | Each | [45 empty] | 4.9577 | 7.1967 | 8.9393 | Normal | 7.1967 | 0.33363 | 1 | 10.795 |  |  |  | 5.7574 | 0.33363 | 5 | Each | 4.9577 | 7.1967 | 8.9393 | Normal | 7.1967 | 0.33364 | 1 | 10.795 |  |  |  | 5.7574 | 0.33364 | 5 | Each | [45 empty] | 1
| B3031.002b |  | B3031.002b | Masonry Chimney - unreinforced, non industrial, above roof 10 ft, replace with framing | 8265 | 9800 | 12720 | LogNormal | 10092.579 | 0.17332 | 1 | 14700 |  |  |  | 7840 | 0.17332 | 5 | Each | 8265 | 9800 | 12720 | LogNormal | 10092.579 | 0.17332 | 1 | 14700 |  |  |  | 7840 | 0.17332 | 5 | Each | [45 empty] | 9.1158 | 10.8088 | 14.0294 | LogNormal | 10.8088 | 0.3042 | 1 | 16.2132 |  |  |  | 8.647 | 0.3042 | 5 | Each | 9.1158 | 10.8088 | 14.0294 | LogNormal | 10.8088 | 0.3042 | 1 | 16.2132 |  |  |  | 8.647 | 0.3042 | 5 | Each | [45 empty] | 1
| B3031.002c |  | B3031.002c | Masonry Chimney - unreinforced, non industrial, above roof 15 ft, replace with framing | 9535 | 13075 | 14785 | Normal | 12464.9929 | 0.16432 | 1 | 19612.5 |  |  |  | 10460 | 0.16432 | 5 | Each | 9535 | 13075 | 14785 | Normal | 12464.902 | 0.16433 | 1 | 19612.5 |  |  |  | 10460 | 0.16433 | 5 | Each | [45 empty] | 10.5165 | 14.421 | 16.307 | Normal | 14.421 | 0.29917 | 1 | 21.6315 |  |  |  | 11.5368 | 0.29917 | 5 | Each | 10.5165 | 14.421 | 16.307 | Normal | 14.421 | 0.29917 | 1 | 21.6315 |  |  |  | 11.5368 | 0.29917 | 5 | Each | [45 empty] | 1
| B3041.001 |  | B3041.001 | Masonry Parapet - unreinforced, unbraced | 340 | 540 | 670 | Normal | 516.6667 | 0.24919 | 10 | 810 |  |  |  | 432 | 0.24919 | 50 | LF 10 | 340 | 540 | 670 | Normal | 516.665 | 0.24918 | 10 | 810 |  |  |  | 432 | 0.24918 | 50 | LF 10 | [45 empty] | 0.33 | 0.5241 | 0.6503 | Normal | 0.50147 | 0.35298 | 10 | 0.78616 |  |  |  | 0.41928 | 0.35298 | 50 | LF 10 | 0.33 | 0.5241 | 0.6503 | Normal | 0.50147 | 0.35298 | 10 | 0.78616 |  |  |  | 0.41928 | 0.35298 | 50 | LF 10 | [45 empty] | 1
| C1011.001a |  | C1011.001a | Wall Partition, Type: Gypsum with metal studs, Full Height, Fixed Below, Fixed Above | 700 | 1785 | 2925 | Normal | 1803.3325 | 0.48138 | 1 | 2677.5 |  |  |  | 1428 | 0.48138 | 10 | 1300 ft^2 | 1850 | 4550 | 8700 | LogNormal | 4297.31 | 0.55591 | 1 | 6825 |  |  |  | 3640 | 0.55591 | 10 | 1300 ft^2 | 7150 | 8750 | 11650 | LogNormal | 8990.9755 | 0.19586 | 1 | 10500 |  |  |  | 7437.5 | 0.19586 | 10 | 1300 ft^2 | [30 empty] | 0.52 | 1.43 | 2.34 | Normal | 1.43 | 0.54243 | 1 | 2.1256 |  |  |  | 1.1518 | 0.54243 | 10 | 1300 ft^2 | 1.43 | 3.51 | 6.76 | LogNormal | 3.3225 | 0.60954 | 1 | 5.2832 |  |  |  | 2.8007 | 0.60954 | 10 | 1300 ft^2 | 5.59 | 6.76 | 9.1 | LogNormal | 6.998 | 0.31759 | 1 | 8.124 |  |  |  | 5.737 | 0.31759 | 10 | 1300 ft^2 | [30 empty] | 1300
| C1011.001b |  | C1011.001b | Wall Partition, Type: Gypsum with metal studs, Partial Height, Fixed Below, Lateral Braced Above | 700 | 1785 | 2925 | Normal | 1803.3325 | 0.48138 | 1 | 3570 |  |  |  | 1071 | 0.48138 | 10 | 1300 ft^2 | 1850 | 4550 | 8700 | LogNormal | 4297.31 | 0.55591 | 1 | 9100 |  |  |  | 2730 | 0.55591 | 10 | 1300 ft^2 | 7150 | 8750 | 11650 | LogNormal | 8990.9755 | 0.19586 | 1 | 17500 |  |  |  | 5250 | 0.19586 | 10 | 1300 ft^2 | [30 empty] | 0.52 | 1.43 | 2.34 | Normal | 1.43 | 0.54243 | 1 | 2.8213 |  |  |  | 0.8735 | 0.54243 | 10 | 1300 ft^2 | 1.43 | 3.51 | 6.76 | LogNormal | 3.3225 | 0.60954 | 1 | 7.0563 |  |  |  | 2.0915 | 0.60954 | 10 | 1300 ft^2 | 5.59 | 6.76 | 9.1 | LogNormal | 6.998 | 0.31759 | 1 | 13.5799 |  |  |  | 4.0321 | 0.31759 | 10 | 1300 ft^2 | [30 empty] | 1300
| C1011.001c |  | C1011.001c | Wall Partition, Type: Gypsum with metal studs, Full Height, Fixed Below, Slip Track Above with returns | 280 | 714 | 1170 | Normal | 721.333 | 0.48138 | 1 | 1428 |  |  |  | 428.4 | 0.48138 | 10 | 1300 ft^2 | 740 | 1820 | 3480 | LogNormal | 1718.9226 | 0.55591 | 1 | 3640 |  |  |  | 1092 | 0.55591 | 10 | 1300 ft^2 | 2860 | 3500 | 4660 | LogNormal | 3596.3884 | 0.19586 | 1 | 7000 |  |  |  | 2100 | 0.19586 | 10 | 1300 ft^2 | [30 empty] | 0.26 | 0.52 | 0.91 | Normal | 0.50245 | 0.54243 | 1 | 1.0765 |  |  |  | 0.2974 | 0.54243 | 10 | 1300 ft^2 | 0.52 | 1.43 | 2.73 | LogNormal | 1.56 | 0.60954 | 1 | 2.8485 |  |  |  | 0.86259 | 0.60954 | 10 | 1300 ft^2 | 2.21 | 2.73 | 3.64 | LogNormal | 2.7979 | 0.31759 | 1 | 5.4579 |  |  |  | 1.6388 | 0.31759 | 10 | 1300 ft^2 | [30 empty] | 1300
| C1011.001d |  | C1011.001d | Wall Partition, Type: Gypsum with metal studs, Full Height, Fixed Below, Slip Track Above w/o returns (friction connections) | 350 | 892.5 | 1462.5 | Normal | 901.6662 | 0.48138 | 1 | 1785 |  |  |  | 535.5 | 0.48138 | 10 | 1300 ft^2 | 925 | 2275 | 4350 | LogNormal | 2148.6535 | 0.55591 | 1 | 4550 |  |  |  | 1365 | 0.55591 | 10 | 1300 ft^2 | [45 empty] | 0.26 | 0.65 | 1.17 | Normal | 0.69333 | 0.54243 | 1 | 1.3456 |  |  |  | 0.37175 | 0.54243 | 10 | 1300 ft^2 | 0.78 | 1.82 | 3.38 | LogNormal | 1.7248 | 0.60954 | 1 | 3.5932 |  |  |  | 1.1107 | 0.60954 | 10 | 1300 ft^2 | [45 empty] | 1300
| C1011.011a |  | C1011.011a | Wall Partition, Type: Gypsum with wood studs, Full Height, Fixed Below, Fixed Above | 700 | 2170 | 3000 | Normal | 1956.6655 | 0.45861 | 1 | 4340 |  |  |  | 1302 | 0.45861 | 10 | 1300 ft^2 | 2050 | 5550 | 8900 | Normal | 5499.9816 | 0.48592 | 1 | 11100 |  |  |  | 3330 | 0.48592 | 10 | 1300 ft^2 | 15450 | 16950 | 26450 | LogNormal | 19005.6361 | 0.23515 | 1 | 33900 |  |  |  | 10170 | 0.23515 | 10 | 1300 ft^2 | [30 empty] | 0.52 | 1.69 | 2.34 | Normal | 1.5167 | 0.52233 | 1 | 3.3813 |  |  |  | 1.0135 | 0.52233 | 10 | 1300 ft^2 | 1.56 | 4.29 | 6.89 | Normal | 4.2467 | 0.54646 | 1 | 8.6157 |  |  |  | 2.5597 | 0.54646 | 10 | 1300 ft^2 | 12.09 | 13.26 | 20.67 | LogNormal | 14.8648 | 0.34321 | 1 | 26.471 |  |  |  | 7.9756 | 0.34321 | 10 | 1300 ft^2 | [30 empty] | 1300
| C2011.001a |  | C2011.001a | Prefabricated steel stair with steel treads and landings with seismic joints that accommodate drift. | 700 | 2170 | 3000 | Normal | 1956.6655 | 0.45861 | 1 | 4340 |  |  |  | 1302 | 0.45861 | 10 | 1300 ft^2 | 2050 | 5550 | 8900 | Normal | 5499.9816 | 0.48592 | 1 | 11100 |  |  |  | 3330 | 0.48592 | 10 | 1300 ft^2 | 15450 | 16950 | 26450 | LogNormal | 19005.6361 | 0.23515 | 1 | 33900 |  |  |  | 10170 | 0.23515 | 10 | 1300 ft^2 | [30 empty] | 0.52 | 1.69 | 2.34 | Normal | 1.5167 | 0.52233 | 1 | 3.3813 |  |  |  | 1.0135 | 0.52233 | 10 | 1300 ft^2 | 1.56 | 4.29 | 6.89 | Normal | 4.2467 | 0.54646 | 1 | 8.6157 |  |  |  | 2.5597 | 0.54646 | 10 | 1300 ft^2 | 12.09 | 13.26 | 20.67 | LogNormal | 14.8648 | 0.34321 | 1 | 26.471 |  |  |  | 7.9756 | 0.34321 | 10 | 1300 ft^2 | [30 empty] | 1300
| C2011.001b |  | C2011.001b | Prefabricated steel stair with steel treads and landings with no seismic joint. | 700 | 2170 | 3000 | Normal | 1956.6655 | 0.45861 | 1 | 4340 |  |  |  | 1302 | 0.45861 | 10 | 1300 ft^2 | 2050 | 5550 | 8900 | Normal | 5499.9816 | 0.48592 | 1 | 11100 |  |  |  | 3330 | 0.48592 | 10 | 1300 ft^2 | 18000 | 18800 | 22800 | LogNormal | 19762.5099 | 0.096878 | 1 | 37600 |  |  |  | 11280 | 0.096878 | 10 | 1300 ft^2 | [30 empty] | 0.52 | 1.69 | 2.34 | Normal | 1.5167 | 0.52233 | 1 | 3.3813 |  |  |  | 1.0135 | 0.52233 | 10 | 1300 ft^2 | 1.56 | 4.29 | 6.89 | Normal | 4.2467 | 0.54646 | 1 | 8.6157 |  |  |  | 2.5597 | 0.54646 | 10 | 1300 ft^2 | 14.04 | 14.69 | 17.81 | LogNormal | 15.4311 | 0.26811 | 1 | 29.3429 |  |  |  | 8.8288 | 0.26811 | 10 | 1300 ft^2 | [30 empty] | 1300
| C2011.011a |  | C2011.011a | Non-monolithic precast concrete stair assembly with concrete stringers and treads with seismic joints that accommodate drift. | 100 | 700 | 1700 | LogNormal | 614.156 | 0.80148 | 5 | 1400 |  |  |  | 420 | 0.80148 | 10 | Each | 1800 | 3700 | 7700 | LogNormal | 3710.7424 | 0.56935 | 5 | 7400 |  |  |  | 2220 | 0.56935 | 10 | Each | 12600 | 22950 | 34100 | Normal | 23216.655 | 0.3613 | 5 | 45900 |  |  |  | 13770 | 0.3613 | 10 | Each | [30 empty] | 0.1103 | 0.7721 | 1.875 | LogNormal | 0.7721 | 0.83956 | 5 | 1.5442 |  |  |  | 0.46328 | 0.83956 | 10 | Each | 1.9853 | 4.0809 | 8.4926 | LogNormal | 4.0809 | 0.62182 | 5 | 8.1618 |  |  |  | 2.4485 | 0.62182 | 10 | Each | 13.8971 | 25.3125 | 37.6103 | Normal | 25.3125 | 0.43936 | 5 | 50.625 |  |  |  | 15.1875 | 0.43936 | 10 | Each | [30 empty] | 1
| C2011.011b |  | C2011.011b | Non-monolithic precast concrete stair assembly with concrete stringers and treads with no seismic joint. | 100 | 700 | 1700 | LogNormal | 614.156 | 0.80148 | 5 | 1400 |  |  |  | 420 | 0.80148 | 10 | Each | 1800 | 3700 | 7700 | LogNormal | 3710.7424 | 0.56935 | 5 | 7400 |  |  |  | 2220 | 0.56935 | 10 | Each | 12600 | 22950 | 34100 | Normal | 23216.655 | 0.3613 | 5 | 45900 |  |  |  | 13770 | 0.3613 | 10 | Each | [30 empty] | 0.1103 | 0.7721 | 1.875 | LogNormal | 0.7721 | 0.83956 | 5 | 1.5442 |  |  |  | 0.46328 | 0.83956 | 10 | Each | 1.9853 | 4.0809 | 8.4926 | LogNormal | 4.0809 | 0.62182 | 5 | 8.1618 |  |  |  | 2.4485 | 0.62182 | 10 | Each | 13.8971 | 25.3125 | 37.6103 | Normal | 25.3125 | 0.43936 | 5 | 50.625 |  |  |  | 15.1875 | 0.43936 | 10 | Each | [30 empty] | 1
| C2011.021a |  | C2011.021a | Monolithic cast-in-place and precast concrete stairs with seismic joints that accommodate drift - replace in kind if replacement is required. | 100 | 700 | 1700 | LogNormal | 614.156 | 0.80148 | 3 | 910 |  |  |  | 560 | 0.80148 | 10 | Each | 1800 | 3700 | 7700 | LogNormal | 3710.7424 | 0.56935 | 3 | 4440 |  |  |  | 3145 | 0.56935 | 10 | Each | 14400 | 24950 | 36700 | Normal | 25349.987 | 0.34321 | 3 | 29940 |  |  |  | 21207.5 | 0.34321 | 10 | Each | [30 empty] | 0.1103 | 0.7721 | 1.875 | LogNormal | 0.7721 | 0.83956 | 3 | 1.0037 |  |  |  | 0.61769 | 0.83956 | 10 | Each | 1.9853 | 4.0809 | 8.4926 | LogNormal | 4.0809 | 0.62182 | 3 | 4.8971 |  |  |  | 3.4688 | 0.62182 | 10 | Each | 15.8824 | 27.5184 | 40.4779 | Normal | 27.5184 | 0.42461 | 3 | 33.0221 |  |  |  | 23.3906 | 0.42461 | 10 | Each | [30 empty] | 1
| C2011.021b |  | C2011.021b | Monolithic cast-in-place and precast concrete stairs with no seismic joints - replace in kind if replacement is required. | 100 | 700 | 1700 | LogNormal | 614.156 | 0.80148 | 3 | 840 |  |  |  | 560 | 0.80148 | 10 | Each | 1800 | 3700 | 7700 | LogNormal | 3710.7424 | 0.56935 | 3 | 4440 |  |  |  | 2960 | 0.56935 | 10 | Each | 14400 | 24950 | 36700 | Normal | 25349.987 | 0.34321 | 3 | 29940 |  |  |  | 19960 | 0.34321 | 10 | Each | [30 empty] | 0.1103 | 0.7721 | 1.875 | LogNormal | 0.7721 | 0.83956 | 3 | 0.92651 |  |  |  | 0.61769 | 0.83956 | 10 | Each | 1.9853 | 4.0809 | 8.4926 | LogNormal | 4.0809 | 0.62182 | 3 | 4.8971 |  |  |  | 3.2647 | 0.62182 | 10 | Each | 15.8824 | 27.5184 | 40.4779 | Normal | 27.5184 | 0.42461 | 3 | 33.0221 |  |  |  | 22.0147 | 0.42461 | 10 | Each | [30 empty] | 1
| C2011.021c |  | C2011.021c | Monolithic cast-in-place and precast concrete stairs with seismic joints that accommodate drift - replace with prefabricated steel stair if replacement is required. | 100 | 700 | 1700 | LogNormal | 614.156 | 0.80148 | 3 | 910 |  |  |  | 560 | 0.80148 | 10 | Each | 1800 | 3700 | 7700 | LogNormal | 3710.7424 | 0.56935 | 3 | 4440 |  |  |  | 3145 | 0.56935 | 10 | Each | 14400 | 24950 | 36700 | Normal | 25349.987 | 0.34321 | 3 | 29940 |  |  |  | 21207.5 | 0.34321 | 10 | Each | [30 empty] | 0.1103 | 0.7721 | 1.875 | LogNormal | 0.7721 | 0.83956 | 3 | 1.0037 |  |  |  | 0.61769 | 0.83956 | 10 | Each | 1.9853 | 4.0809 | 8.4926 | LogNormal | 4.0809 | 0.62182 | 3 | 4.8971 |  |  |  | 3.4688 | 0.62182 | 10 | Each | 15.8824 | 27.5184 | 40.4779 | Normal | 27.5184 | 0.42461 | 3 | 33.0221 |  |  |  | 23.3906 | 0.42461 | 10 | Each | [30 empty] | 1
| C2011.021d |  | C2011.021d | Monolithic cast-in-place and precast concrete stairs with no seismic joints - replace with prefabricated steel stair if replacement is required. | 100 | 700 | 1700 | LogNormal | 614.156 | 0.80148 | 3 | 840 |  |  |  | 560 | 0.80148 | 10 | Each | 1800 | 3700 | 7700 | LogNormal | 3710.7424 | 0.56935 | 3 | 4440 |  |  |  | 2960 | 0.56935 | 10 | Each | 14400 | 24950 | 36700 | Normal | 25349.987 | 0.34321 | 3 | 29940 |  |  |  | 19960 | 0.34321 | 10 | Each | [30 empty] | 0.1103 | 0.7721 | 1.875 | LogNormal | 0.7721 | 0.83956 | 3 | 0.92651 |  |  |  | 0.61769 | 0.83956 | 10 | Each | 1.9853 | 4.0809 | 8.4926 | LogNormal | 4.0809 | 0.62182 | 3 | 4.8971 |  |  |  | 3.2647 | 0.62182 | 10 | Each | 15.8824 | 27.5184 | 40.4779 | Normal | 27.5184 | 0.42461 | 3 | 33.0221 |  |  |  | 22.0147 | 0.42461 | 10 | Each | [30 empty] | 1
| C2011.031a |  | C2011.031a | Hybrid stair assembly with steel stringers and concrete treads and landings with seismic joints that accommodate drift. | 100 | 400 | 1400 | LogNormal | 393.9371 | 0.98993 | 3 | 480 |  |  |  | 320 | 0.98993 | 10 | Each | 1300 | 2700 | 5700 | LogNormal | 2710.2495 | 0.57976 | 3 | 3240 |  |  |  | 2160 | 0.57976 | 10 | Each | 10800 | 20950 | 31500 | Normal | 21083.3228 | 0.38306 | 3 | 25140 |  |  |  | 16760 | 0.38306 | 10 | Each | [30 empty] | 0.1103 | 0.4412 | 1.5441 | LogNormal | 0.4412 | 1.021 | 3 | 0.52944 |  |  |  | 0.35296 | 1.021 | 10 | Each | 1.4338 | 2.9779 | 6.2868 | LogNormal | 2.9779 | 0.63137 | 3 | 3.5735 |  |  |  | 2.3823 | 0.63137 | 10 | Each | 11.9118 | 23.1066 | 34.7426 | Normal | 23.1066 | 0.45742 | 3 | 27.7279 |  |  |  | 18.4853 | 0.45742 | 10 | Each | [30 empty] | 1
| C2011.031b |  | C2011.031b | Hybrid stair assembly with steel stringers and concrete treads and landings with no seismic joints. | 100 | 400 | 1400 | LogNormal | 393.9371 | 0.98993 | 3 | 480 |  |  |  | 320 | 0.98993 | 10 | Each | 1300 | 2700 | 5700 | LogNormal | 2710.2495 | 0.57976 | 3 | 3240 |  |  |  | 2160 | 0.57976 | 10 | Each | 10800 | 20950 | 31500 | Normal | 21083.3228 | 0.38306 | 3 | 25140 |  |  |  | 16760 | 0.38306 | 10 | Each | [30 empty] | 0.0926 | 0.3706 | 1.2971 | LogNormal | 0.3706 | 1.021 | 3 | 0.44472 |  |  |  | 0.29648 | 1.021 | 10 | Each | 1.2044 | 2.5015 | 5.2809 | LogNormal | 2.5015 | 0.63137 | 3 | 3.0018 |  |  |  | 2.0012 | 0.63137 | 10 | Each | 10.0059 | 19.4096 | 29.1838 | Normal | 19.4096 | 0.45742 | 3 | 23.2915 |  |  |  | 15.5277 | 0.45742 | 10 | Each | [30 empty] | 1
| C3011.001a |  | C3011.001a | Wall Partition, Type: Gypsum + Wallpaper, Full Height, Fixed Below, Fixed Above | 2400 | 2700 | 3500 | LogNormal | 2828.8612 | 0.15424 | 1 | 3240 |  |  |  | 2160 | 0.15424 | 3 | Each (9'x100' Panel) | [60 empty] | 2.25 | 2.52 | 3.24 | LogNormal | 2.52 | 0.29375 | 1 | 3.0203 |  |  |  | 2.0197 | 0.29375 | 3 | Each (9'x100' Panel) | [60 empty] | 900
| C3011.001b |  | C3011.001b | Wall Partition, Type: Gypsum + Wallpaper, Partial Height, Fixed Below, Lateral Braced Above | 2400 | 2700 | 3500 | LogNormal | 2828.8612 | 0.15424 | 1 | 3240 |  |  |  | 2160 | 0.15424 | 3 | Each (9'x100' Panel) | [60 empty] | 2.25 | 2.52 | 3.24 | LogNormal | 2.52 | 0.29375 | 1 | 3.0203 |  |  |  | 2.0197 | 0.29375 | 3 | Each (9'x100' Panel) | [60 empty] | 900
| C3011.001c |  | C3011.001c | Wall Partition, Type: Gypsum + Wallpaper, Full Height, Fixed Below, Slip Track Above w/ returns (friction connection) | 2400 | 2700 | 3500 | LogNormal | 2828.8612 | 0.15424 | 1 | 3240 |  |  |  | 2160 | 0.15424 | 3 | Each (9'x100' Panel) | [60 empty] | 2.25 | 2.52 | 3.24 | LogNormal | 2.52 | 0.29375 | 1 | 3.0203 |  |  |  | 2.0197 | 0.29375 | 3 | Each (9'x100' Panel) | [60 empty] | 900
| C3011.001d |  | C3011.001d | Wall Partition, Type: Gypsum + Wallpaper, Full Height, Fixed Below, Slip Track Above w/o returns (friction connection) | 2400 | 2700 | 3500 | LogNormal | 2828.8612 | 0.15424 | 1 | 3240 |  |  |  | 2160 | 0.15424 | 3 | Each (9'x100' Panel) | [60 empty] | 2.25 | 2.52 | 3.24 | LogNormal | 2.52 | 0.29375 | 1 | 3.0203 |  |  |  | 2.0197 | 0.29375 | 3 | Each (9'x100' Panel) | [60 empty] | 900
| C3011.002a |  | C3011.002a | Wall Partition, Type: Gypsum + Ceramic Tile, Full Height, Fixed Below, Fixed Above | 5000 | 7200 | 9000 | Normal | 7066.6433 | 0.22084 | 1 | 8640 |  |  |  | 5760 | 0.22084 | 3 | Each (9'x100' Panel) | 27000 | 29160 | 34200 | LogNormal | 29970.4235 | 0.09478 | 1 | 34992 |  |  |  | 23328 | 0.09478 | 3 | Each (9'x100' Panel) | [45 empty] | 4.59 | 6.66 | 8.37 | Normal | 6.66 | 0.33357 | 1 | 7.9941 |  |  |  | 5.3259 | 0.33357 | 3 | Each (9'x100' Panel) | 25.02 | 27 | 31.68 | LogNormal | 27 | 0.26736 | 1 | 32.4032 |  |  |  | 21.5968 | 0.26736 | 3 | Each (9'x100' Panel) | [45 empty] | 900
| C3011.002b |  | C3011.002b | Wall Partition, Type: Gypsum + Ceramic Tile, Partial Height, Fixed Below, Lateral Braced Above | 5000 | 7200 | 9000 | Normal | 7066.6433 | 0.22084 | 1 | 8640 |  |  |  | 5760 | 0.22084 | 3 | Each (9'x100' Panel) | 27000 | 29160 | 34200 | LogNormal | 29970.4235 | 0.09478 | 1 | 34992 |  |  |  | 23328 | 0.09478 | 3 | Each (9'x100' Panel) | [45 empty] | 4.59 | 6.66 | 8.37 | Normal | 6.66 | 0.33357 | 1 | 7.9941 |  |  |  | 5.3259 | 0.33357 | 3 | Each (9'x100' Panel) | 25.02 | 27 | 31.68 | LogNormal | 27 | 0.26736 | 1 | 32.4032 |  |  |  | 21.5968 | 0.26736 | 3 | Each (9'x100' Panel) | [45 empty] | 900
| C3011.002c |  | C3011.002c | Wall Partition, Type: Gypsum + Ceramic Tile, Full Height, Fixed Below, Slip Track Above w/ returns (friction connection) | 5000 | 7200 | 9000 | Normal | 7066.6433 | 0.22084 | 1 | 8640 |  |  |  | 5760 | 0.22084 | 3 | Each (9'x100' Panel) | 27000 | 29160 | 34200 | LogNormal | 29970.4235 | 0.09478 | 1 | 34992 |  |  |  | 23328 | 0.09478 | 3 | Each (9'x100' Panel) | [45 empty] | 4.59 | 6.66 | 8.37 | Normal | 6.66 | 0.33357 | 1 | 7.9941 |  |  |  | 5.3259 | 0.33357 | 3 | Each (9'x100' Panel) | 25.02 | 27 | 31.68 | LogNormal | 27 | 0.26736 | 1 | 32.4032 |  |  |  | 21.5968 | 0.26736 | 3 | Each (9'x100' Panel) | [45 empty] | 900
| C3011.002d |  | C3011.002d | Wall Partition, Type: Gypsum + Ceramic Tile, Full Height, Fixed Below, Slip Track Above w/o returns (friction connection) | 5000 | 7200 | 9000 | Normal | 7066.6433 | 0.22084 | 1 | 8640 |  |  |  | 5760 | 0.22084 | 3 | Each (9'x100' Panel) | 27000 | 29160 | 34200 | LogNormal | 29970.4235 | 0.09478 | 1 | 34992 |  |  |  | 23328 | 0.09478 | 3 | Each (9'x100' Panel) | [45 empty] | 4.59 | 6.66 | 8.37 | Normal | 6.66 | 0.33357 | 1 | 7.9941 |  |  |  | 5.3259 | 0.33357 | 3 | Each (9'x100' Panel) | 25.02 | 27 | 31.68 | LogNormal | 27 | 0.26736 | 1 | 32.4032 |  |  |  | 21.5968 | 0.26736 | 3 | Each (9'x100' Panel) | [45 empty] | 900
| C3011.003a |  | C3011.003a | Wall Partition, Type: High End Marble or Wood Panel, Full Height, Fixed Below, Fixed Above | 12000 | 18000 | 24000 | Normal | 17999.9939 | 0.2601 | 1 | 36000 |  |  |  | 10800 | 0.2601 | 3 | Each (9'x100' Panel) | 25000 | 45000 | 60000 | Normal | 43333.3111 | 0.31512 | 1 | 90000 |  |  |  | 27000 | 0.31512 | 3 | Each (9'x100' Panel) | [45 empty] | 11.16 | 16.65 | 22.23 | Normal | 16.65 | 0.36077 | 1 | 33.3265 |  |  |  | 9.9794 | 0.36077 | 3 | Each (9'x100' Panel) | 23.13 | 41.67 | 55.62 | Normal | 41.67 | 0.40225 | 1 | 83.3612 |  |  |  | 24.9935 | 0.40225 | 3 | Each (9'x100' Panel) | [45 empty] | 900
| C3011.003b |  | C3011.003b | Wall Partition, Type: High End Marble or Wood Panel, Partial Height, Fixed Below, Lateral Braced Above | 12000 | 18000 | 24000 | Normal | 17999.9939 | 0.2601 | 1 | 36000 |  |  |  | 10800 | 0.2601 | 3 | Each (9'x100' Panel) | 25000 | 45000 | 60000 | Normal | 43333.3111 | 0.31512 | 1 | 90000 |  |  |  | 27000 | 0.31512 | 3 | Each (9'x100' Panel) | [45 empty] | 11.16 | 16.65 | 22.23 | Normal | 16.65 | 0.36077 | 1 | 33.3265 |  |  |  | 9.9794 | 0.36077 | 3 | Each (9'x100' Panel) | 23.13 | 41.67 | 55.62 | Normal | 41.67 | 0.40225 | 1 | 83.3612 |  |  |  | 24.9935 | 0.40225 | 3 | Each (9'x100' Panel) | [45 empty] | 900
| C3011.003c |  | C3011.003c | Wall Partition, Type: High End Marble or Wood Panel, Full Height, Fixed Below, Slip Track Above w/ returns (friction connection) | 12000 | 18000 | 24000 | Normal | 17999.9939 | 0.2601 | 1 | 36000 |  |  |  | 10800 | 0.2601 | 3 | Each (9'x100' Panel) | 25000 | 45000 | 60000 | Normal | 43333.3111 | 0.31512 | 1 | 90000 |  |  |  | 27000 | 0.31512 | 3 | Each (9'x100' Panel) | [45 empty] | 11.16 | 16.65 | 22.23 | Normal | 16.65 | 0.36077 | 1 | 33.3265 |  |  |  | 9.9794 | 0.36077 | 3 | Each (9'x100' Panel) | 23.13 | 41.67 | 55.62 | Normal | 41.67 | 0.40225 | 1 | 83.3612 |  |  |  | 24.9935 | 0.40225 | 3 | Each (9'x100' Panel) | [45 empty] | 900
| C3011.003d |  | C3011.003d | Wall Partition, Type: High End Marble or Wood Panel, Full Height, Fixed Below, Slip Track Above w/o returns (friction connection) | 12000 | 18000 | 24000 | Normal | 17999.9939 | 0.2601 | 1 | 36000 |  |  |  | 10800 | 0.2601 | 3 | Each (9'x100' Panel) | 25000 | 45000 | 60000 | Normal | 43333.3111 | 0.31512 | 1 | 90000 |  |  |  | 27000 | 0.31512 | 3 | Each (9'x100' Panel) | [45 empty] | 11.16 | 16.65 | 22.23 | Normal | 16.65 | 0.36077 | 1 | 33.3265 |  |  |  | 9.9794 | 0.36077 | 3 | Each (9'x100' Panel) | 23.13 | 41.67 | 55.62 | Normal | 41.67 | 0.40225 | 1 | 83.3612 |  |  |  | 24.9935 | 0.40225 | 3 | Each (9'x100' Panel) | [45 empty] | 900
| C3021.001a |  | C3021.001a | Generic Floor Covering - Flooding of floor caused by failure of pipe - Office - Dry | 18.432 | 31.04 | 40.288 | Normal | 29.92 | 0.285 | 500 | 62.08 |  |  |  | 18.624 | 0.285 | 2000 | Each (1'x1') | [60 empty] | 0.0171 | 0.0288 | 0.0373 | Normal | 0.0288 | 0.37911 | 500 | 0.057558 |  |  |  | 0.017297 | 0.37911 | 2000 | Each (1'x1') | [60 empty] | 1
| C3021.001b |  | C3021.001b | Generic Floor Covering - Flooding of floor caused by failure of pipe - Office - Humid | 36.192 | 53.24 | 71.536 | Normal | 53.656 | 0.257 | 500 | 106.48 |  |  |  | 31.944 | 0.257 | 2000 | Each (1'x1') | [60 empty] | 0.0335 | 0.0493 | 0.0663 | Normal | 0.0493 | 0.35854 | 500 | 0.098625 |  |  |  | 0.02957 | 0.35854 | 2000 | Each (1'x1') | [60 empty] | 1
| C3021.001c |  | C3021.001c | Generic Floor Covering - Flooding of floor caused by failure of pipe - Laboratory - Dry | 23.4 | 44.25 | 56.49 | Normal | 41.3799 | 0.31198 | 500 | 88.5 |  |  |  | 26.55 | 0.31198 | 2000 | Each (1'x1') | [60 empty] | 0.0217 | 0.041 | 0.0523 | Normal | 0.041 | 0.39979 | 500 | 0.081996 |  |  |  | 0.024601 | 0.39979 | 2000 | Each (1'x1') | [60 empty] | 1
| C3021.001d |  | C3021.001d | Generic Floor Covering - Flooding of floor caused by failure of pipe - Laboratory - Humid | 68.64 | 100.8 | 135.87 | Normal | 101.7701 | 0.25773 | 500 | 201.6 |  |  |  | 60.48 | 0.25773 | 2000 | Each (1'x1') | [60 empty] | 0.0636 | 0.0934 | 0.1259 | Normal | 0.0934 | 0.35906 | 500 | 0.18679 |  |  |  | 0.056045 | 0.35906 | 2000 | Each (1'x1') | [60 empty] | 1
| C3021.001e |  | C3021.001e | Generic Floor Covering - Flooding of floor caused by failure of pipe - Hospital - Dry | 24.48 | 38.6 | 49.54 | Normal | 37.5399 | 0.26045 | 500 | 77.2 |  |  |  | 23.16 | 0.26045 | 2000 | Each (1'x1') | [60 empty] | 0.0227 | 0.0358 | 0.0459 | Normal | 0.0358 | 0.36102 | 500 | 0.071562 |  |  |  | 0.021495 | 0.36102 | 2000 | Each (1'x1') | [60 empty] | 1
| C3021.001f |  | C3021.001f | Generic Floor Covering - Flooding of floor caused by failure of pipe - Hospital - Humid | 83.04 | 111.8 | 152.32 | LogNormal | 112.2176 | 0.23763 | 500 | 223.6 |  |  |  | 67.08 | 0.23763 | 2000 | Each (1'x1') | [60 empty] | 0.0769 | 0.1036 | 0.1411 | LogNormal | 0.1036 | 0.34492 | 500 | 0.20718 |  |  |  | 0.062168 | 0.34492 | 2000 | Each (1'x1') | [60 empty] | 1
| C3021.001g |  | C3021.001g | Generic Floor Covering - Flooding of floor caused by failure of pipe - School - Dry | 12.288 | 17.36 | 22.532 | Normal | 17.3933 | 0.22978 | 500 | 34.72 |  |  |  | 10.416 | 0.22978 | 2000 | Each (1'x1') | [60 empty] | 0.0114 | 0.0161 | 0.0209 | Normal | 0.0161 | 0.33956 | 500 | 0.032184 |  |  |  | 0.0096666 | 0.33956 | 2000 | Each (1'x1') | [60 empty] | 1
| C3021.001h |  | C3021.001h | Generic Floor Covering - Flooding of floor caused by failure of pipe - School - Humid | 30.56 | 46.2 | 62.08 | Normal | 46.28 | 0.26572 | 500 | 92.4 |  |  |  | 27.72 | 0.26572 | 2000 | Each (1'x1') | [60 empty] | 0.0283 | 0.0428 | 0.0575 | Normal | 0.0428 | 0.36484 | 500 | 0.085603 |  |  |  | 0.025679 | 0.36484 | 2000 | Each (1'x1') | [60 empty] | 1
| C3021.001i |  | C3021.001i | Generic Floor Covering - Flooding of floor caused by failure of pipe - Apartments - Dry | 16.4 | 26.5 | 34.6 | Normal | 25.8333 | 0.27487 | 500 | 53 |  |  |  | 15.9 | 0.27487 | 2000 | Each (1'x1') | [60 empty] | 0.0152 | 0.0246 | 0.0321 | Normal | 0.0246 | 0.37155 | 500 | 0.049151 |  |  |  | 0.014779 | 0.37155 | 2000 | Each (1'x1') | [60 empty] | 1
| C3021.001j |  | C3021.001j | Generic Floor Covering - Flooding of floor caused by failure of pipe - Apartments - Humid | 52.32 | 73.4 | 100.16 | LogNormal | 72.772 | 0.25103 | 500 | 146.8 |  |  |  | 44.04 | 0.25103 | 2000 | Each (1'x1') | [60 empty] | 0.0485 | 0.068 | 0.0928 | LogNormal | 0.068 | 0.35428 | 500 | 0.136 |  |  |  | 0.040799 | 0.35428 | 2000 | Each (1'x1') | [60 empty] | 1
| C3021.001k |  | C3021.001k | Generic Floor Covering - Flooding of floor caused by failure of pipe - Retail - Dry | 13.92 | 29.4 | 37.9 | Normal | 27.0732 | 0.34557 | 500 | 58.8 |  |  |  | 17.64 | 0.34557 | 2000 | Each (1'x1') | [60 empty] | 0.0129 | 0.0272 | 0.0351 | Normal | 0.0272 | 0.42652 | 500 | 0.054438 |  |  |  | 0.016305 | 0.42652 | 2000 | Each (1'x1') | [60 empty] | 1
| C3021.001l |  | C3021.001l | Generic Floor Covering - Flooding of floor caused by failure of pipe - Retail - Humid | 29.92 | 49.4 | 65.96 | Normal | 48.4266 | 0.29036 | 500 | 98.8 |  |  |  | 29.64 | 0.29036 | 2000 | Each (1'x1') | [60 empty] | 0.0277 | 0.0458 | 0.0611 | Normal | 0.0458 | 0.38316 | 500 | 0.091568 |  |  |  | 0.027493 | 0.38316 | 2000 | Each (1'x1') | [60 empty] | 1
| C3021.001m |  | C3021.001m | Generic Floor Covering - Flooding of floor caused by failure of pipe - Warehouse - Dry | 4.04 | 10.05 | 13.47 | Normal | 9.1864 | 0.40052 | 500 | 20.1 |  |  |  | 6.03 | 0.40052 | 2000 | Each (1'x1') | [60 empty] | 0.0037 | 0.0093 | 0.0125 | Normal | 0.0093 | 0.47214 | 500 | 0.018611 |  |  |  | 0.0055756 | 0.47214 | 2000 | Each (1'x1') | [60 empty] | 1
| C3021.001n |  | C3021.001n | Generic Floor Covering - Flooding of floor caused by failure of pipe - Warehouse - Humid | 12.8 | 24 | 32.6 | Normal | 23.1333 | 0.33393 | 500 | 48 |  |  |  | 14.4 | 0.33393 | 2000 | Each (1'x1') | [60 empty] | 0.0119 | 0.0222 | 0.0302 | Normal | 0.0222 | 0.41715 | 500 | 0.044435 |  |  |  | 0.013306 | 0.41715 | 2000 | Each (1'x1') | [60 empty] | 1
| C3021.001o |  | C3021.001o | Generic Floor Covering - Flooding of floor caused by failure of pipe - Hospitality - Dry | 14.32 | 27.9 | 35.7 | Normal | 25.9732 | 0.32115 | 500 | 55.8 |  |  |  | 16.74 | 0.32115 | 2000 | Each (1'x1') | [60 empty] | 0.0139 | 0.0271 | 0.0347 | Normal | 0.0271 | 0.40699 | 500 | 0.054179 |  |  |  | 0.016268 | 0.40699 | 2000 | Each (1'x1') | [60 empty] | 1
| C3021.001p |  | C3021.001p | Generic Floor Covering - Flooding of floor caused by failure of pipe - Hospitality - Humid | 48.16 | 70.2 | 95.18 | Normal | 71.18 | 0.25773 | 500 | 84.24 |  |  |  | 56.16 | 0.25773 | 2000 | Each (1'x1') | [60 empty] | 0.0467 | 0.0681 | 0.0924 | Normal | 0.0681 | 0.35906 | 500 | 0.081727 |  |  |  | 0.054473 | 0.35906 | 2000 | Each (1'x1') | [60 empty] | 1
| C3027.001 |  | C3027.001 | Raised Access Floor, non seismically rated. | 40 | 115 | 630 | LogNormal | 121.399 | 1.2841 | 5 | 138 |  |  |  | 92 | 1.2841 | 20 | 100 ft^2 Units | [60 empty] | 0.04 | 0.11 | 0.61 | LogNormal | 0.11 | 1.3082 | 5 | 0.13232 |  |  |  | 0.087676 | 1.3082 | 20 | 100 ft^2 Units | [60 empty] | 100
| C3027.002 |  | C3027.002 | Raised Access Floor, seismically rated. | 40 | 115 | 630 | LogNormal | 121.399 | 1.2841 | 5 | 138 |  |  |  | 92 | 1.2841 | 20 | 100 ft^2 Units | [60 empty] | 0.04 | 0.12 | 0.68 | LogNormal | 0.12 | 1.3082 | 5 | 0.14469 |  |  |  | 0.095309 | 1.3082 | 20 | 100 ft^2 Units | [60 empty] | 100
| C3032.001a |  | C3032.001a | Suspended Ceiling, SDC A,B,C, Area (A): A < 250, Vert support only | 100 | 362.5 | 600 | Normal | 354.166 | 0.5508 | 1 | 435 |  |  |  | 290 | 0.5508 | 10 | 250 ft^2 Units | 1350 | 2837.5 | 5350 | LogNormal | 2763.2552 | 0.51832 | 1 | 3405 |  |  |  | 2270 | 0.51832 | 10 | 250 ft^2 Units | 4687.5 | 5837.5 | 7787.5 | LogNormal | 5967.8107 | 0.20262 | 1 | 7005 |  |  |  | 4670 | 0.20262 | 10 | 250 ft^2 Units | [30 empty] | 0.1 | 0.35 | 0.575 | Normal | 0.35 | 0.60488 | 1 | 0.4193 |  |  |  | 0.2807 | 0.60488 | 10 | 250 ft^2 Units | 1.3 | 2.7 | 5.125 | LogNormal | 2.7 | 0.57546 | 1 | 3.2425 |  |  |  | 2.1575 | 0.57546 | 10 | 250 ft^2 Units | 4.475 | 5.575 | 7.45 | LogNormal | 5.575 | 0.3218 | 1 | 6.691 |  |  |  | 4.459 | 0.3218 | 10 | 250 ft^2 Units | [30 empty] | 250
| C3032.001b |  | C3032.001b | Suspended Ceiling, SDC A,B,C, Area (A): 250 < A < 1000, Vert support only | 240 | 870 | 1440 | Normal | 849.9996 | 0.5508 | 1 | 1044 |  |  |  | 696 | 0.5508 | 10 | 600 ft^2 Units | 3240 | 6810 | 12840 | LogNormal | 6631.8105 | 0.51832 | 1 | 8172 |  |  |  | 5448 | 0.51832 | 10 | 600 ft^2 Units | 11250 | 14010 | 18690 | LogNormal | 14322.739 | 0.20262 | 1 | 16812 |  |  |  | 11208 | 0.20262 | 10 | 600 ft^2 Units | [30 empty] | 0.24 | 0.78 | 1.32 | Normal | 0.78 | 0.60488 | 1 | 0.93865 |  |  |  | 0.62135 | 0.60488 | 10 | 600 ft^2 Units | 2.94 | 6.18 | 11.7 | LogNormal | 6.18 | 0.57546 | 1 | 7.4218 |  |  |  | 4.9382 | 0.57546 | 10 | 600 ft^2 Units | 10.26 | 12.78 | 17.04 | LogNormal | 12.78 | 0.3218 | 1 | 15.3348 |  |  |  | 10.2252 | 0.3218 | 10 | 600 ft^2 Units | [30 empty] | 600
| C3032.001c |  | C3032.001c | Suspended Ceiling, SDC A,B,C, Area (A): 1000 < A < 2500, Vert support only | 720 | 2610 | 4320 | Normal | 2549.9987 | 0.5508 | 1 | 3132 |  |  |  | 2088 | 0.5508 | 10 | 1800 ft^2 Units | 9720 | 20430 | 38520 | LogNormal | 19895.4195 | 0.51832 | 1 | 24516 |  |  |  | 16344 | 0.51832 | 10 | 1800 ft^2 Units | 33750 | 42030 | 56070 | LogNormal | 42968.2297 | 0.20262 | 1 | 50436 |  |  |  | 33624 | 0.20262 | 10 | 1800 ft^2 Units | [30 empty] | 0.72 | 2.34 | 3.78 | Normal | 2.34 | 0.60488 | 1 | 2.8006 |  |  |  | 1.8794 | 0.60488 | 10 | 1800 ft^2 Units | 8.64 | 18 | 34.02 | LogNormal | 18 | 0.57546 | 1 | 21.6053 |  |  |  | 14.3947 | 0.57546 | 10 | 1800 ft^2 Units | 29.7 | 37.08 | 49.5 | LogNormal | 37.08 | 0.3218 | 1 | 44.4971 |  |  |  | 29.6629 | 0.3218 | 10 | 1800 ft^2 Units | [30 empty] | 1800
| C3032.001d |  | C3032.001d | Suspended Ceiling, SDC A,B,C, Area (A): A > 2500, Vert support only | 1000 | 3625 | 6000 | Normal | 3541.6648 | 0.5508 | 1 | 4350 |  |  |  | 2900 | 0.5508 | 10 | 2500 ft^2 Units | 13500 | 28375 | 53500 | LogNormal | 27632.5627 | 0.51832 | 1 | 34050 |  |  |  | 22700 | 0.51832 | 10 | 2500 ft^2 Units | 46875 | 58375 | 77875 | LogNormal | 59678.1026 | 0.20262 | 1 | 70050 |  |  |  | 46700 | 0.20262 | 10 | 2500 ft^2 Units | [30 empty] | 0.75 | 3 | 5 | Normal | 3 | 0.60488 | 1 | 3.6184 |  |  |  | 2.3816 | 0.60488 | 10 | 2500 ft^2 Units | 11.5 | 24.25 | 45.75 | LogNormal | 24.25 | 0.57546 | 1 | 29.0904 |  |  |  | 19.4096 | 0.57546 | 10 | 2500 ft^2 Units | 40 | 49.75 | 66.5 | LogNormal | 49.75 | 0.3218 | 1 | 59.7081 |  |  |  | 39.7919 | 0.3218 | 10 | 2500 ft^2 Units | [30 empty] | 2500
| C3032.003a |  | C3032.003a | Suspended Ceiling, SDC D,E (Ip=1.0), Area (A): A < 250, Vert & Lat support | 100 | 362.5 | 600 | Normal | 354.166 | 0.5508 | 1 | 725 |  |  |  | 217.5 | 0.5508 | 10 | 250 ft^2 Units | 1350 | 2837.5 | 5350 | LogNormal | 2763.2552 | 0.51832 | 1 | 5675 |  |  |  | 1702.5 | 0.51832 | 10 | 250 ft^2 Units | 4687.5 | 5837.5 | 7787.5 | LogNormal | 5967.8107 | 0.20262 | 1 | 11675 |  |  |  | 3502.5 | 0.20262 | 10 | 250 ft^2 Units | [30 empty] | 0.1 | 0.35 | 0.575 | Normal | 0.35 | 0.60488 | 1 | 0.69651 |  |  |  | 0.2114 | 0.60488 | 10 | 250 ft^2 Units | 1.3 | 2.7 | 5.125 | LogNormal | 2.7 | 0.57546 | 1 | 5.4123 |  |  |  | 1.6151 | 0.57546 | 10 | 250 ft^2 Units | 4.475 | 5.575 | 7.45 | LogNormal | 5.575 | 0.3218 | 1 | 11.155 |  |  |  | 3.343 | 0.3218 | 10 | 250 ft^2 Units | [30 empty] | 250
| C3032.003b |  | C3032.003b | Suspended Ceiling, SDC D,E (Ip=1.0), Area (A): 250 < A < 1000, Vert & Lat support | 240 | 870 | 1440 | Normal | 849.9996 | 0.5508 | 1 | 1740 |  |  |  | 522 | 0.5508 | 10 | 600 ft^2 Units | 3240 | 6810 | 12840 | LogNormal | 6631.8105 | 0.51832 | 1 | 13620 |  |  |  | 4086 | 0.51832 | 10 | 600 ft^2 Units | 11250 | 14010 | 18690 | LogNormal | 14322.739 | 0.20262 | 1 | 28020 |  |  |  | 8406 | 0.20262 | 10 | 600 ft^2 Units | [30 empty] | 0.24 | 0.78 | 1.32 | Normal | 0.78 | 0.60488 | 1 | 1.5732 |  |  |  | 0.46271 | 0.60488 | 10 | 600 ft^2 Units | 2.94 | 6.18 | 11.7 | LogNormal | 6.18 | 0.57546 | 1 | 12.3891 |  |  |  | 3.6964 | 0.57546 | 10 | 600 ft^2 Units | 10.26 | 12.78 | 17.04 | LogNormal | 12.78 | 0.3218 | 1 | 25.5538 |  |  |  | 7.6705 | 0.3218 | 10 | 600 ft^2 Units | [30 empty] | 600
| C3032.003c |  | C3032.003c | Suspended Ceiling, SDC D,E (Ip=1.0), Area (A): 1000 < A < 2500, Vert & Lat support | 720 | 2610 | 4320 | Normal | 2549.9987 | 0.5508 | 1 | 5220 |  |  |  | 1566 | 0.5508 | 10 | 1800 ft^2 Units | 9720 | 20430 | 38520 | LogNormal | 19895.4195 | 0.51832 | 1 | 40860 |  |  |  | 12258 | 0.51832 | 10 | 1800 ft^2 Units | 33750 | 42030 | 56070 | LogNormal | 42968.2297 | 0.20262 | 1 | 84060 |  |  |  | 25218 | 0.20262 | 10 | 1800 ft^2 Units | [30 empty] | 0.72 | 2.34 | 3.78 | Normal | 2.34 | 0.60488 | 1 | 4.6429 |  |  |  | 1.4188 | 0.60488 | 10 | 1800 ft^2 Units | 8.64 | 18 | 34.02 | LogNormal | 18 | 0.57546 | 1 | 36.0265 |  |  |  | 10.7894 | 0.57546 | 10 | 1800 ft^2 Units | 29.7 | 37.08 | 49.5 | LogNormal | 37.08 | 0.3218 | 1 | 74.1653 |  |  |  | 22.2459 | 0.3218 | 10 | 1800 ft^2 Units | [30 empty] | 1800
| C3032.003d |  | C3032.003d | Suspended Ceiling, SDC D,E (Ip=1.0), Area (A): A > 2500, Vert & Lat support | 1000 | 3625 | 6000 | Normal | 3541.6648 | 0.5508 | 1 | 7250 |  |  |  | 2175 | 0.5508 | 10 | 2500 ft^2 Units | 13500 | 28375 | 53500 | LogNormal | 27632.5627 | 0.51832 | 1 | 56750 |  |  |  | 17025 | 0.51832 | 10 | 2500 ft^2 Units | 46875 | 58375 | 77875 | LogNormal | 59678.1026 | 0.20262 | 1 | 116750 |  |  |  | 35025 | 0.20262 | 10 | 2500 ft^2 Units | [30 empty] | 0.75 | 3 | 5 | Normal | 3 | 0.60488 | 1 | 6.0919 |  |  |  | 1.7632 | 0.60488 | 10 | 2500 ft^2 Units | 11.5 | 24.25 | 45.75 | LogNormal | 24.25 | 0.57546 | 1 | 48.4522 |  |  |  | 14.5691 | 0.57546 | 10 | 2500 ft^2 Units | 40 | 49.75 | 66.5 | LogNormal | 49.75 | 0.3218 | 1 | 99.5404 |  |  |  | 29.8338 | 0.3218 | 10 | 2500 ft^2 Units | [30 empty] | 2500
| C3032.004a |  | C3032.004a | Suspended Ceiling, SDC D,E,F (Ip=1.5), Area (A): A < 250, Vert & Lat support | 100 | 362.5 | 600 | Normal | 354.166 | 0.5508 | 1 | 725 |  |  |  | 217.5 | 0.5508 | 10 | 250 ft^2 Units | 1350 | 2837.5 | 5350 | LogNormal | 2763.2552 | 0.51832 | 1 | 5675 |  |  |  | 1702.5 | 0.51832 | 10 | 250 ft^2 Units | 4687.5 | 5837.5 | 7787.5 | LogNormal | 5967.8107 | 0.20262 | 1 | 11675 |  |  |  | 3502.5 | 0.20262 | 10 | 250 ft^2 Units | [30 empty] | 0.1 | 0.35 | 0.575 | Normal | 0.35 | 0.60488 | 1 | 0.69651 |  |  |  | 0.2114 | 0.60488 | 10 | 250 ft^2 Units | 1.3 | 2.7 | 5.125 | LogNormal | 2.7 | 0.57546 | 1 | 5.4123 |  |  |  | 1.6151 | 0.57546 | 10 | 250 ft^2 Units | 4.475 | 5.575 | 7.45 | LogNormal | 5.575 | 0.3218 | 1 | 11.155 |  |  |  | 3.343 | 0.3218 | 10 | 250 ft^2 Units | [30 empty] | 250
| C3032.004b |  | C3032.004b | Suspended Ceiling, SDC D,E,F (Ip=1.5), Area (A): 250 < A < 1000, Vert & Lat support | 240 | 870 | 1440 | Normal | 849.9996 | 0.5508 | 1 | 1740 |  |  |  | 522 | 0.5508 | 10 | 600 ft^2 Units | 3240 | 6810 | 12840 | LogNormal | 6631.8105 | 0.51832 | 1 | 13620 |  |  |  | 4086 | 0.51832 | 10 | 600 ft^2 Units | 11250 | 14010 | 18690 | LogNormal | 14322.739 | 0.20262 | 1 | 28020 |  |  |  | 8406 | 0.20262 | 10 | 600 ft^2 Units | [30 empty] | 0.24 | 0.78 | 1.32 | Normal | 0.78 | 0.60488 | 1 | 1.5732 |  |  |  | 0.46271 | 0.60488 | 10 | 600 ft^2 Units | 2.94 | 6.18 | 11.7 | LogNormal | 6.18 | 0.57546 | 1 | 12.3891 |  |  |  | 3.6964 | 0.57546 | 10 | 600 ft^2 Units | 10.26 | 12.78 | 17.04 | LogNormal | 12.78 | 0.3218 | 1 | 25.5538 |  |  |  | 7.6705 | 0.3218 | 10 | 600 ft^2 Units | [30 empty] | 600
| C3032.004c |  | C3032.004c | Suspended Ceiling, SDC D,E,F (Ip=1.5), Area (A): 1000 < A < 2500, Vert & Lat support | 720 | 2610 | 4320 | Normal | 2549.9987 | 0.5508 | 1 | 5220 |  |  |  | 1566 | 0.5508 | 10 | 1800 ft^2 Units | 9720 | 20430 | 38520 | LogNormal | 19895.4195 | 0.51832 | 1 | 40860 |  |  |  | 12258 | 0.51832 | 10 | 1800 ft^2 Units | 33750 | 42030 | 56070 | LogNormal | 42968.2297 | 0.20262 | 1 | 84060 |  |  |  | 25218 | 0.20262 | 10 | 1800 ft^2 Units | [30 empty] | 0.72 | 2.34 | 3.78 | Normal | 2.34 | 0.60488 | 1 | 4.6429 |  |  |  | 1.4188 | 0.60488 | 10 | 1800 ft^2 Units | 8.64 | 18 | 34.02 | LogNormal | 18 | 0.57546 | 1 | 36.0265 |  |  |  | 10.7894 | 0.57546 | 10 | 1800 ft^2 Units | 29.7 | 37.08 | 49.5 | LogNormal | 37.08 | 0.3218 | 1 | 74.1653 |  |  |  | 22.2459 | 0.3218 | 10 | 1800 ft^2 Units | [30 empty] | 1800
| C3032.004d |  | C3032.004d | Suspended Ceiling, SDC D,E,F (Ip=1.5), Area (A): A > 2500, Vert & Lat support | 1000 | 3625 | 6000 | Normal | 3541.6648 | 0.5508 | 1 | 7250 |  |  |  | 2175 | 0.5508 | 10 | 2500 ft^2 Units | 13500 | 28375 | 53500 | LogNormal | 27632.5627 | 0.51832 | 1 | 56750 |  |  |  | 17025 | 0.51832 | 10 | 2500 ft^2 Units | 46875 | 58375 | 77875 | LogNormal | 59678.1026 | 0.20262 | 1 | 116750 |  |  |  | 35025 | 0.20262 | 10 | 2500 ft^2 Units | [30 empty] | 0.75 | 3 | 5 | Normal | 3 | 0.60488 | 1 | 6.0919 |  |  |  | 1.7632 | 0.60488 | 10 | 2500 ft^2 Units | 11.5 | 24.25 | 45.75 | LogNormal | 24.25 | 0.57546 | 1 | 48.4522 |  |  |  | 14.5691 | 0.57546 | 10 | 2500 ft^2 Units | 40 | 49.75 | 66.5 | LogNormal | 49.75 | 0.3218 | 1 | 99.5404 |  |  |  | 29.8338 | 0.3218 | 10 | 2500 ft^2 Units | [30 empty] | 2500
| C3034.001 |  | C3034.001 | Independent Pendant Lighting - non seismic | 200 | 495 | 1090 | LogNormal | 483.0323 | 0.63694 | 5 | 2.3 |  |  |  | 0.69 | 0.63694 | 10 | Each | [60 empty] | 0.0004 | 0.0011 | 0.0061 | LogNormal | 0.0011 | 0.68425 | 5 | 0.00225 |  |  |  | 0.00064 | 0.68425 | 10 | Each | [60 empty] | 1
| C3034.002 |  | C3034.002 | Independent Pendant Lighting - seismically rated | 200 | 495 | 1090 | LogNormal | 483.0323 | 0.63694 | 5 | 990 |  |  |  | 297 | 0.63694 | 10 | Each | [60 empty] | 0.2 | 0.495 | 1.09 | LogNormal | 0.495 | 0.68425 | 5 | 0.99 |  |  |  | 0.297 | 0.68425 | 10 | Each | [60 empty] | 1
| D1014.011 |  | D1014.011 | Traction Elevator – Applies to most California Installations 1976 or later, most western states installations 1982 or later and most other U.S installations 1998 or later. | 1500 | 4400 | 13600 | LogNormal | 4434.7814 | 0.87408 | 5 | 8800 |  |  |  | 2640 | 0.87408 | 10 | Each | 11400 | 18700 | 24300 | Normal | 18133.1362 | 0.27755 | 5 | 37400 |  |  |  | 11220 | 0.27755 | 10 | Each | 6000 | 16000 | 21000 | Normal | 14333.2259 | 0.4083 | 5 | 32000 |  |  |  | 9600 | 0.4083 | 10 | Each | 500 | 2500 | 3000 | Normal | 1999.999 | 0.48769 | 5 | 5000 |  |  |  | 1500 | 0.48769 | 10 | Each | [15 empty] | 1.4338 | 4.2059 | 13 | LogNormal | 4.2059 | 0.90913 | 5 | 8.4118 |  |  |  | 2.5235 | 0.90913 | 10 | Each | 10.8971 | 17.875 | 23.2279 | Normal | 17.875 | 0.37354 | 5 | 35.75 |  |  |  | 10.725 | 0.37354 | 10 | Each | 5.7353 | 15.2941 | 20.0735 | Normal | 15.2941 | 0.47876 | 5 | 30.5882 |  |  |  | 9.1765 | 0.47876 | 10 | Each | 0.4779 | 2.3897 | 2.8676 | Normal | 2.3897 | 0.54803 | 5 | 4.7794 |  |  |  | 1.4338 | 0.54803 | 10 | Each | [15 empty] | 1
| D1014.012 |  | D1014.012 | Traction Elevator – Applies to most California Installations prior to 1976, most western states installations prior to 1982 and most other U.S installations prior to 1998. | 1500 | 4400 | 13600 | LogNormal | 4434.7814 | 0.87408 | 5 | 8800 |  |  |  | 2640 | 0.87408 | 10 | Each | 11400 | 18700 | 24300 | Normal | 18133.1362 | 0.27755 | 5 | 37400 |  |  |  | 11220 | 0.27755 | 10 | Each | 6000 | 16000 | 21000 | Normal | 14333.2259 | 0.4083 | 5 | 32000 |  |  |  | 9600 | 0.4083 | 10 | Each | 500 | 2500 | 3000 | Normal | 1999.999 | 0.48769 | 5 | 5000 |  |  |  | 1500 | 0.48769 | 10 | Each | [15 empty] | 1.4338 | 4.2059 | 13 | LogNormal | 4.2059 | 0.90913 | 5 | 8.4118 |  |  |  | 2.5235 | 0.90913 | 10 | Each | 10.8971 | 17.875 | 23.2279 | Normal | 17.875 | 0.37354 | 5 | 35.75 |  |  |  | 10.725 | 0.37354 | 10 | Each | 5.7353 | 15.2941 | 20.0735 | Normal | 15.2941 | 0.47876 | 5 | 30.5882 |  |  |  | 9.1765 | 0.47876 | 10 | Each | 0.4779 | 2.3897 | 2.8676 | Normal | 2.3897 | 0.54803 | 5 | 4.7794 |  |  |  | 1.4338 | 0.54803 | 10 | Each | [15 empty] | 1
| D1014.021 |  | D1014.021 | Hydraulic Elevator – Applies to most California Installations 1976 or later, most western states installations postdating 1982 and most U.S installations postdating 1998. | 400 | 800 | 2500 | LogNormal | 867.87 | 0.82186 | 5 | 1600 |  |  |  | 480 | 0.82186 | 10 | Each | 4200 | 8200 | 10500 | Normal | 7633.228 | 0.32202 | 5 | 16400 |  |  |  | 4920 | 0.32202 | 10 | Each | 4000 | 12000 | 16000 | Normal | 10666.6545 | 0.43892 | 5 | 24000 |  |  |  | 7200 | 0.43892 | 10 | Each | 2000 | 2300 | 3600 | LogNormal | 2538.9628 | 0.25352 | 5 | 4600 |  |  |  | 1380 | 0.25352 | 10 | Each | [15 empty] | 0.3824 | 0.7647 | 2.3897 | LogNormal | 0.7647 | 0.85904 | 5 | 1.5294 |  |  |  | 0.45882 | 0.85904 | 10 | Each | 4.0147 | 7.8382 | 10.0368 | Normal | 7.8382 | 0.40767 | 5 | 15.6764 |  |  |  | 4.7029 | 0.40767 | 10 | Each | 3.8235 | 11.4706 | 15.2941 | Normal | 11.4706 | 0.50513 | 5 | 22.9412 |  |  |  | 6.8824 | 0.50513 | 10 | Each | 1.9118 | 2.1985 | 3.4412 | LogNormal | 2.1985 | 0.35605 | 5 | 4.397 |  |  |  | 1.3191 | 0.35605 | 10 | Each | [15 empty] | 1
| D1014.022 |  | D1014.022 | Hydraulic Elevator – Applies to most California Installations prior to 1976, most western states installations prior to 1982 and most U.S installations prior to 1998. | 400 | 800 | 2500 | LogNormal | 867.87 | 0.82186 | 5 | 1600 |  |  |  | 480 | 0.82186 | 10 | Each | 4200 | 8200 | 10500 | Normal | 7633.228 | 0.32202 | 5 | 16400 |  |  |  | 4920 | 0.32202 | 10 | Each | 4000 | 12000 | 16000 | Normal | 10666.6545 | 0.43892 | 5 | 24000 |  |  |  | 7200 | 0.43892 | 10 | Each | 2000 | 2300 | 3600 | LogNormal | 2538.9628 | 0.25352 | 5 | 4600 |  |  |  | 1380 | 0.25352 | 10 | Each | [15 empty] | 0.4 | 0.8 | 2.5 | LogNormal | 0.8 | 0.85904 | 5 | 1.6 |  |  |  | 0.48 | 0.85904 | 10 | Each | 4.2 | 8.2 | 10.5 | Normal | 8.2 | 0.40767 | 5 | 16.4 |  |  |  | 4.92 | 0.40767 | 10 | Each | 4 | 12 | 16 | Normal | 12 | 0.50513 | 5 | 24 |  |  |  | 7.2 | 0.50513 | 10 | Each | 2 | 2.3 | 3.6 | LogNormal | 2.3 | 0.35605 | 5 | 4.6 |  |  |  | 1.38 | 0.35605 | 10 | Each | [15 empty] | 1
| D2061.023a |  | D2061.023a | Steam Piping - Large Diameter Welded Steel - (greater than 2.5 inches in diameter), SDC D, E, or F, PIPING FRAGILITY | 150 | 350 | 800 | LogNormal | 348.485 | 0.64877 | 5 | 700 |  |  |  | 210 | 0.64877 | 10 | Each (1000 ft pipe) | 1800 | 3350 | 5350 | LogNormal | 3212.973 | 0.40381 | 5 | 6700 |  |  |  | 2010 | 0.40381 | 10 | Each (1000 ft pipe) | [45 empty] | 0.1588 | 0.3706 | 0.8471 | LogNormal | 0.3706 | 0.69527 | 5 | 0.74119 |  |  |  | 0.22236 | 0.69527 | 10 | Each (1000 ft pipe) | 1.9059 | 3.5471 | 5.6647 | LogNormal | 3.5471 | 0.47493 | 5 | 7.0942 |  |  |  | 2.1283 | 0.47493 | 10 | Each (1000 ft pipe) | [45 empty] | 1
| D2061.023b |  | D2061.023b | Steam Piping - Large Diameter Welded Steel - (greater than 2.5 inches in diameter), SDC D, E, or F, BRACING FRAGILITY | 150 | 350 | 800 | LogNormal | 348.485 | 0.64877 | 5 | 700 |  |  |  | 210 | 0.64877 | 10 | Each (1000 ft pipe) | 150 | 350 | 800 | LogNormal | 348.485 | 0.64877 | 5 | 700 |  |  |  | 210 | 0.64877 | 10 | Each (1000 ft pipe) | [45 empty] | 0.1588 | 0.3706 | 0.8471 | LogNormal | 0.3706 | 0.69527 | 5 | 0.74119 |  |  |  | 0.22236 | 0.69527 | 10 | Each (1000 ft pipe) | 0.1588 | 0.3706 | 0.8471 | LogNormal | 0.3706 | 0.69527 | 5 | 0.74119 |  |  |  | 0.22236 | 0.69527 | 10 | Each (1000 ft pipe) | [45 empty] | 1
| D2061.024a |  | D2061.024a | Steam Piping - Large Diameter Welded Steel - (greater than 2.5 inches in diameter), SDC D, E, or F (OSHPD or sim), PIPING FRAGILITY | 150 | 350 | 800 | LogNormal | 348.485 | 0.64877 | 5 | 700 |  |  |  | 210 | 0.64877 | 10 | Each (1000 ft pipe) | 1800 | 3350 | 5350 | LogNormal | 3212.973 | 0.40381 | 5 | 6700 |  |  |  | 2010 | 0.40381 | 10 | Each (1000 ft pipe) | [45 empty] | 0.1588 | 0.3706 | 0.8471 | LogNormal | 0.3706 | 0.69527 | 5 | 0.74119 |  |  |  | 0.22236 | 0.69527 | 10 | Each (1000 ft pipe) | 1.9059 | 3.5471 | 5.6647 | LogNormal | 3.5471 | 0.47493 | 5 | 7.0942 |  |  |  | 2.1283 | 0.47493 | 10 | Each (1000 ft pipe) | [45 empty] | 1
| D2061.024b |  | D2061.024b | Steam Piping - Large Diameter Welded Steel - (greater than 2.5 inches in diameter), SDC D, E, or F (OSHPD or sim), BRACING FRAGILITY | 150 | 350 | 800 | LogNormal | 348.485 | 0.64877 | 5 | 700 |  |  |  | 210 | 0.64877 | 10 | Each (1000 ft pipe) | 150 | 350 | 800 | LogNormal | 348.485 | 0.64877 | 5 | 700 |  |  |  | 210 | 0.64877 | 10 | Each (1000 ft pipe) | [45 empty] | 0.1588 | 0.3706 | 0.8471 | LogNormal | 0.3706 | 0.69527 | 5 | 0.74119 |  |  |  | 0.22236 | 0.69527 | 10 | Each (1000 ft pipe) | 0.1588 | 0.3706 | 0.8471 | LogNormal | 0.3706 | 0.69527 | 5 | 0.74119 |  |  |  | 0.22236 | 0.69527 | 10 | Each (1000 ft pipe) | [45 empty] | 1
| D3031.011a |  | D3031.011a | Chiller - Capacity: < 100 Ton - Unanchored equipment that is not vibration isolated - Equipment fragility only | 39100 | 46200 | 60800 | LogNormal | 47847.4484 | 0.17848 | 1 | 50820 |  |  |  | 41580 | 0.17848 | 5 | Each | [60 empty] | 8.05 | 9.5118 | 12.5176 | LogNormal | 9.5118 | 0.30717 | 1 | 14.2677 |  |  |  | 4.7559 | 0.30717 | 5 | Each | [60 empty] | 1
| D3031.011b |  | D3031.011b | Chiller - Capacity: 100 to <350 Ton - Unanchored equipment that is not vibration isolated - Equipment fragility only | 130500 | 153000 | 199300 | LogNormal | 158343.6453 | 0.17106 | 1 | 168300 |  |  |  | 137700 | 0.17106 | 5 | Each | [60 empty] | 20.1507 | 23.625 | 30.7743 | LogNormal | 23.625 | 0.30292 | 1 | 39.375 |  |  |  | 11.8125 | 0.30292 | 5 | Each | [60 empty] | 1
| D3031.011c |  | D3031.011c | Chiller - Capacity: 350 to <750 Ton - Unanchored equipment that is not vibration isolated - Equipment fragility only | 217200 | 255200 | 332600 | LogNormal | 263966.9814 | 0.17205 | 1 | 280720 |  |  |  | 229680 | 0.17205 | 5 | Each | [60 empty] | 22.3588 | 26.2706 | 34.2382 | LogNormal | 26.2706 | 0.30348 | 1 | 52.5412 |  |  |  | 13.1353 | 0.30348 | 5 | Each | [60 empty] | 1
| D3031.011d |  | D3031.011d | Chiller - Capacity: 750 to <1000 Ton - Unanchored equipment that is not vibration isolated - Equipment fragility only | 365500 | 431000 | 561800 | LogNormal | 445291.1546 | 0.17337 | 1 | 474100 |  |  |  | 387900 | 0.17337 | 5 | Each | [60 empty] | 26.3375 | 31.0574 | 40.4826 | LogNormal | 31.0574 | 0.30423 | 1 | 75.425 |  |  |  | 15.5287 | 0.30423 | 5 | Each | [60 empty] | 1
| D3031.012a |  | D3031.012a | Chiller - Capacity: < 100 Ton - Vibration isolated equipment that is not snubbed or restrained - Anchorage fragility only | 500 | 1000 | 1700 | LogNormal | 958.6389 | 0.45231 | 1 | 2000 |  |  |  | 600 | 0.45231 | 5 | Each | 39600 | 47200 | 62500 | LogNormal | 48838.5351 | 0.18434 | 1 | 94400 |  |  |  | 28320 | 0.18434 | 5 | Each | [45 empty] | 0.5147 | 1.0294 | 1.75 | LogNormal | 1.0294 | 0.5168 | 1 | 2.0588 |  |  |  | 0.61764 | 0.5168 | 5 | Each | 8.1529 | 9.7176 | 12.8676 | LogNormal | 9.7176 | 0.31061 | 1 | 58.3058 |  |  |  | 4.8588 | 0.31061 | 5 | Each | [45 empty] | 1
| D3031.012b |  | D3031.012b | Chiller - Capacity: < 100 Ton - Vibration isolated equipment that is not snubbed or restrained - Equipment fragility only | 39100 | 46200 | 60800 | LogNormal | 47847.4484 | 0.17848 | 1 | 50820 |  |  |  | 41580 | 0.17848 | 5 | Each | [60 empty] | 8.05 | 9.5118 | 12.5176 | LogNormal | 9.5118 | 0.30717 | 1 | 14.2677 |  |  |  | 4.7559 | 0.30717 | 5 | Each | [60 empty] | 1
| D3031.012c |  | D3031.012c | Chiller - Capacity: < 100 Ton - Vibration isolated equipment that is not snubbed or restrained - Combined anchorage/isolator & equipment fragility | 500 | 1000 | 1700 | LogNormal | 958.6389 | 0.45231 | 1 | 1100 |  |  |  | 900 | 0.45231 | 5 | Each | 39600 | 47200 | 62500 | LogNormal | 48838.5351 | 0.18434 | 1 | 51920 |  |  |  | 42480 | 0.18434 | 5 | Each | 39600 | 47200 | 62500 | LogNormal | 48838.5351 | 0.18434 | 1 | 51920 |  |  |  | 42480 | 0.18434 | 5 | Each | [30 empty] | 0.5147 | 1.0294 | 1.75 | LogNormal | 1.0294 | 0.5168 | 1 | 1.1323 |  |  |  | 0.92646 | 0.5168 | 5 | Each | 8.1529 | 9.7176 | 12.8676 | LogNormal | 9.7176 | 0.31061 | 1 | 14.5764 |  |  |  | 4.8588 | 0.31061 | 5 | Each | 8.1529 | 9.7176 | 12.8676 | LogNormal | 9.7176 | 0.31061 | 1 | 14.5764 |  |  |  | 4.8588 | 0.31061 | 5 | Each | [30 empty] | 1
| D3031.012d |  | D3031.012d | Chiller - Capacity: 100 to <350 Ton - Vibration isolated equipment that is not snubbed or restrained - Anchorage fragility only | 800 | 1500 | 2400 | Normal | 1566.6663 | 0.39845 | 1 | 3000 |  |  |  | 900 | 0.39845 | 5 | Each | 131300 | 154500 | 201700 | LogNormal | 159816.2659 | 0.17334 | 1 | 309000 |  |  |  | 92700 | 0.17334 | 5 | Each | [45 empty] | 0.8235 | 1.5441 | 2.4706 | Normal | 1.5441 | 0.47039 | 1 | 3.0882 |  |  |  | 0.92645 | 0.47039 | 5 | Each | 20.2743 | 23.8566 | 31.1449 | LogNormal | 23.8566 | 0.30422 | 1 | 182.9007 |  |  |  | 11.9283 | 0.30422 | 5 | Each | [45 empty] | 1
| D3031.012e |  | D3031.012e | Chiller - Capacity: 100 to <350 Ton - Vibration isolated equipment that is not snubbed or restrained - Equipment fragility only | 130500 | 153000 | 199300 | LogNormal | 158343.6453 | 0.17106 | 1 | 168300 |  |  |  | 137700 | 0.17106 | 5 | Each | [60 empty] | 20.1507 | 23.625 | 30.7743 | LogNormal | 23.625 | 0.30292 | 1 | 39.375 |  |  |  | 11.8125 | 0.30292 | 5 | Each | [60 empty] | 1
| D3031.012f |  | D3031.012f | Chiller - Capacity: 100 to <350 Ton - Vibration isolated equipment that is not snubbed or restrained - Combined anchorage/isolator & equipment fragility | 800 | 1500 | 2400 | Normal | 1566.6663 | 0.39845 | 1 | 1650 |  |  |  | 1350 | 0.39845 | 5 | Each | 131300 | 154500 | 201700 | LogNormal | 159816.2659 | 0.17334 | 1 | 169950 |  |  |  | 139050 | 0.17334 | 5 | Each | 131300 | 154500 | 201700 | LogNormal | 159816.2659 | 0.17334 | 1 | 169950 |  |  |  | 139050 | 0.17334 | 5 | Each | [30 empty] | 0.8235 | 1.5441 | 2.4706 | Normal | 1.5441 | 0.47039 | 1 | 1.6985 |  |  |  | 1.3897 | 0.47039 | 5 | Each | 20.2743 | 23.8566 | 31.1449 | LogNormal | 23.8566 | 0.30422 | 1 | 39.761 |  |  |  | 11.9283 | 0.30422 | 5 | Each | 20.2743 | 23.8566 | 31.1449 | LogNormal | 23.8566 | 0.30422 | 1 | 39.761 |  |  |  | 11.9283 | 0.30422 | 5 | Each | [30 empty] | 1
| D3031.012g |  | D3031.012g | Chiller - Capacity: 350 to <750 Ton - Vibration isolated equipment that is not snubbed or restrained - Anchorage fragility only | 1400 | 2200 | 3100 | Normal | 2233.3322 | 0.29698 | 1 | 4400 |  |  |  | 1320 | 0.29698 | 5 | Each | 218600 | 257400 | 335700 | LogNormal | 266110.8376 | 0.17312 | 1 | 514800 |  |  |  | 154440 | 0.17312 | 5 | Each | [45 empty] | 1.4412 | 2.2647 | 3.1912 | Normal | 2.2647 | 0.3882 | 1 | 4.5294 |  |  |  | 1.3588 | 0.3882 | 5 | Each | 22.5029 | 26.4971 | 34.5574 | LogNormal | 26.4971 | 0.30409 | 1 | 291.4677 |  |  |  | 13.2485 | 0.30409 | 5 | Each | [45 empty] | 1
| D3031.012h |  | D3031.012h | Chiller - Capacity: 350 to <750 Ton - Vibration isolated equipment that is not snubbed or restrained - Equipment fragility only | 217200 | 255200 | 332600 | LogNormal | 263966.9814 | 0.17205 | 1 | 280720 |  |  |  | 229680 | 0.17205 | 5 | Each | [60 empty] | 22.3588 | 26.2706 | 34.2382 | LogNormal | 26.2706 | 0.30348 | 1 | 52.5412 |  |  |  | 13.1353 | 0.30348 | 5 | Each | [60 empty] | 1
| D3031.012i |  | D3031.012i | Chiller - Capacity: 350 to <750 Ton - Vibration isolated equipment that is not snubbed or restrained - Combined anchorage/isolator & equipment fragility | 1400 | 2200 | 3100 | Normal | 2233.3322 | 0.29698 | 1 | 2420 |  |  |  | 1980 | 0.29698 | 5 | Each | 218600 | 257400 | 335700 | LogNormal | 266110.8376 | 0.17312 | 1 | 283140 |  |  |  | 231660 | 0.17312 | 5 | Each | 218600 | 257400 | 335700 | LogNormal | 266110.8376 | 0.17312 | 1 | 283140 |  |  |  | 231660 | 0.17312 | 5 | Each | [30 empty] | 1.4412 | 2.2647 | 3.1912 | Normal | 2.2647 | 0.3882 | 1 | 2.4912 |  |  |  | 2.0382 | 0.3882 | 5 | Each | 22.5029 | 26.4971 | 34.5574 | LogNormal | 26.4971 | 0.30409 | 1 | 52.9942 |  |  |  | 13.2485 | 0.30409 | 5 | Each | 22.5029 | 26.4971 | 34.5574 | LogNormal | 26.4971 | 0.30409 | 1 | 52.9942 |  |  |  | 13.2485 | 0.30409 | 5 | Each | [30 empty] | 1
| D3031.012j |  | D3031.012j | Chiller - Capacity: 750 to <1000 Ton - Vibration isolated equipment that is not snubbed or restrained - Anchorage fragility only | 1600 | 2400 | 3400 | LogNormal | 2358.8816 | 0.28852 | 1 | 4800 |  |  |  | 1440 | 0.28852 | 5 | Each | 367100 | 433400 | 565200 | LogNormal | 447663.7689 | 0.174 | 1 | 866800 |  |  |  | 260040 | 0.174 | 5 | Each | [45 empty] | 1.6471 | 2.4706 | 3.5 | LogNormal | 2.4706 | 0.38177 | 1 | 4.9412 |  |  |  | 1.4824 | 0.38177 | 5 | Each | 26.4528 | 31.2303 | 40.7276 | LogNormal | 31.2303 | 0.30459 | 1 | 477.3774 |  |  |  | 15.6151 | 0.30459 | 5 | Each | [45 empty] | 1
| D3031.012k |  | D3031.012k | Chiller - Capacity: 750 to <1000 Ton - Vibration isolated equipment that is not snubbed or restrained - Equipment fragility only | 365500 | 431000 | 561800 | LogNormal | 445291.1546 | 0.17337 | 1 | 474100 |  |  |  | 387900 | 0.17337 | 5 | Each | [60 empty] | 26.3375 | 31.0574 | 40.4826 | LogNormal | 31.0574 | 0.30423 | 1 | 75.425 |  |  |  | 15.5287 | 0.30423 | 5 | Each | [60 empty] | 1
| D3031.012l |  | D3031.012l | Chiller - Capacity: 750 to <1000 Ton - Vibration isolated equipment that is not snubbed or restrained - Combined anchorage/isolator & equipment fragility | 1600 | 2400 | 3400 | LogNormal | 2358.8816 | 0.28852 | 1 | 2640 |  |  |  | 2160 | 0.28852 | 5 | Each | 367100 | 433400 | 565200 | LogNormal | 447663.7689 | 0.174 | 1 | 476740 |  |  |  | 390060 | 0.174 | 5 | Each | 367100 | 433400 | 565200 | LogNormal | 447663.7689 | 0.174 | 1 | 476740 |  |  |  | 390060 | 0.174 | 5 | Each | [30 empty] | 1.6471 | 2.4706 | 3.5 | LogNormal | 2.4706 | 0.38177 | 1 | 2.7177 |  |  |  | 2.2235 | 0.38177 | 5 | Each | 26.4528 | 31.2303 | 40.7276 | LogNormal | 31.2303 | 0.30459 | 1 | 75.845 |  |  |  | 15.6151 | 0.30459 | 5 | Each | 26.4528 | 31.2303 | 40.7276 | LogNormal | 31.2303 | 0.30459 | 1 | 75.845 |  |  |  | 15.6151 | 0.30459 | 5 | Each | [30 empty] | 1
| D3031.013a |  | D3031.013a | Chiller - Capacity: < 100 Ton - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only | 500 | 1000 | 1700 | LogNormal | 958.6389 | 0.45231 | 1 | 1100 |  |  |  | 900 | 0.45231 | 5 | Each | 39600 | 47200 | 62500 | LogNormal | 48838.5351 | 0.18434 | 1 | 51920 |  |  |  | 42480 | 0.18434 | 5 | Each | [45 empty] | 0.5147 | 1.0294 | 1.75 | LogNormal | 1.0294 | 0.5168 | 1 | 1.1323 |  |  |  | 0.92646 | 0.5168 | 5 | Each | 8.1529 | 9.7176 | 12.8676 | LogNormal | 9.7176 | 0.31061 | 1 | 14.5764 |  |  |  | 4.8588 | 0.31061 | 5 | Each | [45 empty] | 1
| D3031.013b |  | D3031.013b | Chiller - Capacity: < 100 Ton - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only | 39100 | 46200 | 60800 | LogNormal | 47847.4484 | 0.17848 | 1 | 50820 |  |  |  | 41580 | 0.17848 | 5 | Each | [60 empty] | 8.05 | 9.5118 | 12.5176 | LogNormal | 9.5118 | 0.30717 | 1 | 14.2677 |  |  |  | 4.7559 | 0.30717 | 5 | Each | [60 empty] | 1
| D3031.013c |  | D3031.013c | Chiller - Capacity: < 100 Ton - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | 500 | 1000 | 1700 | LogNormal | 958.6389 | 0.45231 | 1 | 1100 |  |  |  | 900 | 0.45231 | 5 | Each | 39600 | 47200 | 62500 | LogNormal | 48838.5351 | 0.18434 | 1 | 51920 |  |  |  | 42480 | 0.18434 | 5 | Each | 39600 | 47200 | 62500 | LogNormal | 48838.5351 | 0.18434 | 1 | 51920 |  |  |  | 42480 | 0.18434 | 5 | Each | [30 empty] | 0.5882 | 1.1765 | 2 | LogNormal | 1.1765 | 0.5168 | 1 | 1.2941 |  |  |  | 1.0589 | 0.5168 | 5 | Each | 4.6588 | 5.5529 | 7.3529 | LogNormal | 5.5529 | 0.31061 | 1 | 11.1058 |  |  |  | 2.7765 | 0.31061 | 5 | Each | 9.3176 | 11.1059 | 14.7059 | LogNormal | 11.1059 | 0.31061 | 1 | 16.6588 |  |  |  | 5.553 | 0.31061 | 5 | Each | [30 empty] | 1
| D3031.013d |  | D3031.013d | Chiller - Capacity: 100 to <350 Ton - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only | 800 | 1500 | 2400 | Normal | 1566.6663 | 0.39845 | 1 | 1650 |  |  |  | 1350 | 0.39845 | 5 | Each | 131300 | 154500 | 201700 | LogNormal | 159816.2659 | 0.17334 | 1 | 169950 |  |  |  | 139050 | 0.17334 | 5 | Each | [45 empty] | 0.8235 | 1.5441 | 2.4706 | Normal | 1.5441 | 0.47039 | 1 | 1.6985 |  |  |  | 1.3897 | 0.47039 | 5 | Each | 20.2743 | 23.8566 | 31.1449 | LogNormal | 23.8566 | 0.30422 | 1 | 39.761 |  |  |  | 11.9283 | 0.30422 | 5 | Each | [45 empty] | 1
| D3031.013e |  | D3031.013e | Chiller - Capacity: 100 to <350 Ton - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only | 130500 | 153000 | 199300 | LogNormal | 158343.6453 | 0.17106 | 1 | 168300 |  |  |  | 137700 | 0.17106 | 5 | Each | [60 empty] | 20.1507 | 23.625 | 30.7743 | LogNormal | 23.625 | 0.30292 | 1 | 39.375 |  |  |  | 11.8125 | 0.30292 | 5 | Each | [60 empty] | 1
| D3031.013f |  | D3031.013f | Chiller - Capacity: 100 to <350 Ton - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | 800 | 1500 | 2400 | Normal | 1566.6663 | 0.39845 | 1 | 1650 |  |  |  | 1350 | 0.39845 | 5 | Each | 131300 | 154500 | 201700 | LogNormal | 159816.2659 | 0.17334 | 1 | 169950 |  |  |  | 139050 | 0.17334 | 5 | Each | 131300 | 154500 | 201700 | LogNormal | 159816.2659 | 0.17334 | 1 | 169950 |  |  |  | 139050 | 0.17334 | 5 | Each | [30 empty] | 0.9412 | 1.7647 | 2.8235 | Normal | 1.7647 | 0.47039 | 1 | 1.9412 |  |  |  | 1.5882 | 0.47039 | 5 | Each | 15.4471 | 18.1765 | 23.7294 | LogNormal | 18.1765 | 0.30422 | 1 | 36.353 |  |  |  | 9.0883 | 0.30422 | 5 | Each | 23.1706 | 27.2647 | 35.5941 | LogNormal | 27.2647 | 0.30422 | 1 | 45.4412 |  |  |  | 13.6324 | 0.30422 | 5 | Each | [30 empty] | 1
| D3031.013g |  | D3031.013g | Chiller - Capacity: 350 to <750 Ton - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only | 1400 | 2200 | 3100 | Normal | 2233.3322 | 0.29698 | 1 | 2420 |  |  |  | 1980 | 0.29698 | 5 | Each | 218600 | 257400 | 335700 | LogNormal | 266110.8376 | 0.17312 | 1 | 283140 |  |  |  | 231660 | 0.17312 | 5 | Each | [45 empty] | 1.4412 | 2.2647 | 3.1912 | Normal | 2.2647 | 0.3882 | 1 | 2.4912 |  |  |  | 2.0382 | 0.3882 | 5 | Each | 22.5029 | 26.4971 | 34.5574 | LogNormal | 26.4971 | 0.30409 | 1 | 52.9942 |  |  |  | 13.2485 | 0.30409 | 5 | Each | [45 empty] | 1
| D3031.013h |  | D3031.013h | Chiller - Capacity: 350 to <750 Ton - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only | 217200 | 255200 | 332600 | LogNormal | 263966.9814 | 0.17205 | 1 | 280720 |  |  |  | 229680 | 0.17205 | 5 | Each | [60 empty] | 25.5529 | 30.0235 | 39.1294 | LogNormal | 30.0235 | 0.30348 | 1 | 60.047 |  |  |  | 15.0117 | 0.30348 | 5 | Each | [60 empty] | 1
| D3031.013i |  | D3031.013i | Chiller - Capacity: 350 to <750 Ton - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | 1400 | 2200 | 3100 | Normal | 2233.3322 | 0.29698 | 1 | 2420 |  |  |  | 1980 | 0.29698 | 5 | Each | 218600 | 257400 | 335700 | LogNormal | 266110.8376 | 0.17312 | 1 | 283140 |  |  |  | 231660 | 0.17312 | 5 | Each | 218600 | 257400 | 335700 | LogNormal | 266110.8376 | 0.17312 | 1 | 283140 |  |  |  | 231660 | 0.17312 | 5 | Each | [30 empty] | 0.1647 | 0.2588 | 0.3647 | Normal | 0.2588 | 0.3882 | 1 | 0.28468 |  |  |  | 0.23292 | 0.3882 | 5 | Each | 25.7176 | 30.2824 | 39.4941 | LogNormal | 30.2824 | 0.30409 | 1 | 33.3106 |  |  |  | 27.2542 | 0.30409 | 5 | Each | 25.7176 | 30.2824 | 39.4941 | LogNormal | 30.2824 | 0.30409 | 1 | 33.3106 |  |  |  | 27.2542 | 0.30409 | 5 | Each | [30 empty] | 1
| D3031.013j |  | D3031.013j | Chiller - Capacity: 750 to <1000 Ton - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only | 1600 | 2400 | 3400 | LogNormal | 2358.8816 | 0.28852 | 1 | 2640 |  |  |  | 2160 | 0.28852 | 5 | Each | 367100 | 433400 | 565200 | LogNormal | 447663.7689 | 0.174 | 1 | 476740 |  |  |  | 390060 | 0.174 | 5 | Each | [45 empty] | 1.6471 | 2.4706 | 3.5 | LogNormal | 2.4706 | 0.38177 | 1 | 2.7177 |  |  |  | 2.2235 | 0.38177 | 5 | Each | 26.4528 | 31.2303 | 40.7276 | LogNormal | 31.2303 | 0.30459 | 1 | 75.845 |  |  |  | 15.6151 | 0.30459 | 5 | Each | [45 empty] | 1
| D3031.013k |  | D3031.013k | Chiller - Capacity: 750 to <1000 Ton - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only | 365500 | 431000 | 561800 | LogNormal | 445291.1546 | 0.17337 | 1 | 474100 |  |  |  | 387900 | 0.17337 | 5 | Each | [60 empty] | 30.1 | 35.4941 | 46.2659 | LogNormal | 35.4941 | 0.30423 | 1 | 86.2 |  |  |  | 17.7471 | 0.30423 | 5 | Each | [60 empty] | 1
| D3031.013l |  | D3031.013l | Chiller - Capacity: 750 to <1000 Ton - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | 1600 | 2400 | 3400 | LogNormal | 2358.8816 | 0.28852 | 1 | 2640 |  |  |  | 2160 | 0.28852 | 5 | Each | 367100 | 433400 | 565200 | LogNormal | 447663.7689 | 0.174 | 1 | 476740 |  |  |  | 390060 | 0.174 | 5 | Each | 367100 | 433400 | 565200 | LogNormal | 447663.7689 | 0.174 | 1 | 476740 |  |  |  | 390060 | 0.174 | 5 | Each | [30 empty] | 0.1882 | 0.2824 | 0.4 | LogNormal | 0.2824 | 0.38177 | 1 | 0.31064 |  |  |  | 0.25416 | 0.38177 | 5 | Each | 3.0232 | 3.5692 | 4.6546 | LogNormal | 3.5692 | 0.30459 | 1 | 8.668 |  |  |  | 1.7846 | 0.30459 | 5 | Each | 3.0232 | 3.5692 | 4.6546 | LogNormal | 3.5692 | 0.30459 | 1 | 8.668 |  |  |  | 1.7846 | 0.30459 | 5 | Each | [30 empty] | 1
| D3031.021a |  | D3031.021a | Cooling Tower - Capacity: < 100 Ton - Unanchored equipment that is not vibration isolated - Equipment fragility only | 20100 | 23700 | 30800 | LogNormal | 24462.8398 | 0.17196 | 1 | 26070 |  |  |  | 21330 | 0.17196 | 5 | Each | [60 empty] | 4.7294 | 5.5765 | 7.2471 | LogNormal | 5.5765 | 0.30343 | 1 | 8.3647 |  |  |  | 2.7883 | 0.30343 | 5 | Each | [60 empty] | 1
| D3031.021b |  | D3031.021b | Cooling Tower - Capacity: 100 to <350 Ton - Unanchored equipment that is not vibration isolated - Equipment fragility only | 66500 | 78000 | 102300 | LogNormal | 80890.6253 | 0.17436 | 1 | 85800 |  |  |  | 70200 | 0.17436 | 5 | Each | [60 empty] | 11.7353 | 13.7647 | 18.0529 | LogNormal | 13.7647 | 0.3048 | 1 | 22.9412 |  |  |  | 6.8823 | 0.3048 | 5 | Each | [60 empty] | 1
| D3031.021c |  | D3031.021c | Cooling Tower - Capacity: 350 to <750 Ton - Unanchored equipment that is not vibration isolated - Equipment fragility only | 110200 | 130200 | 170600 | LogNormal | 134657.0647 | 0.17644 | 1 | 143220 |  |  |  | 117180 | 0.17644 | 5 | Each | [60 empty] | 12.9647 | 15.3176 | 20.0706 | LogNormal | 15.3176 | 0.30599 | 1 | 30.6352 |  |  |  | 7.6588 | 0.30599 | 5 | Each | [60 empty] | 1
| D3031.021d |  | D3031.021d | Cooling Tower - Capacity: 750 to <1000 Ton - Unanchored equipment that is not vibration isolated - Equipment fragility only | 185500 | 218500 | 284800 | LogNormal | 225825.8562 | 0.17297 | 1 | 240350 |  |  |  | 196650 | 0.17297 | 5 | Each | [60 empty] | 15.2765 | 17.9941 | 23.4541 | LogNormal | 17.9941 | 0.304 | 1 | 43.7 |  |  |  | 8.997 | 0.304 | 5 | Each | [60 empty] | 1
| D3031.022a |  | D3031.022a | Cooling Tower - Capacity: < 100 Ton - Vibration isolated equipment that is not snubbed or restrained - Anchorage fragility only | 500 | 1000 | 1700 | LogNormal | 958.6389 | 0.45231 | 1 | 1100 |  |  |  | 900 | 0.45231 | 5 | Each | 20600 | 24700 | 32500 | LogNormal | 25455.2131 | 0.18344 | 1 | 27170 |  |  |  | 22230 | 0.18344 | 5 | Each | [45 empty] | 0.0588 | 0.1176 | 0.2 | LogNormal | 0.1176 | 0.5168 | 1 | 0.12936 |  |  |  | 0.10584 | 0.5168 | 5 | Each | 2.4235 | 2.9059 | 3.8235 | LogNormal | 2.9059 | 0.31008 | 1 | 3.1965 |  |  |  | 2.6153 | 0.31008 | 5 | Each | [45 empty] | 1
| D3031.022b |  | D3031.022b | Cooling Tower - Capacity: < 100 Ton - Vibration isolated equipment that is not snubbed or restrained - Equipment fragility only | 20100 | 23700 | 30800 | LogNormal | 24462.8398 | 0.17196 | 1 | 26070 |  |  |  | 21330 | 0.17196 | 5 | Each | [60 empty] | 4.7294 | 5.5765 | 7.2471 | LogNormal | 5.5765 | 0.30343 | 1 | 8.3647 |  |  |  | 2.7883 | 0.30343 | 5 | Each | [60 empty] | 1
| D3031.022c |  | D3031.022c | Cooling Tower - Capacity: < 100 Ton - Vibration isolated equipment that is not snubbed or restrained - Combined anchorage/isolator & equipment fragility | 500 | 1000 | 1700 | LogNormal | 958.6389 | 0.45231 | 1 | 1100 |  |  |  | 900 | 0.45231 | 5 | Each | 20600 | 24700 | 32500 | LogNormal | 25455.2131 | 0.18344 | 1 | 27170 |  |  |  | 22230 | 0.18344 | 5 | Each | 20100 | 23700 | 30800 | LogNormal | 24462.8398 | 0.17196 | 1 | 26070 |  |  |  | 21330 | 0.17196 | 5 | Each | [30 empty] | 0.5882 | 1.1765 | 2 | LogNormal | 1.1765 | 0.5168 | 1 | 1.2941 |  |  |  | 1.0589 | 0.5168 | 5 | Each | 4.8471 | 5.8118 | 7.6471 | LogNormal | 5.8118 | 0.31008 | 1 | 8.7177 |  |  |  | 2.9059 | 0.31008 | 5 | Each | 4.7294 | 5.5765 | 7.2471 | LogNormal | 5.5765 | 0.30343 | 1 | 8.3647 |  |  |  | 2.7883 | 0.30343 | 5 | Each | [30 empty] | 1
| D3031.022d |  | D3031.022d | Cooling Tower - Capacity: 100 to <350 Ton - Vibration isolated equipment that is not snubbed or restrained - Anchorage fragility only | 800 | 1500 | 2400 | Normal | 1566.6663 | 0.39845 | 1 | 1650 |  |  |  | 1350 | 0.39845 | 5 | Each | 67300 | 79500 | 104700 | LogNormal | 82361.4729 | 0.17873 | 1 | 87450 |  |  |  | 71550 | 0.17873 | 5 | Each | [45 empty] | 0.0941 | 0.1765 | 0.2824 | Normal | 0.1765 | 0.47039 | 1 | 0.19415 |  |  |  | 0.15885 | 0.47039 | 5 | Each | 1.1876 | 1.4029 | 1.8476 | LogNormal | 1.4029 | 0.30732 | 1 | 2.3382 |  |  |  | 0.70145 | 0.30732 | 5 | Each | [45 empty] | 1
| D3031.022e |  | D3031.022e | Cooling Tower - Capacity: 100 to <350 Ton - Vibration isolated equipment that is not snubbed or restrained - Equipment fragility only | 66500 | 78000 | 102300 | LogNormal | 80890.6253 | 0.17436 | 1 | 85800 |  |  |  | 70200 | 0.17436 | 5 | Each | [60 empty] | 11.7353 | 13.7647 | 18.0529 | LogNormal | 13.7647 | 0.3048 | 1 | 22.9412 |  |  |  | 6.8823 | 0.3048 | 5 | Each | [60 empty] | 1
| D3031.022f |  | D3031.022f | Cooling Tower - Capacity: 100 to <350 Ton - Vibration isolated equipment that is not snubbed or restrained - Combined anchorage/isolator & equipment fragility | 800 | 1500 | 2400 | Normal | 1566.6663 | 0.39845 | 1 | 1650 |  |  |  | 1350 | 0.39845 | 5 | Each | 67300 | 79500 | 104700 | LogNormal | 82361.4729 | 0.17873 | 1 | 87450 |  |  |  | 71550 | 0.17873 | 5 | Each | 66500 | 78000 | 102300 | LogNormal | 80890.6253 | 0.17436 | 1 | 85800 |  |  |  | 70200 | 0.17436 | 5 | Each | [30 empty] | 0.9412 | 1.7647 | 2.8235 | Normal | 1.7647 | 0.47039 | 1 | 1.9412 |  |  |  | 1.5882 | 0.47039 | 5 | Each | 11.8765 | 14.0294 | 18.4765 | LogNormal | 14.0294 | 0.30732 | 1 | 23.3823 |  |  |  | 7.0147 | 0.30732 | 5 | Each | 11.7353 | 13.7647 | 18.0529 | LogNormal | 13.7647 | 0.3048 | 1 | 22.9412 |  |  |  | 6.8823 | 0.3048 | 5 | Each | [30 empty] | 1
| D3031.022g |  | D3031.022g | Cooling Tower - Capacity: 350 to <750 Ton - Vibration isolated equipment that is not snubbed or restrained - Anchorage fragility only | 1400 | 2200 | 3100 | Normal | 2233.3322 | 0.29698 | 1 | 2420 |  |  |  | 1980 | 0.29698 | 5 | Each | 111600 | 132400 | 173700 | LogNormal | 136799.644 | 0.17844 | 1 | 145640 |  |  |  | 119160 | 0.17844 | 5 | Each | [45 empty] | 1.6471 | 2.5882 | 3.6471 | Normal | 2.5882 | 0.3882 | 1 | 2.847 |  |  |  | 2.3294 | 0.3882 | 5 | Each | 13.1294 | 15.5765 | 20.4353 | LogNormal | 15.5765 | 0.30715 | 1 | 31.153 |  |  |  | 7.7882 | 0.30715 | 5 | Each | [45 empty] | 1
| D3031.022h |  | D3031.022h | Cooling Tower - Capacity: 350 to <750 Ton - Vibration isolated equipment that is not snubbed or restrained - Equipment fragility only | 110200 | 130200 | 170600 | LogNormal | 134657.0647 | 0.17644 | 1 | 143220 |  |  |  | 117180 | 0.17644 | 5 | Each | [60 empty] | 12.9647 | 15.3176 | 20.0706 | LogNormal | 15.3176 | 0.30599 | 1 | 30.6352 |  |  |  | 7.6588 | 0.30599 | 5 | Each | [60 empty] | 1
| D3031.022i |  | D3031.022i | Cooling Tower - Capacity: 350 to <750 Ton - Vibration isolated equipment that is not snubbed or restrained - Combined anchorage/isolator & equipment fragility | 1400 | 2200 | 3100 | Normal | 2233.3322 | 0.29698 | 1 | 2420 |  |  |  | 1980 | 0.29698 | 5 | Each | 111600 | 132400 | 173700 | LogNormal | 136799.644 | 0.17844 | 1 | 145640 |  |  |  | 119160 | 0.17844 | 5 | Each | 110200 | 130200 | 170600 | LogNormal | 134657.0647 | 0.17644 | 1 | 143220 |  |  |  | 117180 | 0.17644 | 5 | Each | [30 empty] | 0.4941 | 0.7765 | 1.0941 | Normal | 0.7765 | 0.3882 | 1 | 0.85415 |  |  |  | 0.69885 | 0.3882 | 5 | Each | 3.9388 | 4.6729 | 6.1306 | LogNormal | 4.6729 | 0.30715 | 1 | 9.3458 |  |  |  | 2.3365 | 0.30715 | 5 | Each | 3.8894 | 4.5953 | 6.0212 | LogNormal | 4.5953 | 0.30599 | 1 | 9.1906 |  |  |  | 2.2976 | 0.30599 | 5 | Each | [30 empty] | 1
| D3031.022j |  | D3031.022j | Cooling Tower - Capacity: 750 to <1000 Ton - Vibration isolated equipment that is not snubbed or restrained - Anchorage fragility only | 1600 | 2400 | 3400 | LogNormal | 2358.8816 | 0.28852 | 1 | 2640 |  |  |  | 2160 | 0.28852 | 5 | Each | 187100 | 220900 | 288200 | LogNormal | 228198.4902 | 0.17421 | 1 | 242990 |  |  |  | 198810 | 0.17421 | 5 | Each | [45 empty] | 1.8824 | 2.8235 | 4 | LogNormal | 2.8235 | 0.38177 | 1 | 3.1059 |  |  |  | 2.5411 | 0.38177 | 5 | Each | 15.4082 | 18.1918 | 23.7341 | LogNormal | 18.1918 | 0.30471 | 1 | 44.18 |  |  |  | 9.0959 | 0.30471 | 5 | Each | [45 empty] | 1
| D3031.022k |  | D3031.022k | Cooling Tower - Capacity: 750 to <1000 Ton - Vibration isolated equipment that is not snubbed or restrained - Equipment fragility only | 185500 | 218500 | 284800 | LogNormal | 225825.8562 | 0.17297 | 1 | 240350 |  |  |  | 196650 | 0.17297 | 5 | Each | [60 empty] | 15.2765 | 17.9941 | 23.4541 | LogNormal | 17.9941 | 0.304 | 1 | 43.7 |  |  |  | 8.997 | 0.304 | 5 | Each | [60 empty] | 1
| D3031.022l |  | D3031.022l | Cooling Tower - Capacity: 750 to <1000 Ton - Vibration isolated equipment that is not snubbed or restrained - Combined anchorage/isolator & equipment fragility | 1600 | 2400 | 3400 | LogNormal | 2358.8816 | 0.28852 | 1 | 2640 |  |  |  | 2160 | 0.28852 | 5 | Each | 187100 | 220900 | 288200 | LogNormal | 228198.4902 | 0.17421 | 1 | 242990 |  |  |  | 198810 | 0.17421 | 5 | Each | 185500 | 218500 | 284800 | LogNormal | 225825.8562 | 0.17297 | 1 | 240350 |  |  |  | 196650 | 0.17297 | 5 | Each | [30 empty] | 0.5647 | 0.8471 | 1.2 | LogNormal | 0.8471 | 0.38177 | 1 | 0.93181 |  |  |  | 0.76239 | 0.38177 | 5 | Each | 4.6225 | 5.4575 | 7.1202 | LogNormal | 5.4575 | 0.30471 | 1 | 13.254 |  |  |  | 2.7287 | 0.30471 | 5 | Each | 4.5829 | 5.3982 | 7.0362 | LogNormal | 5.3982 | 0.304 | 1 | 13.11 |  |  |  | 2.6991 | 0.304 | 5 | Each | [30 empty] | 1
| D3031.023a |  | D3031.023a | Cooling Tower - Capacity: < 100 Ton - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only | 500 | 1000 | 1700 | LogNormal | 958.6389 | 0.45231 | 1 | 1100 |  |  |  | 900 | 0.45231 | 5 | Each | 20600 | 24700 | 32500 | LogNormal | 25455.2131 | 0.18344 | 1 | 27170 |  |  |  | 22230 | 0.18344 | 5 | Each | [45 empty] | 0.1765 | 0.3529 | 0.6 | LogNormal | 0.3529 | 0.5168 | 1 | 0.38819 |  |  |  | 0.31761 | 0.5168 | 5 | Each | 1.4541 | 1.7435 | 2.2941 | LogNormal | 1.7435 | 0.31008 | 1 | 2.6153 |  |  |  | 0.87175 | 0.31008 | 5 | Each | [45 empty] | 1
| D3031.023b |  | D3031.023b | Cooling Tower - Capacity: < 100 Ton - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only | 20100 | 23700 | 30800 | LogNormal | 24462.8398 | 0.17196 | 1 | 26070 |  |  |  | 21330 | 0.17196 | 5 | Each | [60 empty] | 4.7294 | 5.5765 | 7.2471 | LogNormal | 5.5765 | 0.30343 | 1 | 8.3647 |  |  |  | 2.7883 | 0.30343 | 5 | Each | [60 empty] | 1
| D3031.023c |  | D3031.023c | Cooling Tower - Capacity: < 100 Ton - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | 500 | 1000 | 1700 | LogNormal | 958.6389 | 0.45231 | 1 | 1100 |  |  |  | 900 | 0.45231 | 5 | Each | 20600 | 24700 | 32500 | LogNormal | 25455.2131 | 0.18344 | 1 | 27170 |  |  |  | 22230 | 0.18344 | 5 | Each | 20100 | 23700 | 30800 | LogNormal | 24462.8398 | 0.17196 | 1 | 26070 |  |  |  | 21330 | 0.17196 | 5 | Each | [30 empty] | 0.5882 | 1.1765 | 2 | LogNormal | 1.1765 | 0.5168 | 1 | 1.2941 |  |  |  | 1.0589 | 0.5168 | 5 | Each | 4.8471 | 5.8118 | 7.6471 | LogNormal | 5.8118 | 0.31008 | 1 | 8.7177 |  |  |  | 2.9059 | 0.31008 | 5 | Each | 4.7294 | 5.5765 | 7.2471 | LogNormal | 5.5765 | 0.30343 | 1 | 8.3647 |  |  |  | 2.7883 | 0.30343 | 5 | Each | [30 empty] | 1
| D3031.023d |  | D3031.023d | Cooling Tower - Capacity: 100 to <350 Ton - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only | 800 | 1500 | 2400 | Normal | 1566.6663 | 0.39845 | 1 | 1650 |  |  |  | 1350 | 0.39845 | 5 | Each | 67300 | 79500 | 104700 | LogNormal | 82361.4729 | 0.17873 | 1 | 87450 |  |  |  | 71550 | 0.17873 | 5 | Each | [45 empty] | 0.2824 | 0.5294 | 0.8471 | Normal | 0.5294 | 0.47039 | 1 | 0.58234 |  |  |  | 0.47646 | 0.47039 | 5 | Each | 3.5629 | 4.2088 | 5.5429 | LogNormal | 4.2088 | 0.30732 | 1 | 7.0147 |  |  |  | 2.1044 | 0.30732 | 5 | Each | [45 empty] | 1
| D3031.023e |  | D3031.023e | Cooling Tower - Capacity: 100 to <350 Ton - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only | 66500 | 78000 | 102300 | LogNormal | 80890.6253 | 0.17436 | 1 | 85800 |  |  |  | 70200 | 0.17436 | 5 | Each | [60 empty] | 11.7353 | 13.7647 | 18.0529 | LogNormal | 13.7647 | 0.3048 | 1 | 22.9412 |  |  |  | 6.8823 | 0.3048 | 5 | Each | [60 empty] | 1
| D3031.023f |  | D3031.023f | Cooling Tower - Capacity: 100 to <350 Ton - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | 800 | 1500 | 2400 | Normal | 1566.6663 | 0.39845 | 1 | 1650 |  |  |  | 1350 | 0.39845 | 5 | Each | 67300 | 79500 | 104700 | LogNormal | 82361.4729 | 0.17873 | 1 | 87450 |  |  |  | 71550 | 0.17873 | 5 | Each | 66500 | 78000 | 102300 | LogNormal | 80890.6253 | 0.17436 | 1 | 85800 |  |  |  | 70200 | 0.17436 | 5 | Each | [30 empty] | 0.9412 | 1.7647 | 2.8235 | Normal | 1.7647 | 0.47039 | 1 | 1.9412 |  |  |  | 1.5882 | 0.47039 | 5 | Each | 11.8765 | 14.0294 | 18.4765 | LogNormal | 14.0294 | 0.30732 | 1 | 23.3823 |  |  |  | 7.0147 | 0.30732 | 5 | Each | 11.7353 | 13.7647 | 18.0529 | LogNormal | 13.7647 | 0.3048 | 1 | 22.9412 |  |  |  | 6.8823 | 0.3048 | 5 | Each | [30 empty] | 1
| D3031.023g |  | D3031.023g | Cooling Tower - Capacity: 350 to <750 Ton - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only | 1400 | 2200 | 3100 | Normal | 2233.3322 | 0.29698 | 1 | 2420 |  |  |  | 1980 | 0.29698 | 5 | Each | 111600 | 132400 | 173700 | LogNormal | 136799.644 | 0.17844 | 1 | 145640 |  |  |  | 119160 | 0.17844 | 5 | Each | [45 empty] | 1.6471 | 2.5882 | 3.6471 | Normal | 2.5882 | 0.3882 | 1 | 2.847 |  |  |  | 2.3294 | 0.3882 | 5 | Each | 13.1294 | 15.5765 | 20.4353 | LogNormal | 15.5765 | 0.30715 | 1 | 31.153 |  |  |  | 7.7882 | 0.30715 | 5 | Each | [45 empty] | 1
| D3031.023h |  | D3031.023h | Cooling Tower - Capacity: 350 to <750 Ton - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only | 110200 | 130200 | 170600 | LogNormal | 134657.0647 | 0.17644 | 1 | 143220 |  |  |  | 117180 | 0.17644 | 5 | Each | [60 empty] | 12.9647 | 15.3176 | 20.0706 | LogNormal | 15.3176 | 0.30599 | 1 | 30.6352 |  |  |  | 7.6588 | 0.30599 | 5 | Each | [60 empty] | 1
| D3031.023i |  | D3031.023i | Cooling Tower - Capacity: 350 to <750 Ton - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | 1400 | 2200 | 3100 | Normal | 2233.3322 | 0.29698 | 1 | 2420 |  |  |  | 1980 | 0.29698 | 5 | Each | 111600 | 132400 | 173700 | LogNormal | 136799.644 | 0.17844 | 1 | 145640 |  |  |  | 119160 | 0.17844 | 5 | Each | 110200 | 130200 | 170600 | LogNormal | 134657.0647 | 0.17644 | 1 | 143220 |  |  |  | 117180 | 0.17644 | 5 | Each | [30 empty] | 0.4941 | 0.7765 | 1.0941 | Normal | 0.7765 | 0.3882 | 1 | 0.85415 |  |  |  | 0.69885 | 0.3882 | 5 | Each | 3.9388 | 4.6729 | 6.1306 | LogNormal | 4.6729 | 0.30715 | 1 | 9.3458 |  |  |  | 2.3365 | 0.30715 | 5 | Each | 3.8894 | 4.5953 | 6.0212 | LogNormal | 4.5953 | 0.30599 | 1 | 9.1906 |  |  |  | 2.2976 | 0.30599 | 5 | Each | [30 empty] | 1
| D3031.023j |  | D3031.023j | Cooling Tower - Capacity: 750 to <1000 Ton - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only | 1600 | 2400 | 3400 | LogNormal | 2358.8816 | 0.28852 | 1 | 2640 |  |  |  | 2160 | 0.28852 | 5 | Each | 187100 | 220900 | 288200 | LogNormal | 228198.4902 | 0.17421 | 1 | 242990 |  |  |  | 198810 | 0.17421 | 5 | Each | [45 empty] | 1.8824 | 2.8235 | 4 | LogNormal | 2.8235 | 0.38177 | 1 | 3.1059 |  |  |  | 2.5411 | 0.38177 | 5 | Each | 15.4082 | 18.1918 | 23.7341 | LogNormal | 18.1918 | 0.30471 | 1 | 44.18 |  |  |  | 9.0959 | 0.30471 | 5 | Each | [45 empty] | 1
| D3031.023k |  | D3031.023k | Cooling Tower - Capacity: 750 to <1000 Ton - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only | 185500 | 218500 | 284800 | LogNormal | 225825.8562 | 0.17297 | 1 | 240350 |  |  |  | 196650 | 0.17297 | 5 | Each | [60 empty] | 15.2765 | 17.9941 | 23.4541 | LogNormal | 17.9941 | 0.304 | 1 | 43.7 |  |  |  | 8.997 | 0.304 | 5 | Each | [60 empty] | 1
| D3031.023l |  | D3031.023l | Cooling Tower - Capacity: 750 to <1000 Ton - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | 1600 | 2400 | 3400 | LogNormal | 2358.8816 | 0.28852 | 1 | 2640 |  |  |  | 2160 | 0.28852 | 5 | Each | 187100 | 220900 | 288200 | LogNormal | 228198.4902 | 0.17421 | 1 | 242990 |  |  |  | 198810 | 0.17421 | 5 | Each | 185500 | 218500 | 284800 | LogNormal | 225825.8562 | 0.17297 | 1 | 240350 |  |  |  | 196650 | 0.17297 | 5 | Each | [30 empty] | 0.5647 | 0.8471 | 1.2 | LogNormal | 0.8471 | 0.38177 | 1 | 0.93181 |  |  |  | 0.76239 | 0.38177 | 5 | Each | 4.6225 | 5.4575 | 7.1202 | LogNormal | 5.4575 | 0.30471 | 1 | 13.254 |  |  |  | 2.7287 | 0.30471 | 5 | Each | 4.5829 | 5.3982 | 7.0362 | LogNormal | 5.3982 | 0.304 | 1 | 13.11 |  |  |  | 2.6991 | 0.304 | 5 | Each | [30 empty] | 1
| D3032.011a |  | D3032.011a | Compressor - Capacity: Small non medical air supply - Unanchored equipment that is not vibration isolated - Equipment fragility only | 640 | 750 | 980 | LogNormal | 777.0934 | 0.17233 | 1 | 825 |  |  |  | 675 | 0.17233 | 5 | Each | 2210 | 2700 | 3680 | LogNormal | 2796.6778 | 0.20627 | 1 | 2970 |  |  |  | 2430 | 0.20627 | 5 | Each | [45 empty] | 0.7529 | 0.8824 | 1.1529 | LogNormal | 0.8824 | 0.30364 | 1 | 0.97064 |  |  |  | 0.79416 | 0.30364 | 5 | Each | 0.26 | 0.3176 | 0.4329 | LogNormal | 0.3176 | 0.32411 | 1 | 0.63525 |  |  |  | 0.1588 | 0.32411 | 5 | Each | [45 empty] | 1
| D3032.011b |  | D3032.011b | Compressor - Capacity: Large non medical air supply - Unanchored equipment that is not vibration isolated - Equipment fragility only | 2550 | 3000 | 3900 | LogNormal | 3099.1924 | 0.17133 | 1 | 3300 |  |  |  | 2700 | 0.17133 | 5 | Each | 6660 | 8000 | 10730 | LogNormal | 8290.4734 | 0.19298 | 1 | 8800 |  |  |  | 7200 | 0.19298 | 5 | Each | [45 empty] | 3 | 3.5294 | 4.5882 | LogNormal | 3.5294 | 0.30308 | 1 | 3.8823 |  |  |  | 3.1765 | 0.30308 | 5 | Each | 0.7835 | 0.9412 | 1.2624 | LogNormal | 0.9412 | 0.31582 | 1 | 1.8824 |  |  |  | 0.4706 | 0.31582 | 5 | Each | [45 empty] | 1
| D3032.011c |  | D3032.011c | Compressor - Capacity: Small medical quality air supply - Unanchored equipment that is not vibration isolated - Equipment fragility only | 770 | 900 | 1170 | LogNormal | 931.7787 | 0.16907 | 1 | 990 |  |  |  | 810 | 0.16907 | 5 | Each | 6610 | 8200 | 11380 | LogNormal | 8499.388 | 0.21996 | 1 | 9020 |  |  |  | 7380 | 0.21996 | 5 | Each | [45 empty] | 0.9059 | 1.0588 | 1.3765 | LogNormal | 1.0588 | 0.3018 | 1 | 1.1647 |  |  |  | 0.95292 | 0.3018 | 5 | Each | 0.7776 | 0.9647 | 1.3388 | LogNormal | 0.9647 | 0.33299 | 1 | 1.9294 |  |  |  | 0.48235 | 0.33299 | 5 | Each | [45 empty] | 1
| D3032.011d |  | D3032.011d | Compressor - Capacity: Large medical quality air supply - Unanchored equipment that is not vibration isolated - Equipment fragility only | 3400 | 4000 | 5200 | LogNormal | 4132.257 | 0.17133 | 1 | 4400 |  |  |  | 3600 | 0.17133 | 5 | Each | 24860 | 30000 | 39930 | LogNormal | 30965.6449 | 0.19097 | 1 | 33000 |  |  |  | 27000 | 0.19097 | 5 | Each | [45 empty] | 4 | 4.7059 | 6.1176 | LogNormal | 4.7059 | 0.30308 | 1 | 5.1765 |  |  |  | 4.2353 | 0.30308 | 5 | Each | 2.9247 | 3.5294 | 4.6976 | LogNormal | 3.5294 | 0.31459 | 1 | 7.0588 |  |  |  | 1.7647 | 0.31459 | 5 | Each | [45 empty] | 1
| D3032.012a |  | D3032.012a | Compressor - Capacity: Small non medical air supply - Vibration isolated equipment that is not snubbed or restrained - Anchorage fragility only | 250 | 450 | 950 | LogNormal | 468.0885 | 0.54862 | 1 | 495 |  |  |  | 405 | 0.54862 | 5 | Each | 2460 | 3150 | 4630 | LogNormal | 3289.5926 | 0.25821 | 1 | 3465 |  |  |  | 2835 | 0.25821 | 5 | Each | [45 empty] | 0.0882 | 0.1588 | 0.3353 | LogNormal | 0.1588 | 0.60289 | 1 | 0.17468 |  |  |  | 0.14292 | 0.60289 | 5 | Each | 0.8682 | 1.1118 | 1.6341 | LogNormal | 1.1118 | 0.3594 | 1 | 1.223 |  |  |  | 1.0006 | 0.3594 | 5 | Each | [45 empty] | 1
| D3032.012b |  | D3032.012b | Compressor - Capacity: Small non medical air supply - Vibration isolated equipment that is not snubbed or restrained - Equipment fragility only | 640 | 750 | 980 | LogNormal | 777.0934 | 0.17233 | 1 | 825 |  |  |  | 675 | 0.17233 | 5 | Each | 2210 | 2700 | 3680 | LogNormal | 2796.6778 | 0.20627 | 1 | 2970 |  |  |  | 2430 | 0.20627 | 5 | Each | [45 empty] | 0.7529 | 0.8824 | 1.1529 | LogNormal | 0.8824 | 0.30364 | 1 | 0.97064 |  |  |  | 0.79416 | 0.30364 | 5 | Each | 0.26 | 0.3176 | 0.4329 | LogNormal | 0.3176 | 0.32411 | 1 | 0.63525 |  |  |  | 0.1588 | 0.32411 | 5 | Each | [45 empty] | 1
| D3032.012c |  | D3032.012c | Compressor - Capacity: Small non medical air supply - Vibration isolated equipment that is not snubbed or restrained - Combined anchorage/isolator & equipment fragility | 250 | 450 | 950 | LogNormal | 468.0885 | 0.54862 | 1 | 495 |  |  |  | 405 | 0.54862 | 5 | Each | 2460 | 3150 | 4630 | LogNormal | 3289.5926 | 0.25821 | 1 | 3465 |  |  |  | 2835 | 0.25821 | 5 | Each | 640 | 750 | 980 | LogNormal | 777.0934 | 0.17233 | 1 | 825 |  |  |  | 675 | 0.17233 | 5 | Each | 2460 | 3150 | 4630 | LogNormal | 3289.5926 | 0.25821 | 1 | 3465 |  |  |  | 2835 | 0.25821 | 5 | Each | [15 empty] | 0.2941 | 0.5294 | 1.1176 | LogNormal | 0.5294 | 0.60289 | 1 | 0.58234 |  |  |  | 0.47646 | 0.60289 | 5 | Each | 0.2894 | 0.3706 | 0.5447 | LogNormal | 0.3706 | 0.3594 | 1 | 0.74119 |  |  |  | 0.1853 | 0.3594 | 5 | Each | 0.7529 | 0.8824 | 1.1529 | LogNormal | 0.8824 | 0.30364 | 1 | 0.97064 |  |  |  | 0.79416 | 0.30364 | 5 | Each | 2.8941 | 3.7059 | 5.4471 | LogNormal | 3.7059 | 0.3594 | 1 | 4.0765 |  |  |  | 3.3353 | 0.3594 | 5 | Each | [15 empty] | 1
| D3032.012d |  | D3032.012d | Compressor - Capacity: Large non medical air supply - Vibration isolated equipment that is not snubbed or restrained - Anchorage fragility only | 550 | 850 | 1600 | LogNormal | 897.6512 | 0.4444 | 1 | 935 |  |  |  | 765 | 0.4444 | 5 | Each | 7210 | 8850 | 12330 | LogNormal | 9216.5501 | 0.21828 | 1 | 9735 |  |  |  | 7965 | 0.21828 | 5 | Each | [45 empty] | 0.1941 | 0.3 | 0.5647 | LogNormal | 0.3 | 0.50989 | 1 | 0.33 |  |  |  | 0.27 | 0.50989 | 5 | Each | 2.5447 | 3.1235 | 4.3518 | LogNormal | 3.1235 | 0.33188 | 1 | 3.4359 |  |  |  | 2.8111 | 0.33188 | 5 | Each | [45 empty] | 1
| D3032.012e |  | D3032.012e | Compressor - Capacity: Large non medical air supply - Vibration isolated equipment that is not snubbed or restrained - Equipment fragility only | 2550 | 3000 | 3900 | LogNormal | 3099.1924 | 0.17133 | 1 | 3300 |  |  |  | 2700 | 0.17133 | 5 | Each | 6660 | 8000 | 10730 | LogNormal | 8290.4734 | 0.19298 | 1 | 8800 |  |  |  | 7200 | 0.19298 | 5 | Each | [45 empty] | 3 | 3.5294 | 4.5882 | LogNormal | 3.5294 | 0.30308 | 1 | 3.8823 |  |  |  | 3.1765 | 0.30308 | 5 | Each | 0.7835 | 0.9412 | 1.2624 | LogNormal | 0.9412 | 0.31582 | 1 | 1.8824 |  |  |  | 0.4706 | 0.31582 | 5 | Each | [45 empty] | 1
| D3032.012f |  | D3032.012f | Compressor - Capacity: Large non medical air supply - Vibration isolated equipment that is not snubbed or restrained - Combined anchorage/isolator & equipment fragility | 550 | 850 | 1600 | LogNormal | 897.6512 | 0.4444 | 1 | 935 |  |  |  | 765 | 0.4444 | 5 | Each | 7210 | 8850 | 12330 | LogNormal | 9216.5501 | 0.21828 | 1 | 9735 |  |  |  | 7965 | 0.21828 | 5 | Each | 2550 | 3000 | 3900 | LogNormal | 3099.1924 | 0.17133 | 1 | 3300 |  |  |  | 2700 | 0.17133 | 5 | Each | 7210 | 8850 | 12330 | LogNormal | 9216.5501 | 0.21828 | 1 | 9735 |  |  |  | 7965 | 0.21828 | 5 | Each | [15 empty] | 0.6471 | 1 | 1.8824 | LogNormal | 1 | 0.50989 | 1 | 1.1 |  |  |  | 0.9 | 0.50989 | 5 | Each | 0.8482 | 1.0412 | 1.4506 | LogNormal | 1.0412 | 0.33188 | 1 | 2.0824 |  |  |  | 0.5206 | 0.33188 | 5 | Each | 3 | 3.5294 | 4.5882 | LogNormal | 3.5294 | 0.30308 | 1 | 3.8823 |  |  |  | 3.1765 | 0.30308 | 5 | Each | 8.4824 | 10.4118 | 14.5059 | LogNormal | 10.4118 | 0.33188 | 1 | 11.453 |  |  |  | 9.3706 | 0.33188 | 5 | Each | [15 empty] | 1
| D3032.012g |  | D3032.012g | Compressor - Capacity: Small medical quality air supply - Vibration isolated equipment that is not snubbed or restrained - Anchorage fragility only | 250 | 450 | 950 | LogNormal | 468.0885 | 0.54862 | 1 | 495 |  |  |  | 405 | 0.54862 | 5 | Each | 6860 | 8650 | 12330 | LogNormal | 8993.0889 | 0.23821 | 1 | 9515 |  |  |  | 7785 | 0.23821 | 5 | Each | [45 empty] | 0.2941 | 0.5294 | 1.1176 | LogNormal | 0.5294 | 0.60289 | 1 | 0.58234 |  |  |  | 0.47646 | 0.60289 | 5 | Each | 0.8071 | 1.0176 | 1.4506 | LogNormal | 1.0176 | 0.34531 | 1 | 2.0352 |  |  |  | 0.5088 | 0.34531 | 5 | Each | [45 empty] | 1
| D3032.012h |  | D3032.012h | Compressor - Capacity: Small medical quality air supply - Vibration isolated equipment that is not snubbed or restrained - Equipment fragility only | 770 | 900 | 1170 | LogNormal | 931.7787 | 0.16907 | 1 | 990 |  |  |  | 810 | 0.16907 | 5 | Each | 6610 | 8200 | 11380 | LogNormal | 8499.388 | 0.21996 | 1 | 9020 |  |  |  | 7380 | 0.21996 | 5 | Each | [45 empty] | 0.9059 | 1.0588 | 1.3765 | LogNormal | 1.0588 | 0.3018 | 1 | 1.1647 |  |  |  | 0.95292 | 0.3018 | 5 | Each | 0.7776 | 0.9647 | 1.3388 | LogNormal | 0.9647 | 0.33299 | 1 | 1.9294 |  |  |  | 0.48235 | 0.33299 | 5 | Each | [45 empty] | 1
| D3032.012i |  | D3032.012i | Compressor - Capacity: Small medical quality air supply - Vibration isolated equipment that is not snubbed or restrained - Combined anchorage/isolator & equipment fragility | 250 | 450 | 950 | LogNormal | 468.0885 | 0.54862 | 1 | 495 |  |  |  | 405 | 0.54862 | 5 | Each | 6860 | 8650 | 12330 | LogNormal | 8993.0889 | 0.23821 | 1 | 9515 |  |  |  | 7785 | 0.23821 | 5 | Each | 770 | 900 | 1170 | LogNormal | 931.7787 | 0.16907 | 1 | 990 |  |  |  | 810 | 0.16907 | 5 | Each | 6860 | 8650 | 12330 | LogNormal | 8993.0889 | 0.23821 | 1 | 9515 |  |  |  | 7785 | 0.23821 | 5 | Each | [15 empty] | 0.0882 | 0.1588 | 0.3353 | LogNormal | 0.1588 | 0.60289 | 1 | 0.17468 |  |  |  | 0.14292 | 0.60289 | 5 | Each | 2.4212 | 3.0529 | 4.3518 | LogNormal | 3.0529 | 0.34531 | 1 | 3.3582 |  |  |  | 2.7476 | 0.34531 | 5 | Each | 0.2718 | 0.3176 | 0.4129 | LogNormal | 0.3176 | 0.3018 | 1 | 0.34936 |  |  |  | 0.28584 | 0.3018 | 5 | Each | 2.4212 | 3.0529 | 4.3518 | LogNormal | 3.0529 | 0.34531 | 1 | 3.3582 |  |  |  | 2.7476 | 0.34531 | 5 | Each | [15 empty] | 1
| D3032.012j |  | D3032.012j | Compressor - Capacity: Large medical quality air supply - Vibration isolated equipment that is not snubbed or restrained - Anchorage fragility only | 550 | 850 | 1600 | LogNormal | 897.6512 | 0.4444 | 1 | 935 |  |  |  | 765 | 0.4444 | 5 | Each | 25410 | 30850 | 41530 | LogNormal | 31894.833 | 0.19833 | 1 | 33935 |  |  |  | 27765 | 0.19833 | 5 | Each | [45 empty] | 0.6471 | 1 | 1.8824 | LogNormal | 1 | 0.50989 | 1 | 1.1 |  |  |  | 0.9 | 0.50989 | 5 | Each | 2.9894 | 3.6294 | 4.8859 | LogNormal | 3.6294 | 0.31911 | 1 | 7.2588 |  |  |  | 1.8147 | 0.31911 | 5 | Each | [45 empty] | 1
| D3032.012k |  | D3032.012k | Compressor - Capacity: Large medical quality air supply - Vibration isolated equipment that is not snubbed or restrained - Equipment fragility only | 3400 | 4000 | 5200 | LogNormal | 4132.257 | 0.17133 | 1 | 4400 |  |  |  | 3600 | 0.17133 | 5 | Each | 24860 | 30000 | 39930 | LogNormal | 30965.6449 | 0.19097 | 1 | 33000 |  |  |  | 27000 | 0.19097 | 5 | Each | [45 empty] | 4 | 4.7059 | 6.1176 | LogNormal | 4.7059 | 0.30308 | 1 | 5.1765 |  |  |  | 4.2353 | 0.30308 | 5 | Each | 2.9247 | 3.5294 | 4.6976 | LogNormal | 3.5294 | 0.31459 | 1 | 7.0588 |  |  |  | 1.7647 | 0.31459 | 5 | Each | [45 empty] | 1
| D3032.012l |  | D3032.012l | Compressor - Capacity: Large medical quality air supply - Vibration isolated equipment that is not snubbed or restrained - Combined anchorage/isolator & equipment fragility | 550 | 850 | 1600 | LogNormal | 897.6512 | 0.4444 | 1 | 935 |  |  |  | 765 | 0.4444 | 5 | Each | 25410 | 30850 | 41530 | LogNormal | 31894.833 | 0.19833 | 1 | 33935 |  |  |  | 27765 | 0.19833 | 5 | Each | 3400 | 4000 | 5200 | LogNormal | 4132.257 | 0.17133 | 1 | 4400 |  |  |  | 3600 | 0.17133 | 5 | Each | 25410 | 30850 | 41530 | LogNormal | 31894.833 | 0.19833 | 1 | 33935 |  |  |  | 27765 | 0.19833 | 5 | Each | [15 empty] | 0.1941 | 0.3 | 0.5647 | LogNormal | 0.3 | 0.50989 | 1 | 0.33 |  |  |  | 0.27 | 0.50989 | 5 | Each | 8.9682 | 10.8882 | 14.6576 | LogNormal | 10.8882 | 0.31911 | 1 | 11.977 |  |  |  | 9.7994 | 0.31911 | 5 | Each | 1.2 | 1.4118 | 1.8353 | LogNormal | 1.4118 | 0.30308 | 1 | 1.553 |  |  |  | 1.2706 | 0.30308 | 5 | Each | 8.9682 | 10.8882 | 14.6576 | LogNormal | 10.8882 | 0.31911 | 1 | 11.977 |  |  |  | 9.7994 | 0.31911 | 5 | Each | [15 empty] | 1
| D3032.013a |  | D3032.013a | Compressor - Capacity: Small non medical air supply - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only | 250 | 450 | 950 | LogNormal | 468.0885 | 0.54862 | 1 | 495 |  |  |  | 405 | 0.54862 | 5 | Each | 2460 | 3150 | 4630 | LogNormal | 3289.5926 | 0.25821 | 1 | 3465 |  |  |  | 2835 | 0.25821 | 5 | Each | [45 empty] | 0.0882 | 0.1588 | 0.3353 | LogNormal | 0.1588 | 0.60289 | 1 | 0.17468 |  |  |  | 0.14292 | 0.60289 | 5 | Each | 0.8682 | 1.1118 | 1.6341 | LogNormal | 1.1118 | 0.3594 | 1 | 1.223 |  |  |  | 1.0006 | 0.3594 | 5 | Each | [45 empty] | 1
| D3032.013b |  | D3032.013b | Compressor - Capacity: Small non medical air supply - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only | 640 | 750 | 980 | LogNormal | 777.0934 | 0.17233 | 1 | 825 |  |  |  | 675 | 0.17233 | 5 | Each | 2210 | 2700 | 3680 | LogNormal | 2796.6778 | 0.20627 | 1 | 2970 |  |  |  | 2430 | 0.20627 | 5 | Each | [45 empty] | 0.7529 | 0.8824 | 1.1529 | LogNormal | 0.8824 | 0.30364 | 1 | 0.97064 |  |  |  | 0.79416 | 0.30364 | 5 | Each | 0.26 | 0.3176 | 0.4329 | LogNormal | 0.3176 | 0.32411 | 1 | 0.63525 |  |  |  | 0.1588 | 0.32411 | 5 | Each | [45 empty] | 1
| D3032.013c |  | D3032.013c | Compressor - Capacity: Small non medical air supply - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | 250 | 450 | 950 | LogNormal | 468.0885 | 0.54862 | 1 | 495 |  |  |  | 405 | 0.54862 | 5 | Each | 2460 | 3150 | 4630 | LogNormal | 3289.5926 | 0.25821 | 1 | 3465 |  |  |  | 2835 | 0.25821 | 5 | Each | 640 | 750 | 980 | LogNormal | 777.0934 | 0.17233 | 1 | 825 |  |  |  | 675 | 0.17233 | 5 | Each | 2460 | 3150 | 4630 | LogNormal | 3289.5926 | 0.25821 | 1 | 3465 |  |  |  | 2835 | 0.25821 | 5 | Each | [15 empty] | 0.2941 | 0.5294 | 1.1176 | LogNormal | 0.5294 | 0.60289 | 1 | 0.58234 |  |  |  | 0.47646 | 0.60289 | 5 | Each | 0.8682 | 1.1118 | 1.6341 | LogNormal | 1.1118 | 0.3594 | 1 | 1.4824 |  |  |  | 0.74121 | 0.3594 | 5 | Each | 0.7529 | 0.8824 | 1.1529 | LogNormal | 0.8824 | 0.30364 | 1 | 0.97064 |  |  |  | 0.79416 | 0.30364 | 5 | Each | 2.8941 | 3.7059 | 5.4471 | LogNormal | 3.7059 | 0.3594 | 1 | 4.0765 |  |  |  | 3.3353 | 0.3594 | 5 | Each | [15 empty] | 1
| D3032.013d |  | D3032.013d | Compressor - Capacity: Large non medical air supply - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only | 550 | 850 | 1600 | LogNormal | 897.6512 | 0.4444 | 1 | 935 |  |  |  | 765 | 0.4444 | 5 | Each | 7210 | 8850 | 12330 | LogNormal | 9216.5501 | 0.21828 | 1 | 9735 |  |  |  | 7965 | 0.21828 | 5 | Each | [45 empty] | 0.1941 | 0.3 | 0.5647 | LogNormal | 0.3 | 0.50989 | 1 | 0.33 |  |  |  | 0.27 | 0.50989 | 5 | Each | 2.5447 | 3.1235 | 4.3518 | LogNormal | 3.1235 | 0.33188 | 1 | 3.4359 |  |  |  | 2.8111 | 0.33188 | 5 | Each | [45 empty] | 1
| D3032.013e |  | D3032.013e | Compressor - Capacity: Large non medical air supply - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only | 2550 | 3000 | 3900 | LogNormal | 3099.1924 | 0.17133 | 1 | 3300 |  |  |  | 2700 | 0.17133 | 5 | Each | 6660 | 8000 | 10730 | LogNormal | 8290.4734 | 0.19298 | 1 | 8800 |  |  |  | 7200 | 0.19298 | 5 | Each | [45 empty] | 3 | 3.5294 | 4.5882 | LogNormal | 3.5294 | 0.30308 | 1 | 3.8823 |  |  |  | 3.1765 | 0.30308 | 5 | Each | 0.7835 | 0.9412 | 1.2624 | LogNormal | 0.9412 | 0.31582 | 1 | 1.8824 |  |  |  | 0.4706 | 0.31582 | 5 | Each | [45 empty] | 1
| D3032.013f |  | D3032.013f | Compressor - Capacity: Large non medical air supply - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | 550 | 850 | 1600 | LogNormal | 897.6512 | 0.4444 | 1 | 935 |  |  |  | 765 | 0.4444 | 5 | Each | 7210 | 8850 | 12330 | LogNormal | 9216.5501 | 0.21828 | 1 | 9735 |  |  |  | 7965 | 0.21828 | 5 | Each | 2550 | 3000 | 3900 | LogNormal | 3099.1924 | 0.17133 | 1 | 3300 |  |  |  | 2700 | 0.17133 | 5 | Each | 7210 | 8850 | 12330 | LogNormal | 9216.5501 | 0.21828 | 1 | 9735 |  |  |  | 7965 | 0.21828 | 5 | Each | [15 empty] | 0.6471 | 1 | 1.8824 | LogNormal | 1 | 0.50989 | 1 | 1.1 |  |  |  | 0.9 | 0.50989 | 5 | Each | 2.5447 | 3.1235 | 4.3518 | LogNormal | 3.1235 | 0.33188 | 1 | 4.1647 |  |  |  | 2.0823 | 0.33188 | 5 | Each | 3 | 3.5294 | 4.5882 | LogNormal | 3.5294 | 0.30308 | 1 | 3.8823 |  |  |  | 3.1765 | 0.30308 | 5 | Each | 8.4824 | 10.4118 | 14.5059 | LogNormal | 10.4118 | 0.33188 | 1 | 11.453 |  |  |  | 9.3706 | 0.33188 | 5 | Each | [15 empty] | 1
| D3032.013g |  | D3032.013g | Compressor - Capacity: Small medical quality air supply - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only | 250 | 450 | 950 | LogNormal | 468.0885 | 0.54862 | 1 | 495 |  |  |  | 405 | 0.54862 | 5 | Each | 6860 | 8650 | 12330 | LogNormal | 8993.0889 | 0.23821 | 1 | 9515 |  |  |  | 7785 | 0.23821 | 5 | Each | [45 empty] | 0.2941 | 0.5294 | 1.1176 | LogNormal | 0.5294 | 0.60289 | 1 | 0.58234 |  |  |  | 0.47646 | 0.60289 | 5 | Each | 0.8071 | 1.0176 | 1.4506 | LogNormal | 1.0176 | 0.34531 | 1 | 2.0352 |  |  |  | 0.5088 | 0.34531 | 5 | Each | [45 empty] | 1
| D3032.013h |  | D3032.013h | Compressor - Capacity: Small medical quality air supply - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only | 770 | 900 | 1170 | LogNormal | 931.7787 | 0.16907 | 1 | 990 |  |  |  | 810 | 0.16907 | 5 | Each | 6610 | 8200 | 11380 | LogNormal | 8499.388 | 0.21996 | 1 | 9020 |  |  |  | 7380 | 0.21996 | 5 | Each | [45 empty] | 0.9059 | 1.0588 | 1.3765 | LogNormal | 1.0588 | 0.3018 | 1 | 1.1647 |  |  |  | 0.95292 | 0.3018 | 5 | Each | 2.3329 | 2.8941 | 4.0165 | LogNormal | 2.8941 | 0.33299 | 1 | 3.8588 |  |  |  | 1.9294 | 0.33299 | 5 | Each | [45 empty] | 1
| D3032.013i |  | D3032.013i | Compressor - Capacity: Small medical quality air supply - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | 250 | 450 | 950 | LogNormal | 468.0885 | 0.54862 | 1 | 495 |  |  |  | 405 | 0.54862 | 5 | Each | 6860 | 8650 | 12330 | LogNormal | 8993.0889 | 0.23821 | 1 | 9515 |  |  |  | 7785 | 0.23821 | 5 | Each | 770 | 900 | 1170 | LogNormal | 931.7787 | 0.16907 | 1 | 990 |  |  |  | 810 | 0.16907 | 5 | Each | 6860 | 8650 | 12330 | LogNormal | 8993.0889 | 0.23821 | 1 | 9515 |  |  |  | 7785 | 0.23821 | 5 | Each | [15 empty] | 0.2941 | 0.5294 | 1.1176 | LogNormal | 0.5294 | 0.60289 | 1 | 0.58234 |  |  |  | 0.47646 | 0.60289 | 5 | Each | 2.4212 | 3.0529 | 4.3518 | LogNormal | 3.0529 | 0.34531 | 1 | 4.0705 |  |  |  | 2.0353 | 0.34531 | 5 | Each | 0.9059 | 1.0588 | 1.3765 | LogNormal | 1.0588 | 0.3018 | 1 | 1.1647 |  |  |  | 0.95292 | 0.3018 | 5 | Each | 8.0706 | 10.1765 | 14.5059 | LogNormal | 10.1765 | 0.34531 | 1 | 11.1941 |  |  |  | 9.1589 | 0.34531 | 5 | Each | [15 empty] | 1
| D3032.013j |  | D3032.013j | Compressor - Capacity: Large medical quality air supply - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only | 550 | 850 | 1600 | LogNormal | 897.6512 | 0.4444 | 1 | 935 |  |  |  | 765 | 0.4444 | 5 | Each | 25410 | 30850 | 41530 | LogNormal | 31894.833 | 0.19833 | 1 | 33935 |  |  |  | 27765 | 0.19833 | 5 | Each | [45 empty] | 0.6471 | 1 | 1.8824 | LogNormal | 1 | 0.50989 | 1 | 1.1 |  |  |  | 0.9 | 0.50989 | 5 | Each | 2.9894 | 3.6294 | 4.8859 | LogNormal | 3.6294 | 0.31911 | 1 | 7.2588 |  |  |  | 1.8147 | 0.31911 | 5 | Each | [45 empty] | 1
| D3032.013k |  | D3032.013k | Compressor - Capacity: Large medical quality air supply - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only | 3400 | 4000 | 5200 | LogNormal | 4132.257 | 0.17133 | 1 | 4400 |  |  |  | 3600 | 0.17133 | 5 | Each | 24860 | 30000 | 39930 | LogNormal | 30965.6449 | 0.19097 | 1 | 33000 |  |  |  | 27000 | 0.19097 | 5 | Each | [45 empty] | 4 | 4.7059 | 6.1176 | LogNormal | 4.7059 | 0.30308 | 1 | 5.1765 |  |  |  | 4.2353 | 0.30308 | 5 | Each | 8.7741 | 10.5882 | 14.0929 | LogNormal | 10.5882 | 0.31459 | 1 | 14.1176 |  |  |  | 7.0588 | 0.31459 | 5 | Each | [45 empty] | 1
| D3032.013l |  | D3032.013l | Compressor - Capacity: Large medical quality air supply - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | 550 | 850 | 1600 | LogNormal | 897.6512 | 0.4444 | 1 | 935 |  |  |  | 765 | 0.4444 | 5 | Each | 25410 | 30850 | 41530 | LogNormal | 31894.833 | 0.19833 | 1 | 33935 |  |  |  | 27765 | 0.19833 | 5 | Each | 3400 | 4000 | 5200 | LogNormal | 4132.257 | 0.17133 | 1 | 4400 |  |  |  | 3600 | 0.17133 | 5 | Each | 25410 | 30850 | 41530 | LogNormal | 31894.833 | 0.19833 | 1 | 33935 |  |  |  | 27765 | 0.19833 | 5 | Each | [15 empty] | 0.6471 | 1 | 1.8824 | LogNormal | 1 | 0.50989 | 1 | 1.1 |  |  |  | 0.9 | 0.50989 | 5 | Each | 8.9682 | 10.8882 | 14.6576 | LogNormal | 10.8882 | 0.31911 | 1 | 14.5176 |  |  |  | 7.2588 | 0.31911 | 5 | Each | 4 | 4.7059 | 6.1176 | LogNormal | 4.7059 | 0.30308 | 1 | 5.1765 |  |  |  | 4.2353 | 0.30308 | 5 | Each | 29.8941 | 36.2941 | 48.8588 | LogNormal | 36.2941 | 0.31911 | 1 | 39.9235 |  |  |  | 32.6647 | 0.31911 | 5 | Each | [15 empty] | 1
| D3041.001a |  | D3041.001a | HVAC Fan In Line Fan, Fan independently supported and vibration isolators, SDC A or B | 5000 | 7000 | 11500 | LogNormal | 7342.9115 | 0.34252 | 1 | 7700 |  |  |  | 6300 | 0.34252 | 5 | 10 Units | 25000 | 27000 | 31500 | LogNormal | 27701.7659 | 0.092504 | 1 | 29700 |  |  |  | 24300 | 0.092504 | 5 | 10 Units | [45 empty] | 5.882 | 8.235 | 13.529 | LogNormal | 8.235 | 0.42405 | 1 | 9.0585 |  |  |  | 7.4115 | 0.42405 | 5 | 10 Units | 8.824 | 9.529 | 11.118 | LogNormal | 9.529 | 0.26657 | 1 | 12.7055 |  |  |  | 6.3525 | 0.26657 | 5 | 10 Units | [45 empty] | 10
| D3041.001b |  | D3041.001b | HVAC Fan In Line Fan, Fan independently supported and vibration isolators, SDC C | 5000 | 7000 | 11500 | LogNormal | 7342.9115 | 0.34252 | 1 | 7700 |  |  |  | 6300 | 0.34252 | 5 | 10 Units | 25000 | 27000 | 31500 | LogNormal | 27701.7659 | 0.092504 | 1 | 29700 |  |  |  | 24300 | 0.092504 | 5 | 10 Units | [45 empty] | 5.882 | 8.235 | 13.529 | LogNormal | 8.235 | 0.42405 | 1 | 9.0585 |  |  |  | 7.4115 | 0.42405 | 5 | 10 Units | 8.824 | 9.529 | 11.118 | LogNormal | 9.529 | 0.26657 | 1 | 12.7055 |  |  |  | 6.3525 | 0.26657 | 5 | 10 Units | [45 empty] | 10
| D3041.001c |  | D3041.001c | HVAC Fan In Line Fan, Fan independently supported and vibration isolators, SDC D, E, F | 5000 | 7000 | 11500 | LogNormal | 7342.9115 | 0.34252 | 1 | 7700 |  |  |  | 6300 | 0.34252 | 5 | 10 Units | 25000 | 27000 | 31500 | LogNormal | 27701.7659 | 0.092504 | 1 | 29700 |  |  |  | 24300 | 0.092504 | 5 | 10 Units | [45 empty] | 5.882 | 8.235 | 13.529 | LogNormal | 8.235 | 0.42405 | 1 | 9.0585 |  |  |  | 7.4115 | 0.42405 | 5 | 10 Units | 8.824 | 9.529 | 11.118 | LogNormal | 9.529 | 0.26657 | 1 | 12.7055 |  |  |  | 6.3525 | 0.26657 | 5 | 10 Units | [45 empty] | 10
| D3041.001d |  | D3041.001d | HVAC Fan In Line Fan, Fan independently supported and vibration isolators, SDC D, E, F (OSHPD or sim) | 5000 | 7000 | 11500 | LogNormal | 7342.9115 | 0.34252 | 1 | 7700 |  |  |  | 6300 | 0.34252 | 5 | 10 Units | 25000 | 27000 | 31500 | LogNormal | 27701.7659 | 0.092504 | 1 | 29700 |  |  |  | 24300 | 0.092504 | 5 | 10 Units | [45 empty] | 5.882 | 8.235 | 13.529 | LogNormal | 8.235 | 0.42405 | 1 | 9.0585 |  |  |  | 7.4115 | 0.42405 | 5 | 10 Units | 8.824 | 9.529 | 11.118 | LogNormal | 9.529 | 0.26657 | 1 | 12.7055 |  |  |  | 6.3525 | 0.26657 | 5 | 10 Units | [45 empty] | 10
| D3041.002a |  | D3041.002a | HVAC Fan In Line Fan, Fan independently supported but not on vibration isolators, SDC A or B | 5000 | 7000 | 11500 | LogNormal | 7342.9115 | 0.34252 | 1 | 7700 |  |  |  | 6300 | 0.34252 | 5 | 10 Units | [60 empty] | 5.882 | 8.235 | 13.529 | LogNormal | 8.235 | 0.42405 | 1 | 9.0585 |  |  |  | 7.4115 | 0.42405 | 5 | 10 Units | [60 empty] | 10
| D3041.002b |  | D3041.002b | HVAC Fan In Line Fan, Fan independently supported but not on vibration isolators, SDC C | 5000 | 7000 | 11500 | LogNormal | 7342.9115 | 0.34252 | 1 | 7700 |  |  |  | 6300 | 0.34252 | 5 | 10 Units | [60 empty] | 5.882 | 8.235 | 13.529 | LogNormal | 8.235 | 0.42405 | 1 | 9.0585 |  |  |  | 7.4115 | 0.42405 | 5 | 10 Units | [60 empty] | 10
| D3041.002c |  | D3041.002c | HVAC Fan In Line Fan, Fan independently supported but not on vibration isolators, SDC D, E, F | 5000 | 7000 | 11500 | LogNormal | 7342.9115 | 0.34252 | 1 | 7700 |  |  |  | 6300 | 0.34252 | 5 | 10 Units | [60 empty] | 5.882 | 8.235 | 13.529 | LogNormal | 8.235 | 0.42405 | 1 | 9.0585 |  |  |  | 7.4115 | 0.42405 | 5 | 10 Units | [60 empty] | 10
| D3041.002d |  | D3041.002d | HVAC Fan In Line Fan, Fan independently supported but not on vibration isolators, SDC D, E, F (OSHPD or sim) | 5000 | 7000 | 11500 | LogNormal | 7342.9115 | 0.34252 | 1 | 7700 |  |  |  | 6300 | 0.34252 | 5 | 10 Units | [60 empty] | 5.882 | 8.235 | 13.529 | LogNormal | 8.235 | 0.42405 | 1 | 9.0585 |  |  |  | 7.4115 | 0.42405 | 5 | 10 Units | [60 empty] | 10
| D3041.011a |  | D3041.011a | HVAC Galvanized Sheet Metal Ducting less than 6 sq. ft in cross sectional area, SDC A or B | 450 | 650 | 1100 | LogNormal | 680.9247 | 0.36736 | 1 | 715 |  |  |  | 585 | 0.36736 | 5 | Each (1000 ft duct) | 5750 | 6350 | 7400 | LogNormal | 6464.1076 | 0.1002 | 1 | 6985 |  |  |  | 5715 | 0.1002 | 5 | Each (1000 ft duct) | [45 empty] | 0.5294 | 0.7647 | 1.2941 | LogNormal | 0.7647 | 0.44436 | 1 | 0.84117 |  |  |  | 0.68823 | 0.44436 | 5 | Each (1000 ft duct) | 2.0294 | 2.2412 | 2.6118 | LogNormal | 2.2412 | 0.26933 | 1 | 2.9883 |  |  |  | 1.4941 | 0.26933 | 5 | Each (1000 ft duct) | [45 empty] | 1
| D3041.011b |  | D3041.011b | HVAC Galvanized Sheet Metal Ducting less than 6 sq. ft in cross sectional area, SDC C | 450 | 650 | 1100 | LogNormal | 680.9247 | 0.36736 | 1 | 715 |  |  |  | 585 | 0.36736 | 5 | Each (1000 ft duct) | 5750 | 6350 | 7400 | LogNormal | 6464.1076 | 0.1002 | 1 | 6985 |  |  |  | 5715 | 0.1002 | 5 | Each (1000 ft duct) | [45 empty] | 0.5294 | 0.7647 | 1.2941 | LogNormal | 0.7647 | 0.44436 | 1 | 0.84117 |  |  |  | 0.68823 | 0.44436 | 5 | Each (1000 ft duct) | 2.0294 | 2.2412 | 2.6118 | LogNormal | 2.2412 | 0.26933 | 1 | 2.9883 |  |  |  | 1.4941 | 0.26933 | 5 | Each (1000 ft duct) | [45 empty] | 1
| D3041.011c |  | D3041.011c | HVAC Galvanized Sheet Metal Ducting less than 6 sq. ft in cross sectional area, SDC D, E, or F | 450 | 650 | 1100 | LogNormal | 680.9247 | 0.36736 | 1 | 715 |  |  |  | 585 | 0.36736 | 5 | Each (1000 ft duct) | 5750 | 6350 | 7400 | LogNormal | 6464.1076 | 0.1002 | 1 | 6985 |  |  |  | 5715 | 0.1002 | 5 | Each (1000 ft duct) | [45 empty] | 0.5294 | 0.7647 | 1.2941 | LogNormal | 0.7647 | 0.44436 | 1 | 0.84117 |  |  |  | 0.68823 | 0.44436 | 5 | Each (1000 ft duct) | 2.0294 | 2.2412 | 2.6118 | LogNormal | 2.2412 | 0.26933 | 1 | 2.9883 |  |  |  | 1.4941 | 0.26933 | 5 | Each (1000 ft duct) | [45 empty] | 1
| D3041.011d |  | D3041.011d | HVAC Galvanized Sheet Metal Ducting less than 6 sq. ft in cross sectional area, SDC D, E, or F (OSHPD or sim) | 450 | 650 | 1100 | LogNormal | 680.9247 | 0.36736 | 1 | 715 |  |  |  | 585 | 0.36736 | 5 | Each (1000 ft duct) | 5750 | 6350 | 7400 | LogNormal | 6464.1076 | 0.1002 | 1 | 6985 |  |  |  | 5715 | 0.1002 | 5 | Each (1000 ft duct) | [45 empty] | 0.5294 | 0.7647 | 1.2941 | LogNormal | 0.7647 | 0.44436 | 1 | 0.84117 |  |  |  | 0.68823 | 0.44436 | 5 | Each (1000 ft duct) | 2.0294 | 2.2412 | 2.6118 | LogNormal | 2.2412 | 0.26933 | 1 | 2.9883 |  |  |  | 1.4941 | 0.26933 | 5 | Each (1000 ft duct) | [45 empty] | 1
| D3041.012a |  | D3041.012a | HVAC Galvanized Sheet Metal Ducting - 6 sq. ft cross sectional area or greater, SDC A or B | 750 | 950 | 1400 | LogNormal | 996.4315 | 0.25596 | 1 | 1045 |  |  |  | 855 | 0.25596 | 5 | Each (1000 ft duct) | 7250 | 7950 | 8900 | LogNormal | 8004.7744 | 0.080554 | 1 | 8745 |  |  |  | 7155 | 0.080554 | 5 | Each (1000 ft duct) | [45 empty] | 0.8824 | 1.1176 | 1.6471 | LogNormal | 1.1176 | 0.35779 | 1 | 1.2294 |  |  |  | 1.0058 | 0.35779 | 5 | Each (1000 ft duct) | 2.5588 | 2.8059 | 3.1412 | LogNormal | 2.8059 | 0.26266 | 1 | 3.7412 |  |  |  | 1.8706 | 0.26266 | 5 | Each (1000 ft duct) | [45 empty] | 1
| D3041.012b |  | D3041.012b | HVAC Galvanized Sheet Metal Ducting - 6 sq. ft cross sectional area or greater, SDC C | 750 | 950 | 1400 | LogNormal | 996.4315 | 0.25596 | 1 | 1045 |  |  |  | 855 | 0.25596 | 5 | Each (1000 ft duct) | 7250 | 7950 | 8900 | LogNormal | 8004.7744 | 0.080554 | 1 | 8745 |  |  |  | 7155 | 0.080554 | 5 | Each (1000 ft duct) | [45 empty] | 0.8824 | 1.1176 | 1.6471 | LogNormal | 1.1176 | 0.35779 | 1 | 1.2294 |  |  |  | 1.0058 | 0.35779 | 5 | Each (1000 ft duct) | 2.5588 | 2.8059 | 3.1412 | LogNormal | 2.8059 | 0.26266 | 1 | 3.7412 |  |  |  | 1.8706 | 0.26266 | 5 | Each (1000 ft duct) | [45 empty] | 1
| D3041.012c |  | D3041.012c | HVAC Galvanized Sheet Metal Ducting - 6 sq. ft cross sectional area or greater, SDC D, E, or F | 750 | 950 | 1400 | LogNormal | 996.4315 | 0.25596 | 1 | 1045 |  |  |  | 855 | 0.25596 | 5 | Each (1000 ft duct) | 7250 | 7950 | 8900 | LogNormal | 8004.7744 | 0.080554 | 1 | 8745 |  |  |  | 7155 | 0.080554 | 5 | Each (1000 ft duct) | [45 empty] | 0.8824 | 1.1176 | 1.6471 | LogNormal | 1.1176 | 0.35779 | 1 | 1.2294 |  |  |  | 1.0058 | 0.35779 | 5 | Each (1000 ft duct) | 2.5588 | 2.8059 | 3.1412 | LogNormal | 2.8059 | 0.26266 | 1 | 3.7412 |  |  |  | 1.8706 | 0.26266 | 5 | Each (1000 ft duct) | [45 empty] | 1
| D3041.012d |  | D3041.012d | HVAC Galvanized Sheet Metal Ducting - 6 sq. ft cross sectional area or greater, SDC D, E, or F (OSHPD or sim) | 750 | 950 | 1400 | LogNormal | 996.4315 | 0.25596 | 1 | 1045 |  |  |  | 855 | 0.25596 | 5 | Each (1000 ft duct) | 7250 | 7950 | 8900 | LogNormal | 8004.7744 | 0.080554 | 1 | 8745 |  |  |  | 7155 | 0.080554 | 5 | Each (1000 ft duct) | [45 empty] | 0.8824 | 1.1176 | 1.6471 | LogNormal | 1.1176 | 0.35779 | 1 | 1.2294 |  |  |  | 1.0058 | 0.35779 | 5 | Each (1000 ft duct) | 2.5588 | 2.8059 | 3.1412 | LogNormal | 2.8059 | 0.26266 | 1 | 3.7412 |  |  |  | 1.8706 | 0.26266 | 5 | Each (1000 ft duct) | [45 empty] | 1
| D3041.021a |  | D3041.021a | HVAC Stainless Steel Ducting less than 6 sq. ft in cross sectional area, SDC A or B | 1050 | 1250 | 1700 | LogNormal | 1305.037 | 0.19643 | 1 | 1375 |  |  |  | 1125 | 0.19643 | 5 | Each (1000 ft duct) | 12750 | 15950 | 20400 | LogNormal | 16064.0774 | 0.18473 | 1 | 17545 |  |  |  | 14355 | 0.18473 | 5 | Each (1000 ft duct) | [45 empty] | 1.2353 | 1.4706 | 2 | LogNormal | 1.4706 | 0.31794 | 1 | 1.6177 |  |  |  | 1.3235 | 0.31794 | 5 | Each (1000 ft duct) | 4.5 | 5.6294 | 7.2 | LogNormal | 5.6294 | 0.31085 | 1 | 7.5059 |  |  |  | 3.7529 | 0.31085 | 5 | Each (1000 ft duct) | [45 empty] | 1
| D3041.021b |  | D3041.021b | HVAC Stainless Steel Ducting less than 6 sq. ft in cross sectional area, SDC C | 1050 | 1250 | 1700 | LogNormal | 1305.037 | 0.19643 | 1 | 1375 |  |  |  | 1125 | 0.19643 | 5 | Each (1000 ft duct) | 12750 | 15950 | 20400 | LogNormal | 16064.0774 | 0.18473 | 1 | 17545 |  |  |  | 14355 | 0.18473 | 5 | Each (1000 ft duct) | [45 empty] | 1.2353 | 1.4706 | 2 | LogNormal | 1.4706 | 0.31794 | 1 | 1.6177 |  |  |  | 1.3235 | 0.31794 | 5 | Each (1000 ft duct) | 4.5 | 5.6294 | 7.2 | LogNormal | 5.6294 | 0.31085 | 1 | 7.5059 |  |  |  | 3.7529 | 0.31085 | 5 | Each (1000 ft duct) | [45 empty] | 1
| D3041.021c |  | D3041.021c | HVAC Stainless Steel Ducting less than 6 sq. ft in cross sectional area, SDC D, E, or F | 1050 | 1250 | 1700 | LogNormal | 1305.037 | 0.19643 | 1 | 1375 |  |  |  | 1125 | 0.19643 | 5 | Each (1000 ft duct) | 12750 | 15950 | 20400 | LogNormal | 16064.0774 | 0.18473 | 1 | 17545 |  |  |  | 14355 | 0.18473 | 5 | Each (1000 ft duct) | [45 empty] | 1.1581 | 1.3787 | 1.875 | LogNormal | 1.3787 | 0.31794 | 1 | 1.5166 |  |  |  | 1.2408 | 0.31794 | 5 | Each (1000 ft duct) | 14.0625 | 17.5919 | 22.5 | LogNormal | 17.5919 | 0.31085 | 1 | 19.3511 |  |  |  | 15.8327 | 0.31085 | 5 | Each (1000 ft duct) | [45 empty] | 1
| D3041.021d |  | D3041.021d | HVAC Stainless Steel Ducting less than 6 sq. ft in cross sectional area, SDC D, E, or F (OSHPD or sim) | 1050 | 1250 | 1700 | LogNormal | 1305.037 | 0.19643 | 1 | 1375 |  |  |  | 1125 | 0.19643 | 5 | Each (1000 ft duct) | 12750 | 15950 | 20400 | LogNormal | 16064.0774 | 0.18473 | 1 | 17545 |  |  |  | 14355 | 0.18473 | 5 | Each (1000 ft duct) | [45 empty] | 1.1581 | 1.3787 | 1.875 | LogNormal | 1.3787 | 0.31794 | 1 | 1.5166 |  |  |  | 1.2408 | 0.31794 | 5 | Each (1000 ft duct) | 14.0625 | 17.5919 | 22.5 | LogNormal | 17.5919 | 0.31085 | 1 | 19.3511 |  |  |  | 15.8327 | 0.31085 | 5 | Each (1000 ft duct) | [45 empty] | 1
| D3041.022a |  | D3041.022a | HVAC Stainless Steel Ducting - 6 sq. ft cross sectional area or greater, SDC A or B | 1750 | 1950 | 2400 | LogNormal | 2015.1129 | 0.12735 | 1 | 2145 |  |  |  | 1755 | 0.12735 | 5 | Each (1000 ft duct) | 19250 | 21450 | 26900 | LogNormal | 22303.4545 | 0.13575 | 1 | 23595 |  |  |  | 19305 | 0.13575 | 5 | Each (1000 ft duct) | [45 empty] | 1.9301 | 2.1507 | 2.6471 | LogNormal | 2.1507 | 0.28057 | 1 | 2.3658 |  |  |  | 1.9356 | 0.28057 | 5 | Each (1000 ft duct) | 21.2316 | 23.6581 | 29.6691 | LogNormal | 23.6581 | 0.28448 | 1 | 26.0239 |  |  |  | 21.2923 | 0.28448 | 5 | Each (1000 ft duct) | [45 empty] | 1
| D3041.022b |  | D3041.022b | HVAC Stainless Steel Ducting - 6 sq. ft cross sectional area or greater, SDC C | 1750 | 1950 | 2400 | LogNormal | 2015.1129 | 0.12735 | 1 | 2145 |  |  |  | 1755 | 0.12735 | 5 | Each (1000 ft duct) | 19250 | 21450 | 26900 | LogNormal | 22303.4545 | 0.13575 | 1 | 23595 |  |  |  | 19305 | 0.13575 | 5 | Each (1000 ft duct) | [45 empty] | 1.9301 | 2.1507 | 2.6471 | LogNormal | 2.1507 | 0.28057 | 1 | 2.3658 |  |  |  | 1.9356 | 0.28057 | 5 | Each (1000 ft duct) | 21.2316 | 23.6581 | 29.6691 | LogNormal | 23.6581 | 0.28448 | 1 | 26.0239 |  |  |  | 21.2923 | 0.28448 | 5 | Each (1000 ft duct) | [45 empty] | 1
| D3041.022c |  | D3041.022c | HVAC Stainless Steel Ducting - 6 sq. ft cross sectional area or greater, SDC D, E, or F | 1750 | 1950 | 2400 | LogNormal | 2015.1129 | 0.12735 | 1 | 2145 |  |  |  | 1755 | 0.12735 | 5 | Each (1000 ft duct) | 19250 | 21450 | 26900 | LogNormal | 22303.4545 | 0.13575 | 1 | 23595 |  |  |  | 19305 | 0.13575 | 5 | Each (1000 ft duct) | [45 empty] | 1.9301 | 2.1507 | 2.6471 | LogNormal | 2.1507 | 0.28057 | 1 | 2.3658 |  |  |  | 1.9356 | 0.28057 | 5 | Each (1000 ft duct) | 21.2316 | 23.6581 | 29.6691 | LogNormal | 23.6581 | 0.28448 | 1 | 26.0239 |  |  |  | 21.2923 | 0.28448 | 5 | Each (1000 ft duct) | [45 empty] | 1
| D3041.022d |  | D3041.022d | HVAC Stainless Steel Ducting - 6 sq. ft cross sectional area or greater, SDC D, E, or F (OSHPD or sim) | 1750 | 1950 | 2400 | LogNormal | 2015.1129 | 0.12735 | 1 | 2145 |  |  |  | 1755 | 0.12735 | 5 | Each (1000 ft duct) | 19250 | 21450 | 26900 | LogNormal | 22303.4545 | 0.13575 | 1 | 23595 |  |  |  | 19305 | 0.13575 | 5 | Each (1000 ft duct) | [45 empty] | 1.9301 | 2.1507 | 2.6471 | LogNormal | 2.1507 | 0.28057 | 1 | 2.3658 |  |  |  | 1.9356 | 0.28057 | 5 | Each (1000 ft duct) | 21.2316 | 23.6581 | 29.6691 | LogNormal | 23.6581 | 0.28448 | 1 | 26.0239 |  |  |  | 21.2923 | 0.28448 | 5 | Each (1000 ft duct) | [45 empty] | 1
| D3041.031a |  | D3041.031a | HVAC Drops / Diffusers in suspended ceilings - No independent safety wires, SDC A or B | 2000 | 3000 | 3500 | Normal | 2833.3333 | 0.20655 | 1 | 3300 |  |  |  | 2700 | 0.20655 | 5 | 10 Units | [60 empty] | 2.353 | 3.529 | 4.118 | Normal | 3.529 | 0.32429 | 1 | 3.8819 |  |  |  | 3.1761 | 0.32429 | 5 | 10 Units | [60 empty] | 10
| D3041.031b |  | D3041.031b | HVAC Drops / Diffusers in suspended ceilings - No independent safety wires, SDC C | 2000 | 3000 | 3500 | Normal | 2833.3333 | 0.20655 | 1 | 3300 |  |  |  | 2700 | 0.20655 | 5 | 10 Units | [60 empty] | 2.353 | 3.529 | 4.118 | Normal | 3.529 | 0.32429 | 1 | 3.8819 |  |  |  | 3.1761 | 0.32429 | 5 | 10 Units | [60 empty] | 10
| D3041.032a |  | D3041.032a | HVAC Drops / Diffusers without ceilings - supported by ducting only - No independent safety wires, SDC A or B | 2000 | 3000 | 3500 | Normal | 2833.3333 | 0.20655 | 1 | 3300 |  |  |  | 2700 | 0.20655 | 5 | 10 Units | [60 empty] | 2.353 | 3.529 | 4.118 | Normal | 3.529 | 0.32429 | 1 | 3.8819 |  |  |  | 3.1761 | 0.32429 | 5 | 10 Units | [60 empty] | 10
| D3041.032b |  | D3041.032b | HVAC Drops / Diffusers without ceilings - supported by ducting only - No independent safety wires, SDC C | 2000 | 3000 | 3500 | Normal | 2833.3333 | 0.20655 | 1 | 3300 |  |  |  | 2700 | 0.20655 | 5 | 10 Units | [60 empty] | 2.353 | 3.529 | 4.118 | Normal | 3.529 | 0.32429 | 1 | 3.8819 |  |  |  | 3.1761 | 0.32429 | 5 | 10 Units | [60 empty] | 10
| D3041.032c |  | D3041.032c | HVAC Drops / Diffusers without ceilings - supported by ducting only - No independent safety wires, SDC D, E, or F | 2000 | 3000 | 3500 | Normal | 2833.3333 | 0.20655 | 1 | 3300 |  |  |  | 2700 | 0.20655 | 5 | 10 Units | [60 empty] | 2.353 | 3.529 | 4.118 | Normal | 3.529 | 0.32429 | 1 | 3.8819 |  |  |  | 3.1761 | 0.32429 | 5 | 10 Units | [60 empty] | 10
| D3041.032d |  | D3041.032d | HVAC Drops / Diffusers without ceilings - supported by ducting only - No independent safety wires, SDC D, E, or F (OSHPD or sim) | 2000 | 3000 | 3500 | Normal | 2833.3333 | 0.20655 | 1 | 3300 |  |  |  | 2700 | 0.20655 | 5 | 10 Units | [60 empty] | 2.353 | 3.529 | 4.118 | Normal | 3.529 | 0.32429 | 1 | 3.8819 |  |  |  | 3.1761 | 0.32429 | 5 | 10 Units | [60 empty] | 10
| D3041.041a |  | D3041.041a | Variable Air Volume (VAV) box with in-line coil, SDC A or B | 10000 | 15000 | 21500 | LogNormal | 14795.7029 | 0.29415 | 1 | 16500 |  |  |  | 13500 | 0.29415 | 5 | 10 Units | [60 empty] | 11.765 | 17.647 | 25.294 | LogNormal | 17.647 | 0.38604 | 1 | 19.4117 |  |  |  | 15.8823 | 0.38604 | 5 | 10 Units | [60 empty] | 10
| D3041.041b |  | D3041.041b | Variable Air Volume (VAV) box with in-line coil, SDC C | 10000 | 15000 | 21500 | LogNormal | 14795.7029 | 0.29415 | 1 | 16500 |  |  |  | 13500 | 0.29415 | 5 | 10 Units | [60 empty] | 11.765 | 17.647 | 25.294 | LogNormal | 17.647 | 0.38604 | 1 | 19.4117 |  |  |  | 15.8823 | 0.38604 | 5 | 10 Units | [60 empty] | 10
| D3041.101a |  | D3041.101a | HVAC Fan - Capacity: all - Unanchored equipment that is not vibration isolated - Equipment fragility only | 2200 | 2650 | 3150 | LogNormal | 2638.5725 | 0.13942 | 1 | 2915 |  |  |  | 2385 | 0.13942 | 5 | Each | [60 empty] | 2.5882 | 3.1176 | 3.7059 | LogNormal | 3.1176 | 0.28625 | 1 | 3.4294 |  |  |  | 2.8058 | 0.28625 | 5 | Each | [60 empty] | 1
| D3041.102a |  | D3041.102a | HVAC Fan - Capacity: all - Vibration isolated equipment that is not snubbed or restrained - Anchorage fragility only | 500 | 700 | 1150 | LogNormal | 734.2915 | 0.34252 | 1 | 770 |  |  |  | 630 | 0.34252 | 5 | Each | 2700 | 3350 | 4300 | LogNormal | 3386.8507 | 0.18362 | 1 | 3685 |  |  |  | 3015 | 0.18362 | 5 | Each | [45 empty] | 0.5882 | 0.8235 | 1.3529 | LogNormal | 0.8235 | 0.42405 | 1 | 0.90585 |  |  |  | 0.74115 | 0.42405 | 5 | Each | 0.3176 | 0.3941 | 0.5059 | LogNormal | 0.3941 | 0.31019 | 1 | 0.78822 |  |  |  | 0.19705 | 0.31019 | 5 | Each | [45 empty] | 1
| D3041.102b |  | D3041.102b | HVAC Fan - Capacity: all - Vibration isolated equipment that is not snubbed or restrained - Equipment fragility only | 2200 | 2650 | 3150 | LogNormal | 2638.5725 | 0.13942 | 1 | 2915 |  |  |  | 2385 | 0.13942 | 5 | Each | [60 empty] | 2.5882 | 3.1176 | 3.7059 | LogNormal | 3.1176 | 0.28625 | 1 | 3.4294 |  |  |  | 2.8058 | 0.28625 | 5 | Each | [60 empty] | 1
| D3041.102c |  | D3041.102c | HVAC Fan - Capacity: all - Vibration isolated equipment that is not snubbed or restrained - Combined anchorage/isolator & equipment fragility | 500 | 700 | 1150 | LogNormal | 734.2915 | 0.34252 | 1 | 770 |  |  |  | 630 | 0.34252 | 5 | Each | 2700 | 3350 | 4300 | LogNormal | 3386.8507 | 0.18362 | 1 | 3685 |  |  |  | 3015 | 0.18362 | 5 | Each | 2200 | 2650 | 3150 | LogNormal | 2638.5725 | 0.13942 | 1 | 2915 |  |  |  | 2385 | 0.13942 | 5 | Each | [30 empty] | 0.5882 | 0.8235 | 1.3529 | LogNormal | 0.8235 | 0.42405 | 1 | 0.90585 |  |  |  | 0.74115 | 0.42405 | 5 | Each | 0.3176 | 0.3941 | 0.5059 | LogNormal | 0.3941 | 0.31019 | 1 | 0.78822 |  |  |  | 0.19705 | 0.31019 | 5 | Each | 2.5882 | 3.1176 | 3.7059 | LogNormal | 3.1176 | 0.28625 | 1 | 3.4294 |  |  |  | 2.8058 | 0.28625 | 5 | Each | [30 empty] | 1
| D3041.103a |  | D3041.103a | HVAC Fan - Capacity: all - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only | 500 | 700 | 1150 | LogNormal | 734.2915 | 0.34252 | 1 | 770 |  |  |  | 630 | 0.34252 | 5 | Each | 2700 | 3350 | 4300 | LogNormal | 3386.8507 | 0.18362 | 1 | 3685 |  |  |  | 3015 | 0.18362 | 5 | Each | [45 empty] | 0.5882 | 0.8235 | 1.3529 | LogNormal | 0.8235 | 0.42405 | 1 | 0.90585 |  |  |  | 0.74115 | 0.42405 | 5 | Each | 0.3176 | 0.3941 | 0.5059 | LogNormal | 0.3941 | 0.31019 | 1 | 0.78822 |  |  |  | 0.19705 | 0.31019 | 5 | Each | [45 empty] | 1
| D3041.103b |  | D3041.103b | HVAC Fan - Capacity: all - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only | 2200 | 2650 | 3150 | LogNormal | 2638.5725 | 0.13942 | 1 | 2915 |  |  |  | 2385 | 0.13942 | 5 | Each | [60 empty] | 2.5882 | 3.1176 | 3.7059 | LogNormal | 3.1176 | 0.28625 | 1 | 3.4294 |  |  |  | 2.8058 | 0.28625 | 5 | Each | [60 empty] | 1
| D3041.103c |  | D3041.103c | HVAC Fan - Capacity: all - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | 500 | 700 | 1150 | LogNormal | 734.2915 | 0.34252 | 1 | 770 |  |  |  | 630 | 0.34252 | 5 | Each | 2700 | 3350 | 4300 | LogNormal | 3386.8507 | 0.18362 | 1 | 3685 |  |  |  | 3015 | 0.18362 | 5 | Each | 2200 | 2650 | 3150 | LogNormal | 2638.5725 | 0.13942 | 1 | 2915 |  |  |  | 2385 | 0.13942 | 5 | Each | [30 empty] | 0.5882 | 0.8235 | 1.3529 | LogNormal | 0.8235 | 0.42405 | 1 | 0.90585 |  |  |  | 0.74115 | 0.42405 | 5 | Each | 0.3176 | 0.3941 | 0.5059 | LogNormal | 0.3941 | 0.31019 | 1 | 0.78822 |  |  |  | 0.19705 | 0.31019 | 5 | Each | 2.5882 | 3.1176 | 3.7059 | LogNormal | 3.1176 | 0.28625 | 1 | 3.4294 |  |  |  | 2.8058 | 0.28625 | 5 | Each | [30 empty] | 1
| D3052.011a |  | D3052.011a | Air Handling Unit - Capacity: <5000 CFM - Unanchored equipment that is not vibration isolated - Equipment fragility only | 900 | 1000 | 1300 | LogNormal | 1053.1335 | 0.15108 | 1 | 1100 |  |  |  | 900 | 0.15108 | 5 | Each | 25100 | 29200 | 37800 | LogNormal | 30237.1542 | 0.16549 | 1 | 32120 |  |  |  | 26280 | 0.16549 | 5 | Each | [45 empty] | 0.3176 | 0.3529 | 0.4588 | LogNormal | 0.3529 | 0.2921 | 1 | 0.47055 |  |  |  | 0.23525 | 0.2921 | 5 | Each | 5.9059 | 6.8706 | 8.8941 | LogNormal | 6.8706 | 0.29981 | 1 | 10.3059 |  |  |  | 3.4353 | 0.29981 | 5 | Each | [45 empty] | 1
| D3052.011b |  | D3052.011b | Air Handling Unit - Capacity: 5000 to <10000 CFM - Unanchored equipment that is not vibration isolated - Equipment fragility only | 1300 | 1500 | 2000 | LogNormal | 1572.5169 | 0.17627 | 1 | 1650 |  |  |  | 1350 | 0.17627 | 5 | Each | 50500 | 59000 | 77300 | LogNormal | 61246.4427 | 0.1725 | 1 | 64900 |  |  |  | 53100 | 0.1725 | 5 | Each | [45 empty] | 0.4588 | 0.5294 | 0.7059 | LogNormal | 0.5294 | 0.30589 | 1 | 0.70587 |  |  |  | 0.35293 | 0.30589 | 5 | Each | 8.9118 | 10.4118 | 13.6412 | LogNormal | 10.4118 | 0.30374 | 1 | 17.353 |  |  |  | 5.2059 | 0.30374 | 5 | Each | [45 empty] | 1
| D3052.011c |  | D3052.011c | Air Handling Unit - Capacity: 10000 to <25000 CFM - Unanchored equipment that is not vibration isolated - Equipment fragility only | 1700 | 2000 | 2600 | LogNormal | 2066.1278 | 0.17133 | 1 | 2200 |  |  |  | 1800 | 0.17133 | 5 | Each | 106200 | 125200 | 163600 | LogNormal | 129465.7332 | 0.17442 | 1 | 137720 |  |  |  | 112680 | 0.17442 | 5 | Each | [45 empty] | 2 | 2.3529 | 3.0588 | LogNormal | 2.3529 | 0.30308 | 1 | 2.5882 |  |  |  | 2.1176 | 0.30308 | 5 | Each | 12.4941 | 14.7294 | 19.2471 | LogNormal | 14.7294 | 0.30483 | 1 | 29.4588 |  |  |  | 7.3647 | 0.30483 | 5 | Each | [45 empty] | 1
| D3052.011d |  | D3052.011d | Air Handling Unit - Capacity: 25000 to <40000 CFM - Unanchored equipment that is not vibration isolated - Equipment fragility only | 1700 | 2000 | 2600 | LogNormal | 2066.1278 | 0.17133 | 1 | 2200 |  |  |  | 1800 | 0.17133 | 5 | Each | 157500 | 186000 | 242800 | LogNormal | 192163.0648 | 0.17455 | 1 | 204600 |  |  |  | 167400 | 0.17455 | 5 | Each | [45 empty] | 2 | 2.3529 | 3.0588 | LogNormal | 2.3529 | 0.30308 | 1 | 2.5882 |  |  |  | 2.1176 | 0.30308 | 5 | Each | 12.9706 | 15.3176 | 19.9953 | LogNormal | 15.3176 | 0.30491 | 1 | 37.2 |  |  |  | 7.6588 | 0.30491 | 5 | Each | [45 empty] | 1
| D3052.013a |  | D3052.013a | Air Handling Unit - Capacity: <5000 CFM - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only | 500 | 1000 | 1700 | LogNormal | 958.6389 | 0.45231 | 1 | 1100 |  |  |  | 900 | 0.45231 | 5 | Each | 25600 | 30200 | 39500 | LogNormal | 31231.6205 | 0.17508 | 1 | 33220 |  |  |  | 27180 | 0.17508 | 5 | Each | [45 empty] | 0.5882 | 1.1765 | 2 | LogNormal | 1.1765 | 0.5168 | 1 | 1.2941 |  |  |  | 1.0589 | 0.5168 | 5 | Each | 6.0235 | 7.1059 | 9.2941 | LogNormal | 7.1059 | 0.30521 | 1 | 10.6588 |  |  |  | 3.553 | 0.30521 | 5 | Each | [45 empty] | 1
| D3052.013b |  | D3052.013b | Air Handling Unit - Capacity: <5000 CFM - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only | 900 | 1000 | 1300 | LogNormal | 1053.1335 | 0.15108 | 1 | 1100 |  |  |  | 900 | 0.15108 | 5 | Each | 25100 | 29200 | 37800 | LogNormal | 30237.1542 | 0.16549 | 1 | 32120 |  |  |  | 26280 | 0.16549 | 5 | Each | [45 empty] | 0.3176 | 0.3529 | 0.4588 | LogNormal | 0.3529 | 0.2921 | 1 | 0.47055 |  |  |  | 0.23525 | 0.2921 | 5 | Each | 5.9059 | 6.8706 | 8.8941 | LogNormal | 6.8706 | 0.29981 | 1 | 10.3059 |  |  |  | 3.4353 | 0.29981 | 5 | Each | [45 empty] | 1
| D3052.013c |  | D3052.013c | Air Handling Unit - Capacity: <5000 CFM - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | 500 | 1000 | 1700 | LogNormal | 958.6389 | 0.45231 | 1 | 1100 |  |  |  | 900 | 0.45231 | 5 | Each | 25600 | 30200 | 39500 | LogNormal | 31231.6205 | 0.17508 | 1 | 33220 |  |  |  | 27180 | 0.17508 | 5 | Each | 900 | 1000 | 1300 | LogNormal | 1053.1335 | 0.15108 | 1 | 1100 |  |  |  | 900 | 0.15108 | 5 | Each | 25100 | 29200 | 37800 | LogNormal | 30237.1542 | 0.16549 | 1 | 32120 |  |  |  | 26280 | 0.16549 | 5 | Each | [15 empty] | 0.5882 | 1.1765 | 2 | LogNormal | 1.1765 | 0.5168 | 1 | 1.2941 |  |  |  | 1.0589 | 0.5168 | 5 | Each | 6.0235 | 7.1059 | 9.2941 | LogNormal | 7.1059 | 0.30521 | 1 | 10.6588 |  |  |  | 3.553 | 0.30521 | 5 | Each | 0.2118 | 0.2353 | 0.3059 | LogNormal | 0.2353 | 0.2921 | 1 | 0.35295 |  |  |  | 0.11765 | 0.2921 | 5 | Each | 5.9059 | 6.8706 | 8.8941 | LogNormal | 6.8706 | 0.29981 | 1 | 10.3059 |  |  |  | 3.4353 | 0.29981 | 5 | Each | [15 empty] | 1
| D3052.013d |  | D3052.013d | Air Handling Unit - Capacity: 5000 to <10000 CFM - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only | 800 | 1500 | 2400 | Normal | 1566.6663 | 0.39845 | 1 | 1650 |  |  |  | 1350 | 0.39845 | 5 | Each | 51300 | 60500 | 79700 | LogNormal | 62717.7048 | 0.17829 | 1 | 66550 |  |  |  | 54450 | 0.17829 | 5 | Each | [45 empty] | 0.9412 | 1.7647 | 2.8235 | Normal | 1.7647 | 0.47039 | 1 | 1.9412 |  |  |  | 1.5882 | 0.47039 | 5 | Each | 9.0529 | 10.6765 | 14.0647 | LogNormal | 10.6765 | 0.30706 | 1 | 17.7941 |  |  |  | 5.3383 | 0.30706 | 5 | Each | [45 empty] | 1
| D3052.013e |  | D3052.013e | Air Handling Unit - Capacity: 5000 to <10000 CFM - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only | 1300 | 1500 | 2000 | LogNormal | 1572.5169 | 0.17627 | 1 | 1650 |  |  |  | 1350 | 0.17627 | 5 | Each | 50500 | 59000 | 77300 | LogNormal | 61246.4427 | 0.1725 | 1 | 64900 |  |  |  | 53100 | 0.1725 | 5 | Each | [45 empty] | 0.4588 | 0.5294 | 0.7059 | LogNormal | 0.5294 | 0.30589 | 1 | 0.70587 |  |  |  | 0.35293 | 0.30589 | 5 | Each | 8.9118 | 10.4118 | 13.6412 | LogNormal | 10.4118 | 0.30374 | 1 | 17.353 |  |  |  | 5.2059 | 0.30374 | 5 | Each | [45 empty] | 1
| D3052.013f |  | D3052.013f | Air Handling Unit - Capacity: 5000 to <10000 CFM - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | 800 | 1500 | 2400 | Normal | 1566.6663 | 0.39845 | 1 | 1650 |  |  |  | 1350 | 0.39845 | 5 | Each | 51300 | 60500 | 79700 | LogNormal | 62717.7048 | 0.17829 | 1 | 66550 |  |  |  | 54450 | 0.17829 | 5 | Each | 1300 | 1500 | 2000 | LogNormal | 1572.5169 | 0.17627 | 1 | 1650 |  |  |  | 1350 | 0.17627 | 5 | Each | 50500 | 59000 | 77300 | LogNormal | 61246.4427 | 0.1725 | 1 | 64900 |  |  |  | 53100 | 0.1725 | 5 | Each | [15 empty] | 0.9412 | 1.7647 | 2.8235 | Normal | 1.7647 | 0.47039 | 1 | 1.9412 |  |  |  | 1.5882 | 0.47039 | 5 | Each | 9.0529 | 10.6765 | 14.0647 | LogNormal | 10.6765 | 0.30706 | 1 | 17.7941 |  |  |  | 5.3383 | 0.30706 | 5 | Each | 0.3059 | 0.3529 | 0.4706 | LogNormal | 0.3529 | 0.30589 | 1 | 0.52937 |  |  |  | 0.17645 | 0.30589 | 5 | Each | 8.9118 | 10.4118 | 13.6412 | LogNormal | 10.4118 | 0.30374 | 1 | 17.353 |  |  |  | 5.2059 | 0.30374 | 5 | Each | [15 empty] | 1
| D3052.013g |  | D3052.013g | Air Handling Unit - Capacity: 10000 to <25000 CFM - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only | 1400 | 2200 | 3100 | Normal | 2233.3322 | 0.29698 | 1 | 2420 |  |  |  | 1980 | 0.29698 | 5 | Each | 107600 | 127400 | 166700 | LogNormal | 131608.809 | 0.17654 | 1 | 140140 |  |  |  | 114660 | 0.17654 | 5 | Each | [45 empty] | 0.4941 | 0.7765 | 1.0941 | Normal | 0.7765 | 0.3882 | 1 | 1.0353 |  |  |  | 0.51768 | 0.3882 | 5 | Each | 12.6588 | 14.9882 | 19.6118 | LogNormal | 14.9882 | 0.30605 | 1 | 29.9764 |  |  |  | 7.4941 | 0.30605 | 5 | Each | [45 empty] | 1
| D3052.013h |  | D3052.013h | Air Handling Unit - Capacity: 10000 to <25000 CFM - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only | 1700 | 2000 | 2600 | LogNormal | 2066.1278 | 0.17133 | 1 | 2200 |  |  |  | 1800 | 0.17133 | 5 | Each | 106200 | 125200 | 163600 | LogNormal | 129465.7332 | 0.17442 | 1 | 137720 |  |  |  | 112680 | 0.17442 | 5 | Each | [45 empty] | 2 | 2.3529 | 3.0588 | LogNormal | 2.3529 | 0.30308 | 1 | 2.5882 |  |  |  | 2.1176 | 0.30308 | 5 | Each | 12.4941 | 14.7294 | 19.2471 | LogNormal | 14.7294 | 0.30483 | 1 | 29.4588 |  |  |  | 7.3647 | 0.30483 | 5 | Each | [45 empty] | 1
| D3052.013i |  | D3052.013i | Air Handling Unit - Capacity: 10000 to <25000 CFM - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | 1400 | 2200 | 3100 | Normal | 2233.3322 | 0.29698 | 1 | 2420 |  |  |  | 1980 | 0.29698 | 5 | Each | 107600 | 127400 | 166700 | LogNormal | 131608.809 | 0.17654 | 1 | 140140 |  |  |  | 114660 | 0.17654 | 5 | Each | 1700 | 2000 | 2600 | LogNormal | 2066.1278 | 0.17133 | 1 | 2200 |  |  |  | 1800 | 0.17133 | 5 | Each | 106200 | 125200 | 163600 | LogNormal | 129465.7332 | 0.17442 | 1 | 137720 |  |  |  | 112680 | 0.17442 | 5 | Each | [15 empty] | 1.6471 | 2.5882 | 3.6471 | Normal | 2.5882 | 0.3882 | 1 | 2.847 |  |  |  | 2.3294 | 0.3882 | 5 | Each | 12.6588 | 14.9882 | 19.6118 | LogNormal | 14.9882 | 0.30605 | 1 | 29.9764 |  |  |  | 7.4941 | 0.30605 | 5 | Each | 2 | 2.3529 | 3.0588 | LogNormal | 2.3529 | 0.30308 | 1 | 2.5882 |  |  |  | 2.1176 | 0.30308 | 5 | Each | 12.4941 | 14.7294 | 19.2471 | LogNormal | 14.7294 | 0.30483 | 1 | 29.4588 |  |  |  | 7.3647 | 0.30483 | 5 | Each | [15 empty] | 1
| D3052.013j |  | D3052.013j | Air Handling Unit - Capacity: 25000 to <40000 CFM - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only | 1600 | 2400 | 3400 | LogNormal | 2358.8816 | 0.28852 | 1 | 2640 |  |  |  | 2160 | 0.28852 | 5 | Each | 159100 | 188400 | 246200 | LogNormal | 194535.2211 | 0.17599 | 1 | 207240 |  |  |  | 169560 | 0.17599 | 5 | Each | [45 empty] | 0.5647 | 0.8471 | 1.2 | LogNormal | 0.8471 | 0.38177 | 1 | 1.1295 |  |  |  | 0.56475 | 0.38177 | 5 | Each | 13.1024 | 15.5153 | 20.2753 | LogNormal | 15.5153 | 0.30573 | 1 | 37.68 |  |  |  | 7.7576 | 0.30573 | 5 | Each | [45 empty] | 1
| D3052.013k |  | D3052.013k | Air Handling Unit - Capacity: 25000 to <40000 CFM - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only | 1700 | 2000 | 2600 | LogNormal | 2066.1278 | 0.17133 | 1 | 2200 |  |  |  | 1800 | 0.17133 | 5 | Each | 157500 | 186000 | 242800 | LogNormal | 192163.0648 | 0.17455 | 1 | 204600 |  |  |  | 167400 | 0.17455 | 5 | Each | [45 empty] | 2 | 2.3529 | 3.0588 | LogNormal | 2.3529 | 0.30308 | 1 | 2.5882 |  |  |  | 2.1176 | 0.30308 | 5 | Each | 12.9706 | 15.3176 | 19.9953 | LogNormal | 15.3176 | 0.30491 | 1 | 37.2 |  |  |  | 7.6588 | 0.30491 | 5 | Each | [45 empty] | 1
| D3052.013l |  | D3052.013l | Air Handling Unit - Capacity: 25000 to <40000 CFM - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | 1600 | 2400 | 3400 | LogNormal | 2358.8816 | 0.28852 | 1 | 2640 |  |  |  | 2160 | 0.28852 | 5 | Each | 159100 | 188400 | 246200 | LogNormal | 194535.2211 | 0.17599 | 1 | 207240 |  |  |  | 169560 | 0.17599 | 5 | Each | 1700 | 2000 | 2600 | LogNormal | 2066.1278 | 0.17133 | 1 | 2200 |  |  |  | 1800 | 0.17133 | 5 | Each | 157500 | 186000 | 242800 | LogNormal | 192163.0648 | 0.17455 | 1 | 204600 |  |  |  | 167400 | 0.17455 | 5 | Each | [15 empty] | 1.8824 | 2.8235 | 4 | LogNormal | 2.8235 | 0.38177 | 1 | 3.1059 |  |  |  | 2.5411 | 0.38177 | 5 | Each | 13.1024 | 15.5153 | 20.2753 | LogNormal | 15.5153 | 0.30573 | 1 | 37.68 |  |  |  | 7.7576 | 0.30573 | 5 | Each | 2 | 2.3529 | 3.0588 | LogNormal | 2.3529 | 0.30308 | 1 | 2.5882 |  |  |  | 2.1176 | 0.30308 | 5 | Each | 12.9706 | 15.3176 | 19.9953 | LogNormal | 15.3176 | 0.30491 | 1 | 37.2 |  |  |  | 7.6588 | 0.30491 | 5 | Each | [15 empty] | 1
| D3067.011a |  | D3067.011a | Control Panel - Capacity: all - Unanchored equipment that is not vibration isolated - Equipment fragility only | 3200 | 4150 | 5150 | Normal | 4166.6673 | 0.18259 | 1 | 4565 |  |  |  | 3735 | 0.18259 | 5 | Each | [60 empty] | 3.7647 | 4.8824 | 6.0588 | Normal | 4.8824 | 0.30958 | 1 | 5.3706 |  |  |  | 4.3942 | 0.30958 | 5 | Each | [60 empty] | 1
| D3067.012a |  | D3067.012a | Control Panel - Capacity: all - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only | 300 | 500 | 650 | Normal | 483.3331 | 0.28252 | 1 | 550 |  |  |  | 450 | 0.28252 | 5 | Each | 3500 | 4650 | 5800 | Normal | 4649.9977 | 0.19298 | 1 | 5115 |  |  |  | 4185 | 0.19298 | 5 | Each | [45 empty] | 0.1059 | 0.1765 | 0.2294 | Normal | 0.1765 | 0.37725 | 1 | 0.23532 |  |  |  | 0.11768 | 0.37725 | 5 | Each | 4.1176 | 5.4706 | 6.8235 | Normal | 5.4706 | 0.31582 | 1 | 6.0177 |  |  |  | 4.9235 | 0.31582 | 5 | Each | [45 empty] | 1
| D3067.012b |  | D3067.012b | Control Panel - Capacity: all - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only | 3200 | 4150 | 5150 | Normal | 4166.6673 | 0.18259 | 1 | 4565 |  |  |  | 3735 | 0.18259 | 5 | Each | [60 empty] | 1.1294 | 1.4647 | 1.8176 | Normal | 1.4647 | 0.30958 | 1 | 1.9529 |  |  |  | 0.97646 | 0.30958 | 5 | Each | [60 empty] | 1
| D3067.012c |  | D3067.012c | Control Panel - Capacity: all - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | 300 | 500 | 650 | Normal | 483.3331 | 0.28252 | 1 | 550 |  |  |  | 450 | 0.28252 | 5 | Each | 3500 | 4650 | 5800 | Normal | 4649.9977 | 0.19298 | 1 | 5115 |  |  |  | 4185 | 0.19298 | 5 | Each | 3200 | 4150 | 5150 | Normal | 4166.6679 | 0.18259 | 1 | 4565 |  |  |  | 3735 | 0.18259 | 5 | Each | [30 empty] | 0.1059 | 0.1765 | 0.2294 | Normal | 0.1765 | 0.37725 | 1 | 0.23532 |  |  |  | 0.11768 | 0.37725 | 5 | Each | 4.1176 | 5.4706 | 6.8235 | Normal | 5.4706 | 0.31582 | 1 | 6.0177 |  |  |  | 4.9235 | 0.31582 | 5 | Each | 3.7647 | 4.8824 | 6.0588 | Normal | 4.8824 | 0.30958 | 1 | 5.3706 |  |  |  | 4.3942 | 0.30958 | 5 | Each | [30 empty] | 1
| D4011.021a |  | D4011.021a | Fire Sprinkler Water Piping - Horizontal Mains and Branches - Old Style Victaulic - Thin Wall Steel - No bracing, SDC A or B, PIPING FRAGILITY | 150 | 350 | 800 | LogNormal | 348.485 | 0.64877 | 3 | 385 |  |  |  | 315 | 0.64877 | 10 | Each (1000 ft pipe) | 1500 | 2650 | 4350 | LogNormal | 2596.8646 | 0.40537 | 3 | 2915 |  |  |  | 2385 | 0.40537 | 10 | Each (1000 ft pipe) | [45 empty] | 0.175 | 0.41 | 0.94 | LogNormal | 0.41 | 0.69527 | 3 | 0.45118 |  |  |  | 0.36882 | 0.69527 | 10 | Each (1000 ft pipe) | 0.355 | 0.625 | 1.025 | LogNormal | 0.625 | 0.47626 | 3 | 0.93676 |  |  |  | 0.31324 | 0.47626 | 10 | Each (1000 ft pipe) | [45 empty] | 50
| D4011.022a |  | D4011.022a | Fire Sprinkler Water Piping - Horizontal Mains and Branches - Old Style Victaulic - Thin Wall Steel - No bracing, SDC C, PIPING FRAGILITY | 150 | 350 | 800 | LogNormal | 348.485 | 0.64877 | 3 | 385 |  |  |  | 315 | 0.64877 | 10 | Each (1000 ft pipe) | 1500 | 2650 | 4350 | LogNormal | 2596.8646 | 0.40537 | 3 | 2915 |  |  |  | 2385 | 0.40537 | 10 | Each (1000 ft pipe) | [45 empty] | 0.175 | 0.41 | 0.94 | LogNormal | 0.41 | 0.69527 | 3 | 0.45118 |  |  |  | 0.36882 | 0.69527 | 10 | Each (1000 ft pipe) | 0.355 | 0.625 | 1.025 | LogNormal | 0.625 | 0.47626 | 3 | 0.93676 |  |  |  | 0.31324 | 0.47626 | 10 | Each (1000 ft pipe) | [45 empty] | 50
| D4011.023a |  | D4011.023a | Fire Sprinkler Water Piping - Horizontal Mains and Branches - Old Style Victaulic - Thin Wall Steel - Poorly designed bracing, SDC D, E, or F , PIPING FRAGILITY | 150 | 350 | 800 | LogNormal | 348.485 | 0.64877 | 3 | 385 |  |  |  | 315 | 0.64877 | 10 | Each (1000 ft pipe) | 1500 | 2650 | 4350 | LogNormal | 2596.8646 | 0.40537 | 3 | 2915 |  |  |  | 2385 | 0.40537 | 10 | Each (1000 ft pipe) | [45 empty] | 0.175 | 0.41 | 0.94 | LogNormal | 0.41 | 0.69527 | 3 | 0.45118 |  |  |  | 0.36882 | 0.69527 | 10 | Each (1000 ft pipe) | 0.355 | 0.625 | 1.025 | LogNormal | 0.625 | 0.47626 | 3 | 0.93676 |  |  |  | 0.31324 | 0.47626 | 10 | Each (1000 ft pipe) | [45 empty] | 50
| D4011.024a |  | D4011.024a | Fire Sprinkler Water Piping - Horizontal Mains and Branches - Old Style Victaulic - Thin Wall Steel - with designed bracing, SDC D, E, or F (OSHPD or sim), PIPING FRAGILITY | 150 | 350 | 800 | LogNormal | 348.485 | 0.64877 | 3 | 385 |  |  |  | 315 | 0.64877 | 10 | Each (1000 ft pipe) | 1500 | 2650 | 4350 | LogNormal | 2596.8646 | 0.40537 | 3 | 2915 |  |  |  | 2385 | 0.40537 | 10 | Each (1000 ft pipe) | [45 empty] | 0.175 | 0.41 | 0.94 | LogNormal | 0.41 | 0.69527 | 3 | 0.45118 |  |  |  | 0.36882 | 0.69527 | 10 | Each (1000 ft pipe) | 0.355 | 0.625 | 1.025 | LogNormal | 0.625 | 0.47626 | 3 | 0.93676 |  |  |  | 0.31324 | 0.47626 | 10 | Each (1000 ft pipe) | [45 empty] | 50
| D4011.031a |  | D4011.031a | Fire Sprinkler Drop Standard Threaded Steel - Dropping into unbraced lay-in tile SOFT ceiling - 6 ft. long drop maximum, SDC A or B | 350 | 500 | 850 | LogNormal | 526.2585 | 0.36654 | 2 | 550 |  |  |  | 450 | 0.36654 | 5 | 100 Units | 350 | 500 | 850 | LogNormal | 526.2585 | 0.36654 | 2 | 550 |  |  |  | 450 | 0.36654 | 5 | 100 Units | [45 empty] | 0.12 | 0.18 | 0.3 | LogNormal | 0.18 | 0.44368 | 2 | 0.23882 |  |  |  | 0.12118 | 0.44368 | 5 | 100 Units | 0.41 | 0.59 | 1 | LogNormal | 0.59 | 0.44368 | 2 | 0.64882 |  |  |  | 0.53118 | 0.44368 | 5 | 100 Units | [45 empty] | 100
| D4011.032a |  | D4011.032a | Fire Sprinkler Drop Standard Threaded Steel - Dropping into unbraced lay-in tile SOFT ceiling - 6 ft. long drop maximum, SDC C | 350 | 500 | 850 | LogNormal | 526.2585 | 0.36654 | 2 | 550 |  |  |  | 450 | 0.36654 | 5 | 100 Units | 350 | 500 | 850 | LogNormal | 526.2585 | 0.36654 | 2 | 550 |  |  |  | 450 | 0.36654 | 5 | 100 Units | [45 empty] | 0.12 | 0.18 | 0.3 | LogNormal | 0.18 | 0.44368 | 2 | 0.23882 |  |  |  | 0.12118 | 0.44368 | 5 | 100 Units | 0.41 | 0.59 | 1 | LogNormal | 0.59 | 0.44368 | 2 | 0.64882 |  |  |  | 0.53118 | 0.44368 | 5 | 100 Units | [45 empty] | 100
| D4011.033a |  | D4011.033a | Fire Sprinkler Drop Standard Threaded Steel - Dropping into unbraced lay-in tile SOFT ceiling - 6 ft. long drop maximum, SDC D, E, or F | 350 | 500 | 850 | LogNormal | 526.2585 | 0.36654 | 2 | 550 |  |  |  | 450 | 0.36654 | 5 | 100 Units | [60 empty] | 0.41 | 0.59 | 1 | LogNormal | 0.59 | 0.44368 | 2 | 0.64882 |  |  |  | 0.53118 | 0.44368 | 5 | 100 Units | [60 empty] | 100
| D4011.034a |  | D4011.034a | Fire Sprinkler Drop Standard Threaded Steel - Dropping into unbraced lay-in tile SOFT ceiling - 6 ft. long drop maximum, SDC D, E, or F (OSHPD or sim) | 350 | 500 | 850 | LogNormal | 526.2585 | 0.36654 | 2 | 550 |  |  |  | 450 | 0.36654 | 5 | 100 Units | [60 empty] | 0.41 | 0.59 | 1 | LogNormal | 0.59 | 0.44368 | 2 | 0.64882 |  |  |  | 0.53118 | 0.44368 | 5 | 100 Units | [60 empty] | 100
| D4011.041a |  | D4011.041a | Fire Sprinkler Drop Standard Threaded Steel - Dropping into unbraced lay-in tile HARD ceiling - 6 ft. long drop maximum, SDC A or B | 350 | 500 | 850 | LogNormal | 526.2585 | 0.36654 | 2 | 550 |  |  |  | 450 | 0.36654 | 5 | 100 Units | 350 | 500 | 850 | LogNormal | 526.2585 | 0.36654 | 2 | 550 |  |  |  | 450 | 0.36654 | 5 | 100 Units | [45 empty] | 0.41 | 0.59 | 1 | LogNormal | 0.59 | 0.44368 | 2 | 0.64882 |  |  |  | 0.53118 | 0.44368 | 5 | 100 Units | 0.08 | 0.12 | 0.2 | LogNormal | 0.12 | 0.44368 | 2 | 0.17882 |  |  |  | 0.061176 | 0.44368 | 5 | 100 Units | [45 empty] | 100
| D4011.042a |  | D4011.042a | Fire Sprinkler Drop Standard Threaded Steel - Dropping into unbraced lay-in tile HARD ceiling - 6 ft. long drop maximum, SDC C | 350 | 500 | 850 | LogNormal | 526.2585 | 0.36654 | 2 | 550 |  |  |  | 450 | 0.36654 | 5 | 100 Units | 350 | 500 | 850 | LogNormal | 526.2585 | 0.36654 | 2 | 550 |  |  |  | 450 | 0.36654 | 5 | 100 Units | [45 empty] | 0.41 | 0.59 | 1 | LogNormal | 0.59 | 0.44368 | 2 | 0.64882 |  |  |  | 0.53118 | 0.44368 | 5 | 100 Units | 0.08 | 0.12 | 0.2 | LogNormal | 0.12 | 0.44368 | 2 | 0.17882 |  |  |  | 0.061176 | 0.44368 | 5 | 100 Units | [45 empty] | 100
| D4011.053a |  | D4011.053a | Fire Sprinkler Drop Standard Threaded Steel - Dropping into braced lay-in tile SOFT ceiling - 6 ft. long drop maximum, SDC D, E, or F | 350 | 500 | 850 | LogNormal | 526.2585 | 0.36654 | 2 | 550 |  |  |  | 450 | 0.36654 | 5 | 100 Units | 350 | 500 | 850 | LogNormal | 526.2585 | 0.36654 | 2 | 550 |  |  |  | 450 | 0.36654 | 5 | 100 Units | [45 empty] | 0.41 | 0.59 | 1 | LogNormal | 0.59 | 0.44368 | 2 | 0.64882 |  |  |  | 0.53118 | 0.44368 | 5 | 100 Units | 0.08 | 0.12 | 0.2 | LogNormal | 0.12 | 0.44368 | 2 | 0.17882 |  |  |  | 0.061176 | 0.44368 | 5 | 100 Units | [45 empty] | 100
| D4011.054a |  | D4011.054a | Fire Sprinkler Drop Standard Threaded Steel - Dropping into braced lay-in tile SOFT ceiling - 6 ft. long drop maximum, SDC D, E, or F (OSHPD or sim) | 350 | 500 | 850 | LogNormal | 526.2585 | 0.36654 | 2 | 550 |  |  |  | 450 | 0.36654 | 5 | 100 Units | 350 | 500 | 850 | LogNormal | 526.2585 | 0.36654 | 2 | 550 |  |  |  | 450 | 0.36654 | 5 | 100 Units | [45 empty] | 0.41 | 0.59 | 1 | LogNormal | 0.59 | 0.44368 | 2 | 0.64882 |  |  |  | 0.53118 | 0.44368 | 5 | 100 Units | 0.08 | 0.12 | 0.2 | LogNormal | 0.12 | 0.44368 | 2 | 0.17882 |  |  |  | 0.061176 | 0.44368 | 5 | 100 Units | [45 empty] | 100
| D4011.063a |  | D4011.063a | Fire Sprinkler Drop Standard Threaded Steel - Dropping into braced lay-in tile HARD ceiling - 6 ft. long drop maximum, SDC D, E, or F | 350 | 500 | 850 | LogNormal | 526.2585 | 0.36654 | 2 | 550 |  |  |  | 450 | 0.36654 | 5 | 100 Units | 350 | 500 | 850 | LogNormal | 526.2585 | 0.36654 | 2 | 550 |  |  |  | 450 | 0.36654 | 5 | 100 Units | [45 empty] | 0.12 | 0.18 | 0.3 | LogNormal | 0.18 | 0.44368 | 2 | 0.23882 |  |  |  | 0.12118 | 0.44368 | 5 | 100 Units | 0.41 | 0.59 | 1 | LogNormal | 0.59 | 0.44368 | 2 | 0.64882 |  |  |  | 0.53118 | 0.44368 | 5 | 100 Units | [45 empty] | 100
| D4011.064a |  | D4011.064a | Fire Sprinkler Drop Standard Threaded Steel - Dropping into braced lay-in tile HARD ceiling - 6 ft. long drop maximum, SDC D, E, or F (OSHPD or sim) | 350 | 500 | 850 | LogNormal | 526.2585 | 0.36654 | 2 | 550 |  |  |  | 450 | 0.36654 | 5 | 100 Units | 350 | 500 | 850 | LogNormal | 526.2585 | 0.36654 | 2 | 550 |  |  |  | 450 | 0.36654 | 5 | 100 Units | [45 empty] | 0.12 | 0.18 | 0.3 | LogNormal | 0.18 | 0.44368 | 2 | 0.23882 |  |  |  | 0.12118 | 0.44368 | 5 | 100 Units | 0.41 | 0.59 | 1 | LogNormal | 0.59 | 0.44368 | 2 | 0.64882 |  |  |  | 0.53118 | 0.44368 | 5 | 100 Units | [45 empty] | 100
| D4011.071a |  | D4011.071a | Fire Sprinkler Drop Standard Threaded Steel - No Ceiling - 6 ft. long drop maximum, SDC A or B | 350 | 500 | 850 | LogNormal | 526.2585 | 0.36654 | 2 | 550 |  |  |  | 450 | 0.36654 | 5 | 100 Units | 350 | 500 | 850 | LogNormal | 526.2585 | 0.36654 | 2 | 550 |  |  |  | 450 | 0.36654 | 5 | 100 Units | [45 empty] | 0.12 | 0.18 | 0.3 | LogNormal | 0.18 | 0.44368 | 2 | 0.23882 |  |  |  | 0.12118 | 0.44368 | 5 | 100 Units | 0.41 | 0.59 | 1 | LogNormal | 0.59 | 0.44368 | 2 | 0.64882 |  |  |  | 0.53118 | 0.44368 | 5 | 100 Units | [45 empty] | 100
| D4011.072a |  | D4011.072a | Fire Sprinkler Drop Standard Threaded Steel - No Ceiling - 6 ft. long drop maximum, SDC C | 350 | 500 | 850 | LogNormal | 526.2585 | 0.36654 | 2 | 550 |  |  |  | 450 | 0.36654 | 5 | 100 Units | 350 | 500 | 850 | LogNormal | 526.2585 | 0.36654 | 2 | 550 |  |  |  | 450 | 0.36654 | 5 | 100 Units | [45 empty] | 0.12 | 0.18 | 0.3 | LogNormal | 0.18 | 0.44368 | 2 | 0.23882 |  |  |  | 0.12118 | 0.44368 | 5 | 100 Units | 0.41 | 0.59 | 1 | LogNormal | 0.59 | 0.44368 | 2 | 0.64882 |  |  |  | 0.53118 | 0.44368 | 5 | 100 Units | [45 empty] | 100
| D4011.073a |  | D4011.073a | Fire Sprinkler Drop Standard Threaded Steel - No Ceiling - 6 ft. long drop maximum, SDC D, E, or F | 350 | 500 | 850 | LogNormal | 526.2585 | 0.36654 | 2 | 550 |  |  |  | 450 | 0.36654 | 5 | 100 Units | 350 | 500 | 850 | LogNormal | 526.2585 | 0.36654 | 2 | 550 |  |  |  | 450 | 0.36654 | 5 | 100 Units | [45 empty] | 0.41 | 0.59 | 1 | LogNormal | 0.59 | 0.44368 | 2 | 0.64882 |  |  |  | 0.53118 | 0.44368 | 5 | 100 Units | 0.08 | 0.12 | 0.2 | LogNormal | 0.12 | 0.44368 | 2 | 0.17882 |  |  |  | 0.061176 | 0.44368 | 5 | 100 Units | [45 empty] | 100
| D4011.074a |  | D4011.074a | Fire Sprinkler Drop Standard Threaded Steel - No Ceiling - 6 ft. long drop maximum, SDC D, E, or F (OSHPD or sim) | 350 | 500 | 850 | LogNormal | 526.2585 | 0.36654 | 2 | 550 |  |  |  | 450 | 0.36654 | 5 | 100 Units | 350 | 500 | 850 | LogNormal | 526.2585 | 0.36654 | 2 | 550 |  |  |  | 450 | 0.36654 | 5 | 100 Units | [45 empty] | 0.41 | 0.59 | 1 | LogNormal | 0.59 | 0.44368 | 2 | 0.64882 |  |  |  | 0.53118 | 0.44368 | 5 | 100 Units | 0.08 | 0.12 | 0.2 | LogNormal | 0.12 | 0.44368 | 2 | 0.17882 |  |  |  | 0.061176 | 0.44368 | 5 | 100 Units | [45 empty] | 100
| D5011.011a |  | D5011.011a | Transformer/primary service - Capacity: <100 kVA - Unanchored equipment that is not vibration isolated - Equipment fragility only | 6100 | 7575 | 9800 | LogNormal | 7675.5785 | 0.1875 | 1 | 8332.5 |  |  |  | 6817.5 | 0.1875 | 5 | Each | [60 empty] | 1.4353 | 1.7824 | 2.3059 | LogNormal | 1.7824 | 0.3125 | 1 | 2.6736 |  |  |  | 0.89122 | 0.3125 | 5 | Each | [60 empty] | 1
| D5011.011b |  | D5011.011b | Transformer/primary service - Capacity: 100 to <350 kVA - Unanchored equipment that is not vibration isolated - Equipment fragility only | 20500 | 24250 | 32300 | LogNormal | 25202.726 | 0.18447 | 1 | 26675 |  |  |  | 21825 | 0.18447 | 5 | Each | [60 empty] | 3.6176 | 4.2794 | 5.7 | LogNormal | 4.2794 | 0.31069 | 1 | 7.1323 |  |  |  | 2.1397 | 0.31069 | 5 | Each | [60 empty] | 1
| D5011.011c |  | D5011.011c | Transformer/primary service - Capacity: 350 to <750 kVA - Unanchored equipment that is not vibration isolated - Equipment fragility only | 36200 | 42700 | 56600 | LogNormal | 44350.7178 | 0.18123 | 1 | 46970 |  |  |  | 38430 | 0.18123 | 5 | Each | [60 empty] | 4.2588 | 5.0235 | 6.6588 | LogNormal | 5.0235 | 0.30878 | 1 | 10.047 |  |  |  | 2.5118 | 0.30878 | 5 | Each | [60 empty] | 1
| D5011.011d |  | D5011.011d | Transformer/primary service - Capacity: 750 to 1500 kVA - Unanchored equipment that is not vibration isolated - Equipment fragility only | 47500 | 57000 | 74800 | LogNormal | 58676.6753 | 0.18249 | 1 | 62700 |  |  |  | 51300 | 0.18249 | 5 | Each | [60 empty] | 3.9118 | 4.6941 | 6.16 | LogNormal | 4.6941 | 0.30952 | 1 | 11.4 |  |  |  | 2.347 | 0.30952 | 5 | Each | [60 empty] | 1
| D5011.013a |  | D5011.013a | Transformer/primary service - Capacity: <100 kVA - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only | 500 | 1000 | 1700 | LogNormal | 958.6389 | 0.45231 | 1 | 1100 |  |  |  | 900 | 0.45231 | 5 | Each | 6600 | 8575 | 11500 | LogNormal | 8661.7283 | 0.21894 | 1 | 9432.5 |  |  |  | 7717.5 | 0.21894 | 5 | Each | [45 empty] | 0.5882 | 1.1765 | 2 | LogNormal | 1.1765 | 0.5168 | 1 | 1.2941 |  |  |  | 1.0589 | 0.5168 | 5 | Each | 7.7647 | 10.0882 | 13.5294 | LogNormal | 10.0882 | 0.33232 | 1 | 11.097 |  |  |  | 9.0794 | 0.33232 | 5 | Each | [45 empty] | 1
| D5011.013b |  | D5011.013b | Transformer/primary service - Capacity: <100 kVA - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only | 6100 | 7575 | 9800 | LogNormal | 7675.5785 | 0.1875 | 1 | 8332.5 |  |  |  | 6817.5 | 0.1875 | 5 | Each | [60 empty] | 5.8309 | 7.2408 | 9.3676 | LogNormal | 7.2408 | 0.3125 | 1 | 7.9649 |  |  |  | 6.5167 | 0.3125 | 5 | Each | [60 empty] | 1
| D5011.013c |  | D5011.013c | Transformer/primary service - Capacity: <100 kVA - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | 500 | 1000 | 1700 | LogNormal | 958.6389 | 0.45231 | 1 | 1100 |  |  |  | 900 | 0.45231 | 5 | Each | 6600 | 8575 | 11500 | LogNormal | 8661.7283 | 0.21894 | 1 | 9432.5 |  |  |  | 7717.5 | 0.21894 | 5 | Each | 6100 | 7575 | 9800 | LogNormal | 7675.5785 | 0.1875 | 1 | 8332.5 |  |  |  | 6817.5 | 0.1875 | 5 | Each | [30 empty] | 0.4779 | 0.9559 | 1.625 | LogNormal | 0.9559 | 0.5168 | 1 | 1.0515 |  |  |  | 0.86031 | 0.5168 | 5 | Each | 1.2618 | 1.6393 | 2.1985 | LogNormal | 1.6393 | 0.33232 | 1 | 2.459 |  |  |  | 0.81965 | 0.33232 | 5 | Each | 1.1662 | 1.4482 | 1.8735 | LogNormal | 1.4482 | 0.3125 | 1 | 2.1723 |  |  |  | 0.72412 | 0.3125 | 5 | Each | [30 empty] | 1
| D5011.013d |  | D5011.013d | Transformer/primary service - Capacity: 100 to <350 kVA - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only | 800 | 1500 | 2400 | Normal | 1566.6663 | 0.39845 | 1 | 1650 |  |  |  | 1350 | 0.39845 | 5 | Each | 21300 | 25750 | 34700 | LogNormal | 26668.4293 | 0.19736 | 1 | 28325 |  |  |  | 23175 | 0.19736 | 5 | Each | [45 empty] | 0.7647 | 1.4338 | 2.2941 | Normal | 1.4338 | 0.47039 | 1 | 1.5772 |  |  |  | 1.2904 | 0.47039 | 5 | Each | 3.054 | 3.6921 | 4.9754 | LogNormal | 3.6921 | 0.31851 | 1 | 6.1535 |  |  |  | 1.846 | 0.31851 | 5 | Each | [45 empty] | 1
| D5011.013e |  | D5011.013e | Transformer/primary service - Capacity: 100 to <350 kVA - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only | 20500 | 24250 | 32300 | LogNormal | 25202.726 | 0.18447 | 1 | 26675 |  |  |  | 21825 | 0.18447 | 5 | Each | [60 empty] | 2.9393 | 3.477 | 4.6313 | LogNormal | 3.477 | 0.31069 | 1 | 5.795 |  |  |  | 1.7385 | 0.31069 | 5 | Each | [60 empty] | 1
| D5011.013f |  | D5011.013f | Transformer/primary service - Capacity: 100 to <350 kVA - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | 800 | 1500 | 2400 | Normal | 1566.6663 | 0.39845 | 1 | 1650 |  |  |  | 1350 | 0.39845 | 5 | Each | 21300 | 25750 | 34700 | LogNormal | 26668.4293 | 0.19736 | 1 | 28325 |  |  |  | 23175 | 0.19736 | 5 | Each | 20500 | 24250 | 32300 | LogNormal | 25202.726 | 0.18447 | 1 | 26675 |  |  |  | 21825 | 0.18447 | 5 | Each | [30 empty] | 0.7647 | 1.4338 | 2.2941 | Normal | 1.4338 | 0.47039 | 1 | 1.5772 |  |  |  | 1.2904 | 0.47039 | 5 | Each | 3.054 | 3.6921 | 4.9754 | LogNormal | 3.6921 | 0.31851 | 1 | 6.1535 |  |  |  | 1.846 | 0.31851 | 5 | Each | 2.9393 | 3.477 | 4.6313 | LogNormal | 3.477 | 0.31069 | 1 | 5.795 |  |  |  | 1.7385 | 0.31069 | 5 | Each | [30 empty] | 1
| D5011.013g |  | D5011.013g | Transformer/primary service - Capacity: 350 to <750 kVA - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only | 1400 | 2200 | 3100 | Normal | 2233.3322 | 0.29698 | 1 | 2420 |  |  |  | 1980 | 0.29698 | 5 | Each | 37600 | 44900 | 59700 | LogNormal | 46491.3579 | 0.1869 | 1 | 49390 |  |  |  | 40410 | 0.1869 | 5 | Each | [45 empty] | 1.3382 | 2.1029 | 2.9632 | Normal | 2.1029 | 0.3882 | 1 | 2.3132 |  |  |  | 1.8926 | 0.3882 | 5 | Each | 3.5941 | 4.2919 | 5.7066 | LogNormal | 4.2919 | 0.31214 | 1 | 8.5838 |  |  |  | 2.146 | 0.31214 | 5 | Each | [45 empty] | 1
| D5011.013h |  | D5011.013h | Transformer/primary service - Capacity: 350 to <750 kVA - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only | 36200 | 42700 | 56600 | LogNormal | 44350.7178 | 0.18123 | 1 | 46970 |  |  |  | 38430 | 0.18123 | 5 | Each | [60 empty] | 3.4603 | 4.0816 | 5.4103 | LogNormal | 4.0816 | 0.30878 | 1 | 8.1632 |  |  |  | 2.0408 | 0.30878 | 5 | Each | [60 empty] | 1
| D5011.013i |  | D5011.013i | Transformer/primary service - Capacity: 350 to <750 kVA - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | 1400 | 2200 | 3100 | Normal | 2233.3322 | 0.29698 | 1 | 2420 |  |  |  | 1980 | 0.29698 | 5 | Each | 37600 | 44900 | 59700 | LogNormal | 46491.3579 | 0.1869 | 1 | 49390 |  |  |  | 40410 | 0.1869 | 5 | Each | 36200 | 42700 | 56600 | LogNormal | 44350.7178 | 0.18123 | 1 | 46970 |  |  |  | 38430 | 0.18123 | 5 | Each | [30 empty] | 1.3382 | 2.1029 | 2.9632 | Normal | 2.1029 | 0.3882 | 1 | 2.3132 |  |  |  | 1.8926 | 0.3882 | 5 | Each | 3.5941 | 4.2919 | 5.7066 | LogNormal | 4.2919 | 0.31214 | 1 | 8.5838 |  |  |  | 2.146 | 0.31214 | 5 | Each | 3.4603 | 4.0816 | 5.4103 | LogNormal | 4.0816 | 0.30878 | 1 | 8.1632 |  |  |  | 2.0408 | 0.30878 | 5 | Each | [30 empty] | 1
| D5011.013j |  | D5011.013j | Transformer/primary service - Capacity: 750 to 1500 kVA - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only | 1600 | 2400 | 3400 | LogNormal | 2358.8816 | 0.28852 | 1 | 2640 |  |  |  | 2160 | 0.28852 | 5 | Each | 49100 | 59400 | 78200 | LogNormal | 61046.5725 | 0.18673 | 1 | 65340 |  |  |  | 53460 | 0.18673 | 5 | Each | [45 empty] | 1.5294 | 2.2941 | 3.25 | LogNormal | 2.2941 | 0.38177 | 1 | 2.5235 |  |  |  | 2.0647 | 0.38177 | 5 | Each | 3.2854 | 3.9746 | 5.2325 | LogNormal | 3.9746 | 0.31204 | 1 | 9.6525 |  |  |  | 1.9873 | 0.31204 | 5 | Each | [45 empty] | 1
| D5011.013k |  | D5011.013k | Transformer/primary service - Capacity: 750 to 1500 kVA - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only | 47500 | 57000 | 74800 | LogNormal | 58676.6753 | 0.18249 | 1 | 62700 |  |  |  | 51300 | 0.18249 | 5 | Each | [60 empty] | 3.1783 | 3.814 | 5.005 | LogNormal | 3.814 | 0.30952 | 1 | 9.2625 |  |  |  | 1.907 | 0.30952 | 5 | Each | [60 empty] | 1
| D5011.013l |  | D5011.013l | Transformer/primary service - Capacity: 750 to 1500 kVA - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | 1600 | 2400 | 3400 | LogNormal | 2358.8816 | 0.28852 | 1 | 2640 |  |  |  | 2160 | 0.28852 | 5 | Each | 49100 | 59400 | 78200 | LogNormal | 61046.5725 | 0.18673 | 1 | 65340 |  |  |  | 53460 | 0.18673 | 5 | Each | 47500 | 57000 | 74800 | LogNormal | 58676.6753 | 0.18249 | 1 | 62700 |  |  |  | 51300 | 0.18249 | 5 | Each | [30 empty] | 1.5294 | 2.2941 | 3.25 | LogNormal | 2.2941 | 0.38177 | 1 | 2.5235 |  |  |  | 2.0647 | 0.38177 | 5 | Each | 3.2854 | 3.9746 | 5.2325 | LogNormal | 3.9746 | 0.31204 | 1 | 9.6525 |  |  |  | 1.9873 | 0.31204 | 5 | Each | 3.1783 | 3.814 | 5.005 | LogNormal | 3.814 | 0.30952 | 1 | 9.2625 |  |  |  | 1.907 | 0.30952 | 5 | Each | [30 empty] | 1
| D5012.013a |  | D5012.013a | Motor Control Center - Capacity: all - Unanchored equipment that is not vibration isolated - Equipment fragility only | 3200 | 4150 | 5150 | Normal | 4166.6673 | 0.18259 | 1 | 4565 |  |  |  | 3735 | 0.18259 | 5 | Each | [60 empty] | 1.1294 | 1.4647 | 1.8176 | Normal | 1.4647 | 0.30958 | 1 | 1.9529 |  |  |  | 0.97646 | 0.30958 | 5 | Each | [60 empty] | 1
| D5012.013b |  | D5012.013b | Motor Control Center - Capacity: all - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only | 300 | 500 | 650 | Normal | 483.3331 | 0.28252 | 1 | 550 |  |  |  | 450 | 0.28252 | 5 | Each | 3500 | 4650 | 5800 | Normal | 4649.9977 | 0.19298 | 1 | 5115 |  |  |  | 4185 | 0.19298 | 5 | Each | [45 empty] | 0.3529 | 0.5882 | 0.7647 | Normal | 0.5882 | 0.37725 | 1 | 0.64702 |  |  |  | 0.52938 | 0.37725 | 5 | Each | 0.8235 | 1.0941 | 1.3647 | Normal | 1.0941 | 0.31582 | 1 | 1.6412 |  |  |  | 0.54705 | 0.31582 | 5 | Each | [45 empty] | 1
| D5012.013c |  | D5012.013c | Motor Control Center - Capacity: all - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only | 3200 | 4150 | 5150 | Normal | 4166.6673 | 0.18259 | 1 | 4565 |  |  |  | 3735 | 0.18259 | 5 | Each | [60 empty] | 3.7647 | 4.8824 | 6.0588 | Normal | 4.8824 | 0.30958 | 1 | 5.3706 |  |  |  | 4.3942 | 0.30958 | 5 | Each | [60 empty] | 1
| D5012.013d |  | D5012.013d | Motor Control Center - Capacity: all - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | 300 | 500 | 650 | Normal | 483.3331 | 0.28252 | 1 | 550 |  |  |  | 450 | 0.28252 | 5 | Each | 3500 | 4650 | 5800 | Normal | 4649.9977 | 0.19298 | 1 | 5115 |  |  |  | 4185 | 0.19298 | 5 | Each | 3200 | 4150 | 5150 | Normal | 4166.6679 | 0.18259 | 1 | 4565 |  |  |  | 3735 | 0.18259 | 5 | Each | [30 empty] | 0.3529 | 0.5882 | 0.7647 | Normal | 0.5882 | 0.37725 | 1 | 0.64702 |  |  |  | 0.52938 | 0.37725 | 5 | Each | 0.8235 | 1.0941 | 1.3647 | Normal | 1.0941 | 0.31582 | 1 | 1.6412 |  |  |  | 0.54705 | 0.31582 | 5 | Each | 0.7529 | 0.9765 | 1.2118 | Normal | 0.9765 | 0.30958 | 1 | 1.4647 |  |  |  | 0.48826 | 0.30958 | 5 | Each | [30 empty] | 1
| D5012.021a |  | D5012.021a | Low Voltage Switchgear - Capacity: 100 to <350 Amp - Unanchored equipment that is not vibration isolated - Equipment fragility only | 8200 | 9275 | 12050 | LogNormal | 9706.9698 | 0.1572 | 1 | 10202.5 |  |  |  | 8347.5 | 0.1572 | 5 | Each | [60 empty] | 1.9294 | 2.1824 | 2.8353 | LogNormal | 2.1824 | 0.29532 | 1 | 3.2736 |  |  |  | 1.0912 | 0.29532 | 5 | Each | [60 empty] | 1
| D5012.021b |  | D5012.021b | Low Voltage Switchgear - Capacity: 350 to <750 Amp - Unanchored equipment that is not vibration isolated - Equipment fragility only | 14700 | 17300 | 17300 | Normal | 16433.3258 | 0.061728 | 1 | 19030 |  |  |  | 15570 | 0.061728 | 5 | Each | [60 empty] | 2.5941 | 3.0529 | 3.0529 | Normal | 3.0529 | 0.25751 | 1 | 5.0882 |  |  |  | 1.5265 | 0.25751 | 5 | Each | [60 empty] | 1
| D5012.021c |  | D5012.021c | Low Voltage Switchgear - Capacity: 750 to <1200 Amp - Unanchored equipment that is not vibration isolated - Equipment fragility only | 24400 | 29600 | 29600 | Normal | 27866.6521 | 0.072804 | 1 | 32560 |  |  |  | 26640 | 0.072804 | 5 | Each | [60 empty] | 2.8706 | 3.4824 | 3.4824 | Normal | 3.4824 | 0.26039 | 1 | 6.9648 |  |  |  | 1.7412 | 0.26039 | 5 | Each | [60 empty] | 1
| D5012.021d |  | D5012.021d | Low Voltage Switchgear - Capacity: 1200 to 2000 Amp - Unanchored equipment that is not vibration isolated - Equipment fragility only | 42900 | 51400 | 51400 | Normal | 48566.6409 | 0.068284 | 1 | 56540 |  |  |  | 46260 | 0.068284 | 5 | Each | [60 empty] | 3.5329 | 4.2329 | 4.2329 | Normal | 4.2329 | 0.25916 | 1 | 10.28 |  |  |  | 2.1164 | 0.25916 | 5 | Each | [60 empty] | 1
| D5012.023a |  | D5012.023a | Low Voltage Switchgear - Capacity: 100 to <350 Amp - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only | 300 | 500 | 650 | Normal | 483.3331 | 0.28252 | 1 | 550 |  |  |  | 450 | 0.28252 | 5 | Each | 8500 | 9775 | 12700 | LogNormal | 10173.3898 | 0.1631 | 1 | 10752.5 |  |  |  | 8797.5 | 0.1631 | 5 | Each | [45 empty] | 0.3529 | 0.5882 | 0.7647 | Normal | 0.5882 | 0.37725 | 1 | 0.64702 |  |  |  | 0.52938 | 0.37725 | 5 | Each | 2 | 2.3 | 2.9882 | LogNormal | 2.3 | 0.2985 | 1 | 3.45 |  |  |  | 1.15 | 0.2985 | 5 | Each | [45 empty] | 1
| D5012.023b |  | D5012.023b | Low Voltage Switchgear - Capacity: 100 to <350 Amp - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only | 8200 | 9275 | 12050 | LogNormal | 9706.9698 | 0.1572 | 1 | 10202.5 |  |  |  | 8347.5 | 0.1572 | 5 | Each | [60 empty] | 1.9294 | 2.1824 | 2.8353 | LogNormal | 2.1824 | 0.29532 | 1 | 3.2736 |  |  |  | 1.0912 | 0.29532 | 5 | Each | [60 empty] | 1
| D5012.023c |  | D5012.023c | Low Voltage Switchgear - Capacity: 100 to <350 Amp - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | 300 | 500 | 650 | Normal | 483.3331 | 0.28252 | 1 | 550 |  |  |  | 450 | 0.28252 | 5 | Each | 8500 | 9775 | 12700 | LogNormal | 10173.3898 | 0.1631 | 1 | 10752.5 |  |  |  | 8797.5 | 0.1631 | 5 | Each | 8200 | 9275 | 12050 | LogNormal | 9706.9698 | 0.1572 | 1 | 10202.5 |  |  |  | 8347.5 | 0.1572 | 5 | Each | [30 empty] | 0.3529 | 0.5882 | 0.7647 | Normal | 0.5882 | 0.37725 | 1 | 0.64702 |  |  |  | 0.52938 | 0.37725 | 5 | Each | 2 | 2.3 | 2.9882 | LogNormal | 2.3 | 0.2985 | 1 | 3.45 |  |  |  | 1.15 | 0.2985 | 5 | Each | 1.9294 | 2.1824 | 2.8353 | LogNormal | 2.1824 | 0.29532 | 1 | 3.2736 |  |  |  | 1.0912 | 0.29532 | 5 | Each | [30 empty] | 1
| D5012.023d |  | D5012.023d | Low Voltage Switchgear - Capacity: 350 to <750 Amp - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only | 500 | 800 | 1400 | LogNormal | 820.3261 | 0.41375 | 1 | 880 |  |  |  | 720 | 0.41375 | 5 | Each | 15200 | 18100 | 24100 | LogNormal | 18767.5266 | 0.18659 | 1 | 19910 |  |  |  | 16290 | 0.18659 | 5 | Each | [45 empty] | 0.5882 | 0.9412 | 1.6471 | LogNormal | 0.9412 | 0.48342 | 1 | 1.0353 |  |  |  | 0.84708 | 0.48342 | 5 | Each | 2.6824 | 3.1941 | 4.2529 | LogNormal | 3.1941 | 0.31195 | 1 | 5.3235 |  |  |  | 1.5971 | 0.31195 | 5 | Each | [45 empty] | 1
| D5012.023e |  | D5012.023e | Low Voltage Switchgear - Capacity: 350 to <750 Amp - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only | 14700 | 17300 | 17300 | Normal | 16433.3258 | 0.061728 | 1 | 19030 |  |  |  | 15570 | 0.061728 | 5 | Each | [60 empty] | 2.5941 | 3.0529 | 3.0529 | Normal | 3.0529 | 0.25751 | 1 | 5.0882 |  |  |  | 1.5265 | 0.25751 | 5 | Each | [60 empty] | 1
| D5012.023f |  | D5012.023f | Low Voltage Switchgear - Capacity: 350 to <750 Amp - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | 500 | 800 | 1400 | LogNormal | 820.3261 | 0.41375 | 1 | 880 |  |  |  | 720 | 0.41375 | 5 | Each | 15200 | 18100 | 24100 | LogNormal | 18767.5266 | 0.18659 | 1 | 19910 |  |  |  | 16290 | 0.18659 | 5 | Each | 14700 | 17300 | 17300 | Normal | 16433.3294 | 0.061728 | 1 | 19030 |  |  |  | 15570 | 0.061728 | 5 | Each | [30 empty] | 0.5882 | 0.9412 | 1.6471 | LogNormal | 0.9412 | 0.48342 | 1 | 1.0353 |  |  |  | 0.84708 | 0.48342 | 5 | Each | 2.6824 | 3.1941 | 4.2529 | LogNormal | 3.1941 | 0.31195 | 1 | 5.3235 |  |  |  | 1.5971 | 0.31195 | 5 | Each | 2.5941 | 3.0529 | 3.0529 | Normal | 3.0529 | 0.25751 | 1 | 5.0882 |  |  |  | 1.5265 | 0.25751 | 5 | Each | [30 empty] | 1
| D5012.023g |  | D5012.023g | Low Voltage Switchgear - Capacity: 750 to <1200 Amp - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only | 900 | 1200 | 2000 | LogNormal | 1283.8705 | 0.33516 | 1 | 1320 |  |  |  | 1080 | 0.33516 | 5 | Each | 25300 | 30800 | 41000 | LogNormal | 31700.7593 | 0.19401 | 1 | 33880 |  |  |  | 27720 | 0.19401 | 5 | Each | [45 empty] | 1.0588 | 1.4118 | 2.3529 | LogNormal | 1.4118 | 0.41813 | 1 | 1.553 |  |  |  | 1.2706 | 0.41813 | 5 | Each | 2.9765 | 3.6235 | 4.8235 | LogNormal | 3.6235 | 0.31645 | 1 | 7.247 |  |  |  | 1.8117 | 0.31645 | 5 | Each | [45 empty] | 1
| D5012.023h |  | D5012.023h | Low Voltage Switchgear - Capacity: 750 to <1200 Amp - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only | 24400 | 29600 | 29600 | Normal | 27866.6521 | 0.072804 | 1 | 32560 |  |  |  | 26640 | 0.072804 | 5 | Each | [60 empty] | 2.8706 | 3.4824 | 3.4824 | Normal | 3.4824 | 0.26039 | 1 | 6.9648 |  |  |  | 1.7412 | 0.26039 | 5 | Each | [60 empty] | 1
| D5012.023i |  | D5012.023i | Low Voltage Switchgear - Capacity: 750 to <1200 Amp - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | 900 | 1200 | 2000 | LogNormal | 1283.8705 | 0.33516 | 1 | 1320 |  |  |  | 1080 | 0.33516 | 5 | Each | 25300 | 30800 | 41000 | LogNormal | 31700.7593 | 0.19401 | 1 | 33880 |  |  |  | 27720 | 0.19401 | 5 | Each | 24400 | 29600 | 29600 | Normal | 27866.594 | 0.072803 | 1 | 32560 |  |  |  | 26640 | 0.072803 | 5 | Each | [30 empty] | 1.0588 | 1.4118 | 2.3529 | LogNormal | 1.4118 | 0.41813 | 1 | 1.553 |  |  |  | 1.2706 | 0.41813 | 5 | Each | 2.9765 | 3.6235 | 4.8235 | LogNormal | 3.6235 | 0.31645 | 1 | 7.247 |  |  |  | 1.8117 | 0.31645 | 5 | Each | 2.8706 | 3.4824 | 3.4824 | Normal | 3.4824 | 0.26038 | 1 | 6.9648 |  |  |  | 1.7412 | 0.26038 | 5 | Each | [30 empty] | 1
| D5012.023j |  | D5012.023j | Low Voltage Switchgear - Capacity: 1200 to 2000 Amp - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only | 900 | 1200 | 2000 | LogNormal | 1283.8705 | 0.33516 | 1 | 1320 |  |  |  | 1080 | 0.33516 | 5 | Each | 43800 | 52600 | 69500 | LogNormal | 54252.8179 | 0.18591 | 1 | 57860 |  |  |  | 47340 | 0.18591 | 5 | Each | [45 empty] | 1.0588 | 1.4118 | 2.3529 | LogNormal | 1.4118 | 0.41813 | 1 | 1.553 |  |  |  | 1.2706 | 0.41813 | 5 | Each | 3.6071 | 4.3318 | 5.7235 | LogNormal | 4.3318 | 0.31155 | 1 | 10.52 |  |  |  | 2.1659 | 0.31155 | 5 | Each | [45 empty] | 1
| D5012.023k |  | D5012.023k | Low Voltage Switchgear - Capacity: 1200 to 2000 Amp - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only | 42900 | 51400 | 51400 | Normal | 48566.6409 | 0.068284 | 1 | 56540 |  |  |  | 46260 | 0.068284 | 5 | Each | [60 empty] | 3.5329 | 4.2329 | 4.2329 | Normal | 4.2329 | 0.25916 | 1 | 10.28 |  |  |  | 2.1164 | 0.25916 | 5 | Each | [60 empty] | 1
| D5012.023l |  | D5012.023l | Low Voltage Switchgear - Capacity: 1200 to 2000 Amp - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | 900 | 1200 | 2000 | LogNormal | 1283.8705 | 0.33516 | 1 | 1320 |  |  |  | 1080 | 0.33516 | 5 | Each | 43800 | 52600 | 69500 | LogNormal | 54252.8179 | 0.18591 | 1 | 57860 |  |  |  | 47340 | 0.18591 | 5 | Each | 42900 | 51400 | 51400 | Normal | 48566.6488 | 0.068283 | 1 | 56540 |  |  |  | 46260 | 0.068283 | 5 | Each | [30 empty] | 1.0588 | 1.4118 | 2.3529 | LogNormal | 1.4118 | 0.41813 | 1 | 1.553 |  |  |  | 1.2706 | 0.41813 | 5 | Each | 3.6071 | 4.3318 | 5.7235 | LogNormal | 4.3318 | 0.31155 | 1 | 10.52 |  |  |  | 2.1659 | 0.31155 | 5 | Each | 3.5329 | 4.2329 | 4.2329 | Normal | 4.2329 | 0.25916 | 1 | 10.28 |  |  |  | 2.1164 | 0.25916 | 5 | Each | [30 empty] | 1
| D5012.031a |  | D5012.031a | Distribution Panel - Capacity: 100 to <350 Amp - Unanchored equipment that is not vibration isolated - Equipment fragility only | 8200 | 9275 | 12050 | LogNormal | 9706.9698 | 0.1572 | 1 | 12057.5 |  |  |  | 8347.5 | 0.1572 | 5 | Each | [60 empty] | 1.9294 | 2.1824 | 2.8353 | LogNormal | 2.1824 | 0.29532 | 1 | 5.4559 |  |  |  | 1.0912 | 0.29532 | 5 | Each | [60 empty] | 1
| D5012.031b |  | D5012.031b | Distribution Panel - Capacity: 350 to <750 Amp - Unanchored equipment that is not vibration isolated - Equipment fragility only | 14700 | 17300 | 17300 | Normal | 16433.3258 | 0.061728 | 1 | 22490 |  |  |  | 15570 | 0.061728 | 5 | Each | [60 empty] | 2.5941 | 3.0529 | 3.0529 | Normal | 3.0529 | 0.25751 | 1 | 9.1588 |  |  |  | 1.5265 | 0.25751 | 5 | Each | [60 empty] | 1
| D5012.031c |  | D5012.031c | Distribution Panel - Capacity: 750 to <1200 Amp - Unanchored equipment that is not vibration isolated - Equipment fragility only | 24400 | 29600 | 29600 | Normal | 27866.6521 | 0.072804 | 1 | 38480 |  |  |  | 26640 | 0.072804 | 5 | Each | [60 empty] | 2.8706 | 3.4824 | 3.4824 | Normal | 3.4824 | 0.26039 | 1 | 13.9295 |  |  |  | 1.7412 | 0.26039 | 5 | Each | [60 empty] | 1
| D5012.031d |  | D5012.031d | Distribution Panel - Capacity: 1200 to 2000 Amp - Unanchored equipment that is not vibration isolated - Equipment fragility only | 42900 | 51400 | 51400 | Normal | 48566.6409 | 0.068284 | 1 | 66820 |  |  |  | 46260 | 0.068284 | 5 | Each | [60 empty] | 3.5329 | 4.2329 | 4.2329 | Normal | 4.2329 | 0.25916 | 1 | 22.3741 |  |  |  | 2.1164 | 0.25916 | 5 | Each | [60 empty] | 1
| D5012.033a |  | D5012.033a | Distribution Panel - Capacity: 100 to <350 Amp - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only | 300 | 500 | 650 | Normal | 483.3331 | 0.28252 | 1 | 650 |  |  |  | 450 | 0.28252 | 5 | Each | 8500 | 9775 | 12700 | LogNormal | 10173.3898 | 0.1631 | 1 | 12707.5 |  |  |  | 8797.5 | 0.1631 | 5 | Each | [45 empty] | 0.353 | 0.588 | 0.765 | Normal | 0.588 | 0.37725 | 1 | 0.76447 |  |  |  | 0.52918 | 0.37725 | 5 | Each | 2 | 2.3 | 2.9882 | LogNormal | 2.3 | 0.2985 | 1 | 5.75 |  |  |  | 1.15 | 0.2985 | 5 | Each | [45 empty] | 1
| D5012.033b |  | D5012.033b | Distribution Panel - Capacity: 100 to <350 Amp - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only | 8200 | 9275 | 12050 | LogNormal | 9706.9698 | 0.1572 | 1 | 11130 |  |  |  | 7420 | 0.1572 | 5 | Each | [60 empty] | 2.1706 | 2.4551 | 3.1897 | LogNormal | 2.4551 | 0.29532 | 1 | 4.9102 |  |  |  | 1.2275 | 0.29532 | 5 | Each | [60 empty] | 1
| D5012.033c |  | D5012.033c | Distribution Panel - Capacity: 100 to <350 Amp - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | 300 | 500 | 650 | Normal | 483.3331 | 0.28252 | 1 | 600 |  |  |  | 400 | 0.28252 | 5 | Each | 8500 | 9775 | 12700 | LogNormal | 10173.3898 | 0.1631 | 1 | 11730 |  |  |  | 7820 | 0.1631 | 5 | Each | 8200 | 9275 | 12050 | LogNormal | 9706.9698 | 0.1572 | 1 | 11130 |  |  |  | 7420 | 0.1572 | 5 | Each | [30 empty] | 0.3971 | 0.6618 | 0.8603 | Normal | 0.6618 | 0.37725 | 1 | 0.79415 |  |  |  | 0.52945 | 0.37725 | 5 | Each | 2.25 | 2.5875 | 3.3618 | LogNormal | 2.5875 | 0.2985 | 1 | 5.175 |  |  |  | 1.2937 | 0.2985 | 5 | Each | 2.1706 | 2.4551 | 3.1897 | LogNormal | 2.4551 | 0.29532 | 1 | 4.9102 |  |  |  | 1.2275 | 0.29532 | 5 | Each | [30 empty] | 1
| D5012.033d |  | D5012.033d | Distribution Panel - Capacity: 350 to <750 Amp - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only | 500 | 800 | 1400 | LogNormal | 820.3261 | 0.41375 | 1 | 1040 |  |  |  | 720 | 0.41375 | 5 | Each | 15200 | 18100 | 24100 | LogNormal | 18767.5266 | 0.18659 | 1 | 23530 |  |  |  | 16290 | 0.18659 | 5 | Each | [45 empty] | 0.588 | 0.941 | 1.647 | LogNormal | 0.941 | 0.48342 | 1 | 1.2234 |  |  |  | 0.84688 | 0.48342 | 5 | Each | 2.6824 | 3.1941 | 4.2529 | LogNormal | 3.1941 | 0.31195 | 1 | 9.5823 |  |  |  | 1.5971 | 0.31195 | 5 | Each | [45 empty] | 1
| D5012.033e |  | D5012.033e | Distribution Panel - Capacity: 350 to <750 Amp - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only | 14700 | 17300 | 17300 | Normal | 16433.3258 | 0.061728 | 1 | 20760 |  |  |  | 13840 | 0.061728 | 5 | Each | [60 empty] | 2.9184 | 3.4346 | 3.4346 | Normal | 3.4346 | 0.25751 | 1 | 8.014 |  |  |  | 1.7173 | 0.25751 | 5 | Each | [60 empty] | 1
| D5012.033f |  | D5012.033f | Distribution Panel - Capacity: 350 to <750 Amp - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | 500 | 800 | 1400 | LogNormal | 820.3261 | 0.41375 | 1 | 960 |  |  |  | 640 | 0.41375 | 5 | Each | 15200 | 18100 | 24100 | LogNormal | 18767.5266 | 0.18659 | 1 | 21720 |  |  |  | 14480 | 0.18659 | 5 | Each | 14700 | 17300 | 17300 | Normal | 16433.3294 | 0.061728 | 1 | 20760 |  |  |  | 13840 | 0.061728 | 5 | Each | [30 empty] | 0.6618 | 1.0588 | 1.8529 | LogNormal | 1.0588 | 0.48342 | 1 | 1.2706 |  |  |  | 0.84704 | 0.48342 | 5 | Each | 3.0176 | 3.5934 | 4.7846 | LogNormal | 3.5934 | 0.31195 | 1 | 8.3846 |  |  |  | 1.7967 | 0.31195 | 5 | Each | 2.9184 | 3.4346 | 3.4346 | Normal | 3.4346 | 0.25751 | 1 | 8.014 |  |  |  | 1.7173 | 0.25751 | 5 | Each | [30 empty] | 1
| D5012.033g |  | D5012.033g | Distribution Panel - Capacity: 750 to <1200 Amp - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only | 900 | 1200 | 2000 | LogNormal | 1283.8705 | 0.33516 | 1 | 1560 |  |  |  | 1080 | 0.33516 | 5 | Each | 25300 | 30800 | 41000 | LogNormal | 31700.7593 | 0.19401 | 1 | 40040 |  |  |  | 27720 | 0.19401 | 5 | Each | [45 empty] | 1.059 | 1.412 | 2.353 | LogNormal | 1.412 | 0.41813 | 1 | 1.8355 |  |  |  | 1.2708 | 0.41813 | 5 | Each | 2.9765 | 3.6235 | 4.8235 | LogNormal | 3.6235 | 0.31645 | 1 | 14.4941 |  |  |  | 1.8117 | 0.31645 | 5 | Each | [45 empty] | 1
| D5012.033h |  | D5012.033h | Distribution Panel - Capacity: 750 to <1200 Amp - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only | 24400 | 29600 | 29600 | Normal | 27866.6521 | 0.072804 | 1 | 35520 |  |  |  | 23680 | 0.072804 | 5 | Each | [60 empty] | 3.2294 | 3.9176 | 3.9176 | Normal | 3.9176 | 0.26039 | 1 | 11.7529 |  |  |  | 1.9588 | 0.26039 | 5 | Each | [60 empty] | 1
| D5012.033i |  | D5012.033i | Distribution Panel - Capacity: 750 to <1200 Amp - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | 900 | 1200 | 2000 | LogNormal | 1283.8705 | 0.33516 | 1 | 1440 |  |  |  | 960 | 0.33516 | 5 | Each | 25300 | 30800 | 41000 | LogNormal | 31700.7593 | 0.19401 | 1 | 36960 |  |  |  | 24640 | 0.19401 | 5 | Each | 24400 | 29600 | 29600 | Normal | 27866.594 | 0.072803 | 1 | 35520 |  |  |  | 23680 | 0.072803 | 5 | Each | [30 empty] | 1.1912 | 1.5882 | 2.6471 | LogNormal | 1.5882 | 0.41813 | 1 | 1.9058 |  |  |  | 1.2706 | 0.41813 | 5 | Each | 3.3485 | 4.0765 | 5.4265 | LogNormal | 4.0765 | 0.31645 | 1 | 12.2294 |  |  |  | 2.0383 | 0.31645 | 5 | Each | 3.2294 | 3.9176 | 3.9176 | Normal | 3.9176 | 0.26038 | 1 | 11.7529 |  |  |  | 1.9588 | 0.26038 | 5 | Each | [30 empty] | 1
| D5012.033j |  | D5012.033j | Distribution Panel - Capacity: 1200 to 2000 Amp - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only | 900 | 1200 | 2000 | LogNormal | 1283.8705 | 0.33516 | 1 | 1560 |  |  |  | 1080 | 0.33516 | 5 | Each | 43800 | 52600 | 69500 | LogNormal | 54252.8179 | 0.18591 | 1 | 68380 |  |  |  | 47340 | 0.18591 | 5 | Each | [45 empty] | 1.059 | 1.412 | 2.353 | LogNormal | 1.412 | 0.41813 | 1 | 1.8355 |  |  |  | 1.2708 | 0.41813 | 5 | Each | 3.6071 | 4.3318 | 5.7235 | LogNormal | 4.3318 | 0.31155 | 1 | 22.8965 |  |  |  | 2.1659 | 0.31155 | 5 | Each | [45 empty] | 1
| D5012.033k |  | D5012.033k | Distribution Panel - Capacity: 1200 to 2000 Amp - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only | 42900 | 51400 | 51400 | Normal | 48566.6409 | 0.068284 | 1 | 61680 |  |  |  | 41120 | 0.068284 | 5 | Each | [60 empty] | 3.9746 | 4.7621 | 4.7621 | Normal | 4.7621 | 0.25916 | 1 | 18.368 |  |  |  | 2.3811 | 0.25916 | 5 | Each | [60 empty] | 1
| D5012.033l |  | D5012.033l | Distribution Panel - Capacity: 1200 to 2000 Amp - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | 900 | 1200 | 2000 | LogNormal | 1283.8705 | 0.33516 | 1 | 1440 |  |  |  | 960 | 0.33516 | 5 | Each | 43800 | 52600 | 69500 | LogNormal | 54252.8179 | 0.18591 | 1 | 63120 |  |  |  | 42080 | 0.18591 | 5 | Each | 42900 | 51400 | 51400 | Normal | 48566.6488 | 0.068283 | 1 | 61680 |  |  |  | 41120 | 0.068283 | 5 | Each | [30 empty] | 1.1912 | 1.5882 | 2.6471 | LogNormal | 1.5882 | 0.41813 | 1 | 1.9058 |  |  |  | 1.2706 | 0.41813 | 5 | Each | 4.0579 | 4.8732 | 6.439 | LogNormal | 4.8732 | 0.31155 | 1 | 18.7967 |  |  |  | 2.4366 | 0.31155 | 5 | Each | 3.9746 | 4.7621 | 4.7621 | Normal | 4.7621 | 0.25916 | 1 | 18.368 |  |  |  | 2.3811 | 0.25916 | 5 | Each | [30 empty] | 1
| D5092.011a |  | D5092.011a | Battery Rack - Capacity: all - Unanchored equipment that is not vibration isolated - Equipment fragility only | 11000 | 12000 | 14000 | LogNormal | 12270.3904 | 0.096207 | 1 | 14400 |  |  |  | 9600 | 0.096207 | 5 | Each | 400 | 750 | 900 | Normal | 683.333 | 0.28548 | 1 | 900 |  |  |  | 600 | 0.28548 | 5 | Each | 2200 | 3150 | 4150 | Normal | 3166.6658 | 0.24025 | 1 | 3780 |  |  |  | 2520 | 0.24025 | 5 | Each | [30 empty] | 14.5588 | 15.8824 | 18.5294 | LogNormal | 15.8824 | 0.26787 | 1 | 19.0589 |  |  |  | 12.7059 | 0.26787 | 5 | Each | 0.5294 | 0.9926 | 1.1912 | Normal | 0.9926 | 0.37947 | 1 | 1.1911 |  |  |  | 0.79407 | 0.37947 | 5 | Each | 2.9118 | 4.1691 | 5.4926 | Normal | 4.1691 | 0.34673 | 1 | 5.0029 |  |  |  | 3.3353 | 0.34673 | 5 | Each | [30 empty] | 1
| D5092.013a |  | D5092.013a | Battery Rack - Capacity: all - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only | 800 | 1000 | 1150 | Normal | 983.3316 | 0.13887 | 1 | 1200 |  |  |  | 800 | 0.13887 | 5 | Each | 14000 | 16150 | 19300 | LogNormal | 16338.5182 | 0.12674 | 1 | 19380 |  |  |  | 12920 | 0.12674 | 5 | Each | [45 empty] | 1.0588 | 1.3235 | 1.5221 | Normal | 1.3235 | 0.28598 | 1 | 1.5882 |  |  |  | 1.0588 | 0.28598 | 5 | Each | 18.5294 | 21.375 | 25.5441 | LogNormal | 21.375 | 0.28029 | 1 | 25.65 |  |  |  | 17.1 | 0.28029 | 5 | Each | [45 empty] | 1
| D5092.013b |  | D5092.013b | Battery Rack - Capacity: all - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only | 11000 | 12000 | 14000 | LogNormal | 12270.3904 | 0.096207 | 1 | 14400 |  |  |  | 9600 | 0.096207 | 5 | Each | 400 | 750 | 900 | Normal | 683.333 | 0.28548 | 1 | 900 |  |  |  | 600 | 0.28548 | 5 | Each | 2200 | 3150 | 4150 | Normal | 3166.6658 | 0.24025 | 1 | 3780 |  |  |  | 2520 | 0.24025 | 5 | Each | [30 empty] | 14.5588 | 15.8824 | 18.5294 | LogNormal | 15.8824 | 0.26787 | 1 | 19.0589 |  |  |  | 12.7059 | 0.26787 | 5 | Each | 0.5294 | 0.9926 | 1.1912 | Normal | 0.9926 | 0.37947 | 1 | 1.1911 |  |  |  | 0.79407 | 0.37947 | 5 | Each | 2.9118 | 4.1691 | 5.4926 | Normal | 4.1691 | 0.34673 | 1 | 5.0029 |  |  |  | 3.3353 | 0.34673 | 5 | Each | [30 empty] | 1
| D5092.013c |  | D5092.013c | Battery Rack - Capacity: all - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | 800 | 1000 | 1150 | Normal | 983.3316 | 0.13887 | 1 | 1200 |  |  |  | 800 | 0.13887 | 5 | Each | 14000 | 16150 | 19300 | LogNormal | 16338.5182 | 0.12674 | 1 | 19380 |  |  |  | 12920 | 0.12674 | 5 | Each | 11000 | 12000 | 14000 | LogNormal | 12270.3904 | 0.096207 | 1 | 14400 |  |  |  | 9600 | 0.096207 | 5 | Each | 11400 | 12750 | 14900 | LogNormal | 12936.3953 | 0.106 | 1 | 15300 |  |  |  | 10200 | 0.106 | 5 | Each | 14400 | 16900 | 20200 | LogNormal | 17001.4949 | 0.13285 | 1 | 20280 |  |  |  | 13520 | 0.13285 | 5 | Each | 1.0588 | 1.3235 | 1.5221 | Normal | 1.3235 | 0.28598 | 1 | 1.5882 |  |  |  | 1.0588 | 0.28598 | 5 | Each | 18.5294 | 21.375 | 25.5441 | LogNormal | 21.375 | 0.28029 | 1 | 25.65 |  |  |  | 17.1 | 0.28029 | 5 | Each | 14.5588 | 15.8824 | 18.5294 | LogNormal | 15.8824 | 0.26787 | 1 | 19.0589 |  |  |  | 12.7059 | 0.26787 | 5 | Each | 15.0882 | 16.875 | 19.7206 | LogNormal | 16.875 | 0.27154 | 1 | 20.25 |  |  |  | 13.5 | 0.27154 | 5 | Each | 19.0588 | 22.3676 | 26.7353 | LogNormal | 22.3676 | 0.28311 | 1 | 26.8411 |  |  |  | 17.8941 | 0.28311 | 5 | Each | 1
| D5092.021a |  | D5092.021a | Battery Charger - Capacity: all - Unanchored equipment that is not vibration isolated - Equipment fragility only | 600 | 800 | 900 | Normal | 766.6676 | 0.15267 | 1 | 960 |  |  |  | 640 | 0.15267 | 5 | Each | 10200 | 12150 | 14150 | Normal | 12166.6628 | 0.12667 | 1 | 14580 |  |  |  | 9720 | 0.12667 | 5 | Each | [45 empty] | 0.7941 | 1.0588 | 1.1912 | Normal | 1.0588 | 0.29293 | 1 | 1.2706 |  |  |  | 0.84704 | 0.29293 | 5 | Each | 13.5 | 16.0809 | 18.7279 | Normal | 16.0809 | 0.28026 | 1 | 19.2971 |  |  |  | 12.8647 | 0.28026 | 5 | Each | [45 empty] | 1
| D5092.023a |  | D5092.023a | Battery Charger - Capacity: all - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only | 500 | 700 | 850 | Normal | 683.3297 | 0.19983 | 1 | 770 |  |  |  | 630 | 0.19983 | 5 | Each | 10700 | 12850 | 15000 | Normal | 12850.0001 | 0.13056 | 1 | 14135 |  |  |  | 11565 | 0.13056 | 5 | Each | [45 empty] | 0.6618 | 0.9265 | 1.125 | Normal | 0.9265 | 0.32005 | 1 | 1.0191 |  |  |  | 0.83385 | 0.32005 | 5 | Each | 14.1618 | 17.0074 | 19.8529 | Normal | 17.0074 | 0.28204 | 1 | 18.7081 |  |  |  | 15.3067 | 0.28204 | 5 | Each | [45 empty] | 1
| D5092.023b |  | D5092.023b | Battery Charger - Capacity: all - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only | 600 | 800 | 900 | Normal | 766.6676 | 0.15267 | 1 | 1040 |  |  |  | 720 | 0.15267 | 5 | Each | 10200 | 12150 | 14150 | Normal | 12166.6628 | 0.12667 | 1 | 15795 |  |  |  | 10935 | 0.12667 | 5 | Each | [45 empty] | 0.7059 | 0.9412 | 1.0588 | Normal | 0.9412 | 0.29293 | 1 | 1.2236 |  |  |  | 0.84708 | 0.29293 | 5 | Each | 12 | 14.2941 | 16.6471 | Normal | 14.2941 | 0.28026 | 1 | 18.5823 |  |  |  | 12.8647 | 0.28026 | 5 | Each | [45 empty] | 1
| D5092.023c |  | D5092.023c | Battery Charger - Capacity: all - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | 500 | 700 | 850 | Normal | 683.3297 | 0.19983 | 1 | 910 |  |  |  | 630 | 0.19983 | 5 | Each | 10700 | 12850 | 15000 | Normal | 12850.0001 | 0.13056 | 1 | 16705 |  |  |  | 11565 | 0.13056 | 5 | Each | 10200 | 12150 | 14150 | Normal | 12166.6628 | 0.12667 | 1 | 15795 |  |  |  | 10935 | 0.12667 | 5 | Each | 10200 | 12150 | 14150 | Normal | 12166.6628 | 0.12667 | 1 | 15795 |  |  |  | 10935 | 0.12667 | 5 | Each | [15 empty] | 0.5882 | 0.8235 | 1 | Normal | 0.8235 | 0.32005 | 1 | 1.0706 |  |  |  | 0.74115 | 0.32005 | 5 | Each | 12.5882 | 15.1176 | 17.6471 | Normal | 15.1176 | 0.28204 | 1 | 19.6529 |  |  |  | 13.6058 | 0.28204 | 5 | Each | 12 | 14.2941 | 16.6471 | Normal | 14.2941 | 0.28026 | 1 | 18.5823 |  |  |  | 12.8647 | 0.28026 | 5 | Each | 12 | 14.2941 | 16.6471 | Normal | 14.2941 | 0.28026 | 1 | 18.5823 |  |  |  | 12.8647 | 0.28026 | 5 | Each | [15 empty] | 1
| D5092.031a |  | D5092.031a | Diesel generator - Capacity: 100 to <350 kVA - Unanchored equipment that is not vibration isolated - Equipment fragility only | 170 | 200 | 260 | LogNormal | 206.6128 | 0.17133 | 1 | 220 |  |  |  | 180 | 0.17133 | 5 | Each | 2130 | 2500 | 3250 | LogNormal | 2584.6827 | 0.17052 | 1 | 3250 |  |  |  | 2000 | 0.17052 | 5 | Each | 430 | 500 | 650 | LogNormal | 518.5517 | 0.16726 | 1 | 600 |  |  |  | 400 | 0.16726 | 5 | Each | 430 | 500 | 650 | LogNormal | 518.5517 | 0.16726 | 1 | 600 |  |  |  | 400 | 0.16726 | 5 | Each | [15 empty] | 0.15 | 0.1765 | 0.2294 | LogNormal | 0.1765 | 0.30308 | 1 | 0.19415 |  |  |  | 0.15885 | 0.30308 | 5 | Each | 1.8794 | 2.2059 | 2.8676 | LogNormal | 2.2059 | 0.30262 | 1 | 2.8677 |  |  |  | 1.7647 | 0.30262 | 5 | Each | 0.3794 | 0.4412 | 0.5735 | LogNormal | 0.4412 | 0.30079 | 1 | 0.52944 |  |  |  | 0.35296 | 0.30079 | 5 | Each | 0.3794 | 0.4412 | 0.5735 | LogNormal | 0.4412 | 0.30079 | 1 | 0.52944 |  |  |  | 0.35296 | 0.30079 | 5 | Each | [15 empty] | 1
| D5092.031b |  | D5092.031b | Diesel generator - Capacity: 350 to <750 kVA - Unanchored equipment that is not vibration isolated - Equipment fragility only | 340 | 400 | 520 | LogNormal | 413.2256 | 0.17133 | 1 | 440 |  |  |  | 360 | 0.17133 | 5 | Each | 4250 | 5000 | 6500 | LogNormal | 5165.3205 | 0.17133 | 1 | 6500 |  |  |  | 4000 | 0.17133 | 5 | Each | 680 | 800 | 1040 | LogNormal | 826.4512 | 0.17133 | 1 | 960 |  |  |  | 640 | 0.17133 | 5 | Each | 680 | 800 | 1040 | LogNormal | 826.4512 | 0.17133 | 1 | 960 |  |  |  | 640 | 0.17133 | 5 | Each | [15 empty] | 0.3 | 0.3529 | 0.4588 | LogNormal | 0.3529 | 0.30308 | 1 | 0.38819 |  |  |  | 0.31761 | 0.30308 | 5 | Each | 3.75 | 4.4118 | 5.7353 | LogNormal | 4.4118 | 0.30308 | 1 | 5.7353 |  |  |  | 3.5294 | 0.30308 | 5 | Each | 0.6 | 0.7059 | 0.9176 | LogNormal | 0.7059 | 0.30308 | 1 | 0.84708 |  |  |  | 0.56472 | 0.30308 | 5 | Each | 0.6 | 0.7059 | 0.9176 | LogNormal | 0.7059 | 0.30308 | 1 | 0.84708 |  |  |  | 0.56472 | 0.30308 | 5 | Each | [15 empty] | 1
| D5092.031c |  | D5092.031c | Diesel generator - Capacity: 750 to 1200 kVA - Unanchored equipment that is not vibration isolated - Equipment fragility only | 770 | 900 | 1170 | LogNormal | 931.7787 | 0.16907 | 1 | 990 |  |  |  | 810 | 0.16907 | 5 | Each | 6800 | 8000 | 10400 | LogNormal | 8264.513 | 0.17133 | 1 | 10400 |  |  |  | 6400 | 0.17133 | 5 | Each | 1020 | 1200 | 1560 | LogNormal | 1239.6767 | 0.17133 | 1 | 1440 |  |  |  | 960 | 0.17133 | 5 | Each | 1020 | 1200 | 1560 | LogNormal | 1239.6767 | 0.17133 | 1 | 1440 |  |  |  | 960 | 0.17133 | 5 | Each | [15 empty] | 0.6794 | 0.7941 | 1.0324 | LogNormal | 0.7941 | 0.3018 | 1 | 0.87351 |  |  |  | 0.71469 | 0.3018 | 5 | Each | 6 | 7.0588 | 9.1765 | LogNormal | 7.0588 | 0.30308 | 1 | 9.1764 |  |  |  | 5.647 | 0.30308 | 5 | Each | 0.9 | 1.0588 | 1.3765 | LogNormal | 1.0588 | 0.30308 | 1 | 1.2706 |  |  |  | 0.84704 | 0.30308 | 5 | Each | 0.9 | 1.0588 | 1.3765 | LogNormal | 1.0588 | 0.30308 | 1 | 1.2706 |  |  |  | 0.84704 | 0.30308 | 5 | Each | [15 empty] | 1
| D5092.031d |  | D5092.031d | Diesel generator - Capacity: 1200 to 2000 kVa - Unanchored equipment that is not vibration isolated - Equipment fragility only | 1280 | 1500 | 1950 | LogNormal | 1551.6177 | 0.16997 | 1 | 1950 |  |  |  | 1350 | 0.16997 | 5 | Each | 8500 | 10000 | 13000 | LogNormal | 10330.6406 | 0.17133 | 1 | 13000 |  |  |  | 9000 | 0.17133 | 5 | Each | 1020 | 1200 | 1560 | LogNormal | 1239.6767 | 0.17133 | 1 | 1560 |  |  |  | 1080 | 0.17133 | 5 | Each | 1020 | 1200 | 1560 | LogNormal | 1239.6767 | 0.17133 | 1 | 1560 |  |  |  | 1080 | 0.17133 | 5 | Each | [15 empty] | 1.3176 | 1.5441 | 2.0074 | LogNormal | 1.5441 | 0.30231 | 1 | 2.0073 |  |  |  | 1.3897 | 0.30231 | 5 | Each | 8.75 | 10.2941 | 13.3824 | LogNormal | 10.2941 | 0.30308 | 1 | 13.3823 |  |  |  | 9.2647 | 0.30308 | 5 | Each | 1.05 | 1.2353 | 1.6059 | LogNormal | 1.2353 | 0.30308 | 1 | 1.6059 |  |  |  | 1.1118 | 0.30308 | 5 | Each | 1.05 | 1.2353 | 1.6059 | LogNormal | 1.2353 | 0.30308 | 1 | 1.6059 |  |  |  | 1.1118 | 0.30308 | 5 | Each | [15 empty] | 1
| D5092.032a |  | D5092.032a | Diesel generator - Capacity: 100 to <350 kVA - Vibration isolated equipment that is not snubbed or restrained - Anchorage fragility only | 500 | 1000 | 1700 | LogNormal | 958.6389 | 0.45231 | 1 | 1300 |  |  |  | 900 | 0.45231 | 5 | Each | 86600 | 102200 | 133500 | LogNormal | 105633.7468 | 0.17462 | 1 | 132860 |  |  |  | 91980 | 0.17462 | 5 | Each | [45 empty] | 0.4412 | 0.8824 | 1.5 | LogNormal | 0.8824 | 0.5168 | 1 | 1.1471 |  |  |  | 0.79416 | 0.5168 | 5 | Each | 15.2824 | 18.0353 | 23.5588 | LogNormal | 18.0353 | 0.30495 | 1 | 45.0882 |  |  |  | 9.0177 | 0.30495 | 5 | Each | [45 empty] | 1
| D5092.032b |  | D5092.032b | Diesel generator - Capacity: 100 to <350 kVA - Vibration isolated equipment that is not snubbed or restrained - Equipment fragility only | 170 | 200 | 260 | LogNormal | 206.6128 | 0.17133 | 1 | 220 |  |  |  | 180 | 0.17133 | 5 | Each | 2130 | 2500 | 3250 | LogNormal | 2584.6827 | 0.17052 | 1 | 3250 |  |  |  | 2000 | 0.17052 | 5 | Each | 430 | 500 | 650 | LogNormal | 518.5517 | 0.16726 | 1 | 600 |  |  |  | 400 | 0.16726 | 5 | Each | 430 | 500 | 650 | LogNormal | 518.5517 | 0.16726 | 1 | 600 |  |  |  | 400 | 0.16726 | 5 | Each | [15 empty] | 0.15 | 0.1765 | 0.2294 | LogNormal | 0.1765 | 0.30308 | 1 | 0.19415 |  |  |  | 0.15885 | 0.30308 | 5 | Each | 1.8794 | 2.2059 | 2.8676 | LogNormal | 2.2059 | 0.30262 | 1 | 2.8677 |  |  |  | 1.7647 | 0.30262 | 5 | Each | 0.3794 | 0.4412 | 0.5735 | LogNormal | 0.4412 | 0.30079 | 1 | 0.52944 |  |  |  | 0.35296 | 0.30079 | 5 | Each | 0.3794 | 0.4412 | 0.5735 | LogNormal | 0.4412 | 0.30079 | 1 | 0.52944 |  |  |  | 0.35296 | 0.30079 | 5 | Each | [15 empty] | 1
| D5092.032c |  | D5092.032c | Diesel generator - Capacity: 100 to <350 kVA - Vibration isolated equipment that is not snubbed or restrained - Combined anchorage/isolator & equipment fragility | 500 | 1000 | 1700 | LogNormal | 958.6389 | 0.45231 | 1 | 1300 |  |  |  | 900 | 0.45231 | 5 | Each | 86600 | 102200 | 133500 | LogNormal | 105633.7468 | 0.17462 | 1 | 132860 |  |  |  | 91980 | 0.17462 | 5 | Each | 170 | 200 | 260 | LogNormal | 206.6128 | 0.17133 | 1 | 260 |  |  |  | 180 | 0.17133 | 5 | Each | 2130 | 2500 | 3250 | LogNormal | 2584.6827 | 0.17052 | 1 | 3250 |  |  |  | 2250 | 0.17052 | 5 | Each | 430 | 500 | 650 | LogNormal | 518.5517 | 0.16726 | 1 | 650 |  |  |  | 450 | 0.16726 | 5 | Each | 0.5147 | 1.0294 | 1.75 | LogNormal | 1.0294 | 0.5168 | 1 | 1.3382 |  |  |  | 0.92646 | 0.5168 | 5 | Each | 17.8294 | 21.0412 | 27.4853 | LogNormal | 21.0412 | 0.30495 | 1 | 52.603 |  |  |  | 10.5206 | 0.30495 | 5 | Each | 0.175 | 0.2059 | 0.2676 | LogNormal | 0.2059 | 0.30308 | 1 | 0.26766 |  |  |  | 0.18531 | 0.30308 | 5 | Each | 2.1926 | 2.5735 | 3.3456 | LogNormal | 2.5735 | 0.30262 | 1 | 3.3456 |  |  |  | 2.3161 | 0.30262 | 5 | Each | 0.4426 | 0.5147 | 0.6691 | LogNormal | 0.5147 | 0.30079 | 1 | 0.66911 |  |  |  | 0.46323 | 0.30079 | 5 | Each | 1
| D5092.032d |  | D5092.032d | Diesel generator - Capacity: 350 to <750 kVA - Vibration isolated equipment that is not snubbed or restrained - Anchorage fragility only | 800 | 1500 | 2400 | Normal | 1566.6663 | 0.39845 | 1 | 1650 |  |  |  | 1350 | 0.39845 | 5 | Each | 173300 | 204500 | 266700 | LogNormal | 211266.9 | 0.17385 | 1 | 265850 |  |  |  | 163600 | 0.17385 | 5 | Each | [45 empty] | 0.7059 | 1.3235 | 2.1176 | Normal | 1.3235 | 0.47039 | 1 | 1.4559 |  |  |  | 1.1911 | 0.47039 | 5 | Each | 22.9368 | 27.0662 | 35.2985 | LogNormal | 27.0662 | 0.30451 | 1 | 81.1986 |  |  |  | 13.5331 | 0.30451 | 5 | Each | [45 empty] | 1
| D5092.032e |  | D5092.032e | Diesel generator - Capacity: 350 to <750 kVA - Vibration isolated equipment that is not snubbed or restrained - Equipment fragility only | 340 | 400 | 520 | LogNormal | 413.2256 | 0.17133 | 1 | 440 |  |  |  | 360 | 0.17133 | 5 | Each | 4250 | 5000 | 6500 | LogNormal | 5165.3205 | 0.17133 | 1 | 6500 |  |  |  | 4000 | 0.17133 | 5 | Each | 680 | 800 | 1040 | LogNormal | 826.4512 | 0.17133 | 1 | 960 |  |  |  | 640 | 0.17133 | 5 | Each | 680 | 800 | 1040 | LogNormal | 826.4512 | 0.17133 | 1 | 960 |  |  |  | 640 | 0.17133 | 5 | Each | [15 empty] | 0.3 | 0.3529 | 0.4588 | LogNormal | 0.3529 | 0.30308 | 1 | 0.38819 |  |  |  | 0.31761 | 0.30308 | 5 | Each | 3.75 | 4.4118 | 5.7353 | LogNormal | 4.4118 | 0.30308 | 1 | 5.7353 |  |  |  | 3.5294 | 0.30308 | 5 | Each | 0.6 | 0.7059 | 0.9176 | LogNormal | 0.7059 | 0.30308 | 1 | 0.84708 |  |  |  | 0.56472 | 0.30308 | 5 | Each | 0.6 | 0.7059 | 0.9176 | LogNormal | 0.7059 | 0.30308 | 1 | 0.84708 |  |  |  | 0.56472 | 0.30308 | 5 | Each | [15 empty] | 1
| D5092.032f |  | D5092.032f | Diesel generator - Capacity: 350 to <750 kVA - Vibration isolated equipment that is not snubbed or restrained - Combined anchorage/isolator & equipment fragility | 800 | 1500 | 2400 | Normal | 1566.6663 | 0.39845 | 1 | 1950 |  |  |  | 1350 | 0.39845 | 5 | Each | 173300 | 204500 | 266700 | LogNormal | 211266.9 | 0.17385 | 1 | 265850 |  |  |  | 184050 | 0.17385 | 5 | Each | 340 | 400 | 520 | LogNormal | 413.2256 | 0.17133 | 1 | 520 |  |  |  | 360 | 0.17133 | 5 | Each | 4250 | 5000 | 6500 | LogNormal | 5165.3205 | 0.17133 | 1 | 6500 |  |  |  | 4500 | 0.17133 | 5 | Each | 680 | 800 | 1040 | LogNormal | 826.4512 | 0.17133 | 1 | 1040 |  |  |  | 720 | 0.17133 | 5 | Each | 0.8235 | 1.5441 | 2.4706 | Normal | 1.5441 | 0.47039 | 1 | 2.0073 |  |  |  | 1.3897 | 0.47039 | 5 | Each | 26.7596 | 31.5772 | 41.1816 | LogNormal | 31.5772 | 0.30451 | 1 | 94.7316 |  |  |  | 15.7886 | 0.30451 | 5 | Each | 0.35 | 0.4118 | 0.5353 | LogNormal | 0.4118 | 0.30308 | 1 | 0.53533 |  |  |  | 0.37062 | 0.30308 | 5 | Each | 4.375 | 5.1471 | 6.6912 | LogNormal | 5.1471 | 0.30308 | 1 | 6.6912 |  |  |  | 4.6324 | 0.30308 | 5 | Each | 0.7 | 0.8235 | 1.0706 | LogNormal | 0.8235 | 0.30308 | 1 | 1.0706 |  |  |  | 0.74115 | 0.30308 | 5 | Each | 1
| D5092.032g |  | D5092.032g | Diesel generator - Capacity: 750 to 1200 kVA - Vibration isolated equipment that is not snubbed or restrained - Anchorage fragility only | 1400 | 2200 | 3100 | Normal | 2233.3322 | 0.29698 | 1 | 2420 |  |  |  | 1980 | 0.29698 | 5 | Each | 324600 | 382400 | 498700 | LogNormal | 395270.8031 | 0.17326 | 1 | 497120 |  |  |  | 305920 | 0.17326 | 5 | Each | [45 empty] | 1.5441 | 2.4265 | 3.4191 | Normal | 2.4265 | 0.3882 | 1 | 2.6691 |  |  |  | 2.1839 | 0.3882 | 5 | Each | 35.8015 | 42.1765 | 55.0037 | LogNormal | 42.1765 | 0.30417 | 1 | 168.7059 |  |  |  | 21.0882 | 0.30417 | 5 | Each | [45 empty] | 1
| D5092.032h |  | D5092.032h | Diesel generator - Capacity: 750 to 1200 kVA - Vibration isolated equipment that is not snubbed or restrained - Equipment fragility only | 770 | 900 | 1170 | LogNormal | 931.7787 | 0.16907 | 1 | 990 |  |  |  | 810 | 0.16907 | 5 | Each | 6800 | 8000 | 10400 | LogNormal | 8264.513 | 0.17133 | 1 | 10400 |  |  |  | 6400 | 0.17133 | 5 | Each | 1020 | 1200 | 1560 | LogNormal | 1239.6767 | 0.17133 | 1 | 1440 |  |  |  | 960 | 0.17133 | 5 | Each | 1020 | 1200 | 1560 | LogNormal | 1239.6767 | 0.17133 | 1 | 1440 |  |  |  | 960 | 0.17133 | 5 | Each | [15 empty] | 0.6794 | 0.7941 | 1.0324 | LogNormal | 0.7941 | 0.3018 | 1 | 0.87351 |  |  |  | 0.71469 | 0.3018 | 5 | Each | 6 | 7.0588 | 9.1765 | LogNormal | 7.0588 | 0.30308 | 1 | 9.1764 |  |  |  | 5.647 | 0.30308 | 5 | Each | 0.9 | 1.0588 | 1.3765 | LogNormal | 1.0588 | 0.30308 | 1 | 1.2706 |  |  |  | 0.84704 | 0.30308 | 5 | Each | 0.9 | 1.0588 | 1.3765 | LogNormal | 1.0588 | 0.30308 | 1 | 1.2706 |  |  |  | 0.84704 | 0.30308 | 5 | Each | [15 empty] | 1
| D5092.032i |  | D5092.032i | Diesel generator - Capacity: 750 to 1200 kVA - Vibration isolated equipment that is not snubbed or restrained - Combined anchorage/isolator & equipment fragility | 1400 | 2200 | 3100 | Normal | 2233.3322 | 0.29698 | 1 | 2860 |  |  |  | 1980 | 0.29698 | 5 | Each | 324600 | 382400 | 498700 | LogNormal | 395270.8031 | 0.17326 | 1 | 497120 |  |  |  | 344160 | 0.17326 | 5 | Each | 770 | 900 | 1170 | LogNormal | 931.7787 | 0.16907 | 1 | 1170 |  |  |  | 810 | 0.16907 | 5 | Each | 6800 | 8000 | 10400 | LogNormal | 8264.513 | 0.17133 | 1 | 10400 |  |  |  | 7200 | 0.17133 | 5 | Each | 1020 | 1200 | 1560 | LogNormal | 1239.6767 | 0.17133 | 1 | 1560 |  |  |  | 1080 | 0.17133 | 5 | Each | 1.4412 | 2.2647 | 3.1912 | Normal | 2.2647 | 0.3882 | 1 | 2.9441 |  |  |  | 2.0382 | 0.3882 | 5 | Each | 33.4147 | 39.3647 | 51.3368 | LogNormal | 39.3647 | 0.30417 | 1 | 157.4588 |  |  |  | 19.6823 | 0.30417 | 5 | Each | 0.7926 | 0.9265 | 1.2044 | LogNormal | 0.9265 | 0.3018 | 1 | 1.2044 |  |  |  | 0.83385 | 0.3018 | 5 | Each | 7 | 8.2353 | 10.7059 | LogNormal | 8.2353 | 0.30308 | 1 | 10.7059 |  |  |  | 7.4118 | 0.30308 | 5 | Each | 1.05 | 1.2353 | 1.6059 | LogNormal | 1.2353 | 0.30308 | 1 | 1.6059 |  |  |  | 1.1118 | 0.30308 | 5 | Each | 1
| D5092.032j |  | D5092.032j | Diesel generator - Capacity: 1200 to 2000 kVa - Vibration isolated equipment that is not snubbed or restrained - Anchorage fragility only | 1600 | 2400 | 3400 | LogNormal | 2358.8816 | 0.28852 | 1 | 2640 |  |  |  | 2160 | 0.28852 | 5 | Each | 484100 | 570900 | 743200 | LogNormal | 589568.9572 | 0.1728 | 1 | 742170 |  |  |  | 456720 | 0.1728 | 5 | Each | [45 empty] | 1.4118 | 2.1176 | 3 | LogNormal | 2.1176 | 0.38177 | 1 | 2.3294 |  |  |  | 1.9058 | 0.38177 | 5 | Each | 29.9003 | 35.2615 | 45.9035 | LogNormal | 35.2615 | 0.30391 | 1 | 186.3821 |  |  |  | 17.6307 | 0.30391 | 5 | Each | [45 empty] | 1
| D5092.032k |  | D5092.032k | Diesel generator - Capacity: 1200 to 2000 kVa - Vibration isolated equipment that is not snubbed or restrained - Equipment fragility only | 1280 | 1500 | 1950 | LogNormal | 1551.6177 | 0.16997 | 1 | 1950 |  |  |  | 1350 | 0.16997 | 5 | Each | 8500 | 10000 | 13000 | LogNormal | 10330.6406 | 0.17133 | 1 | 13000 |  |  |  | 9000 | 0.17133 | 5 | Each | 1020 | 1200 | 1560 | LogNormal | 1239.6767 | 0.17133 | 1 | 1560 |  |  |  | 1080 | 0.17133 | 5 | Each | 1020 | 1200 | 1560 | LogNormal | 1239.6767 | 0.17133 | 1 | 1560 |  |  |  | 1080 | 0.17133 | 5 | Each | [15 empty] | 1.3176 | 1.5441 | 2.0074 | LogNormal | 1.5441 | 0.30231 | 1 | 2.0073 |  |  |  | 1.3897 | 0.30231 | 5 | Each | 8.75 | 10.2941 | 13.3824 | LogNormal | 10.2941 | 0.30308 | 1 | 13.3823 |  |  |  | 9.2647 | 0.30308 | 5 | Each | 1.05 | 1.2353 | 1.6059 | LogNormal | 1.2353 | 0.30308 | 1 | 1.6059 |  |  |  | 1.1118 | 0.30308 | 5 | Each | 1.05 | 1.2353 | 1.6059 | LogNormal | 1.2353 | 0.30308 | 1 | 1.6059 |  |  |  | 1.1118 | 0.30308 | 5 | Each | [15 empty] | 1
| D5092.032l |  | D5092.032l | Diesel generator - Capacity: 1200 to 2000 kVa - Vibration isolated equipment that is not snubbed or restrained - Combined anchorage/isolator & equipment fragility | 1600 | 2400 | 3400 | LogNormal | 2358.8816 | 0.28852 | 1 | 3120 |  |  |  | 2160 | 0.28852 | 5 | Each | 484100 | 570900 | 743200 | LogNormal | 589568.9572 | 0.1728 | 1 | 742170 |  |  |  | 513810 | 0.1728 | 5 | Each | 1280 | 1500 | 1950 | LogNormal | 1551.6177 | 0.16997 | 1 | 1950 |  |  |  | 1350 | 0.16997 | 5 | Each | 8500 | 10000 | 13000 | LogNormal | 10330.6406 | 0.17133 | 1 | 13000 |  |  |  | 9000 | 0.17133 | 5 | Each | 1020 | 1200 | 1560 | LogNormal | 1239.6767 | 0.17133 | 1 | 1560 |  |  |  | 1080 | 0.17133 | 5 | Each | 1.6471 | 2.4706 | 3.5 | LogNormal | 2.4706 | 0.38177 | 1 | 3.2118 |  |  |  | 2.2235 | 0.38177 | 5 | Each | 34.8837 | 41.1384 | 53.5541 | LogNormal | 41.1384 | 0.30391 | 1 | 217.4458 |  |  |  | 20.5692 | 0.30391 | 5 | Each | 1.3176 | 1.5441 | 2.0074 | LogNormal | 1.5441 | 0.30231 | 1 | 2.0073 |  |  |  | 1.3897 | 0.30231 | 5 | Each | 8.75 | 10.2941 | 13.3824 | LogNormal | 10.2941 | 0.30308 | 1 | 13.3823 |  |  |  | 9.2647 | 0.30308 | 5 | Each | 1.05 | 1.2353 | 1.6059 | LogNormal | 1.2353 | 0.30308 | 1 | 1.6059 |  |  |  | 1.1118 | 0.30308 | 5 | Each | 1
| D5092.033a |  | D5092.033a | Diesel generator - Capacity: 100 to <350 kVA - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only | 500 | 1000 | 1700 | LogNormal | 958.6389 | 0.45231 | 1 | 1300 |  |  |  | 900 | 0.45231 | 5 | Each | 86600 | 102200 | 133500 | LogNormal | 105633.7468 | 0.17462 | 1 | 132860 |  |  |  | 91980 | 0.17462 | 5 | Each | [45 empty] | 0.5147 | 1.0294 | 1.75 | LogNormal | 1.0294 | 0.5168 | 1 | 1.3382 |  |  |  | 0.92646 | 0.5168 | 5 | Each | 17.8294 | 21.0412 | 27.4853 | LogNormal | 21.0412 | 0.30495 | 1 | 52.603 |  |  |  | 10.5206 | 0.30495 | 5 | Each | [45 empty] | 1
| D5092.033b |  | D5092.033b | Diesel generator - Capacity: 100 to <350 kVA - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only | 170 | 200 | 260 | LogNormal | 206.6128 | 0.17133 | 1 | 260 |  |  |  | 180 | 0.17133 | 5 | Each | 2130 | 2500 | 3250 | LogNormal | 2584.6827 | 0.17052 | 1 | 3250 |  |  |  | 2250 | 0.17052 | 5 | Each | 430 | 500 | 650 | LogNormal | 518.5517 | 0.16726 | 1 | 650 |  |  |  | 450 | 0.16726 | 5 | Each | 430 | 500 | 650 | LogNormal | 518.5517 | 0.16726 | 1 | 650 |  |  |  | 450 | 0.16726 | 5 | Each | [15 empty] | 0.175 | 0.2059 | 0.2676 | LogNormal | 0.2059 | 0.30308 | 1 | 0.26766 |  |  |  | 0.18531 | 0.30308 | 5 | Each | 2.1926 | 2.5735 | 3.3456 | LogNormal | 2.5735 | 0.30262 | 1 | 3.3456 |  |  |  | 2.3161 | 0.30262 | 5 | Each | 0.4426 | 0.5147 | 0.6691 | LogNormal | 0.5147 | 0.30079 | 1 | 0.66911 |  |  |  | 0.46323 | 0.30079 | 5 | Each | 0.4426 | 0.5147 | 0.6691 | LogNormal | 0.5147 | 0.30079 | 1 | 0.66911 |  |  |  | 0.46323 | 0.30079 | 5 | Each | [15 empty] | 1
| D5092.033c |  | D5092.033c | Diesel generator - Capacity: 100 to <350 kVA - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | 500 | 1000 | 1700 | LogNormal | 958.6389 | 0.45231 | 1 | 1100 |  |  |  | 700 | 0.45231 | 5 | Each | 86600 | 102200 | 133500 | LogNormal | 105633.7468 | 0.17462 | 1 | 112420 |  |  |  | 91980 | 0.17462 | 5 | Each | 170 | 200 | 260 | LogNormal | 206.6128 | 0.17133 | 1 | 220 |  |  |  | 180 | 0.17133 | 5 | Each | 2130 | 2500 | 3250 | LogNormal | 2584.6827 | 0.17052 | 1 | 2750 |  |  |  | 2250 | 0.17052 | 5 | Each | 430 | 500 | 650 | LogNormal | 518.5517 | 0.16726 | 1 | 550 |  |  |  | 450 | 0.16726 | 5 | Each | 0.0735 | 0.1471 | 0.25 | LogNormal | 0.1471 | 0.5168 | 1 | 0.16181 |  |  |  | 0.10298 | 0.5168 | 5 | Each | 2.5471 | 3.0059 | 3.9265 | LogNormal | 3.0059 | 0.30495 | 1 | 4.5088 |  |  |  | 1.503 | 0.30495 | 5 | Each | 0.025 | 0.0294 | 0.0382 | LogNormal | 0.0294 | 0.30308 | 1 | 0.032341 |  |  |  | 0.026459 | 0.30308 | 5 | Each | 0.3132 | 0.3676 | 0.4779 | LogNormal | 0.3676 | 0.30262 | 1 | 0.40436 |  |  |  | 0.33084 | 0.30262 | 5 | Each | 0.0632 | 0.0735 | 0.0956 | LogNormal | 0.0735 | 0.30079 | 1 | 0.080853 |  |  |  | 0.066147 | 0.30079 | 5 | Each | 1
| D5092.033d |  | D5092.033d | Diesel generator - Capacity: 350 to <750 kVA - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only | 800 | 1500 | 2400 | Normal | 1566.6663 | 0.39845 | 1 | 1950 |  |  |  | 1350 | 0.39845 | 5 | Each | 173300 | 204500 | 266700 | LogNormal | 211266.9 | 0.17385 | 1 | 265850 |  |  |  | 184050 | 0.17385 | 5 | Each | [45 empty] | 0.8235 | 1.5441 | 2.4706 | Normal | 1.5441 | 0.47039 | 1 | 2.0073 |  |  |  | 1.3897 | 0.47039 | 5 | Each | 26.7596 | 31.5772 | 41.1816 | LogNormal | 31.5772 | 0.30451 | 1 | 94.7316 |  |  |  | 15.7886 | 0.30451 | 5 | Each | [45 empty] | 1
| D5092.033e |  | D5092.033e | Diesel generator - Capacity: 350 to <750 kVA - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only | 340 | 400 | 520 | LogNormal | 413.2256 | 0.17133 | 1 | 520 |  |  |  | 320 | 0.17133 | 5 | Each | 4250 | 5000 | 6500 | LogNormal | 5165.3205 | 0.17133 | 1 | 6500 |  |  |  | 4000 | 0.17133 | 5 | Each | 680 | 800 | 1040 | LogNormal | 826.4512 | 0.17133 | 1 | 960 |  |  |  | 640 | 0.17133 | 5 | Each | 680 | 800 | 1040 | LogNormal | 826.4512 | 0.17133 | 1 | 960 |  |  |  | 640 | 0.17133 | 5 | Each | [15 empty] | 0.45 | 0.5294 | 0.6882 | LogNormal | 0.5294 | 0.30308 | 1 | 0.68822 |  |  |  | 0.42352 | 0.30308 | 5 | Each | 5.625 | 6.6176 | 8.6029 | LogNormal | 6.6176 | 0.30308 | 1 | 8.6029 |  |  |  | 5.2941 | 0.30308 | 5 | Each | 0.9 | 1.0588 | 1.3765 | LogNormal | 1.0588 | 0.30308 | 1 | 1.2706 |  |  |  | 0.84704 | 0.30308 | 5 | Each | 0.9 | 1.0588 | 1.3765 | LogNormal | 1.0588 | 0.30308 | 1 | 1.2706 |  |  |  | 0.84704 | 0.30308 | 5 | Each | [15 empty] | 1
| D5092.033f |  | D5092.033f | Diesel generator - Capacity: 350 to <750 kVA - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | 800 | 1500 | 2400 | Normal | 1566.6663 | 0.39845 | 1 | 1650 |  |  |  | 1350 | 0.39845 | 5 | Each | 173300 | 204500 | 266700 | LogNormal | 211266.9 | 0.17385 | 1 | 224950 |  |  |  | 184050 | 0.17385 | 5 | Each | 340 | 400 | 520 | LogNormal | 413.2256 | 0.17133 | 1 | 440 |  |  |  | 360 | 0.17133 | 5 | Each | 4250 | 5000 | 6500 | LogNormal | 5165.3205 | 0.17133 | 1 | 5500 |  |  |  | 4500 | 0.17133 | 5 | Each | 680 | 800 | 1040 | LogNormal | 826.4512 | 0.17133 | 1 | 880 |  |  |  | 720 | 0.17133 | 5 | Each | 0.8824 | 1.6544 | 2.6471 | Normal | 1.6544 | 0.47039 | 1 | 1.8198 |  |  |  | 1.489 | 0.47039 | 5 | Each | 28.671 | 33.8327 | 44.1232 | LogNormal | 33.8327 | 0.30451 | 1 | 56.3878 |  |  |  | 16.9164 | 0.30451 | 5 | Each | 0.375 | 0.4412 | 0.5735 | LogNormal | 0.4412 | 0.30308 | 1 | 0.48532 |  |  |  | 0.39708 | 0.30308 | 5 | Each | 4.6875 | 5.5147 | 7.1691 | LogNormal | 5.5147 | 0.30308 | 1 | 6.0662 |  |  |  | 4.9632 | 0.30308 | 5 | Each | 0.75 | 0.8824 | 1.1471 | LogNormal | 0.8824 | 0.30308 | 1 | 0.97064 |  |  |  | 0.79416 | 0.30308 | 5 | Each | 1
| D5092.033g |  | D5092.033g | Diesel generator - Capacity: 750 to 1200 kVA - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only | 1400 | 2200 | 3100 | Normal | 2233.3322 | 0.29698 | 1 | 2860 |  |  |  | 1980 | 0.29698 | 5 | Each | 324600 | 382400 | 498700 | LogNormal | 395270.8031 | 0.17326 | 1 | 497120 |  |  |  | 344160 | 0.17326 | 5 | Each | [45 empty] | 1.4412 | 2.2647 | 3.1912 | Normal | 2.2647 | 0.3882 | 1 | 2.9441 |  |  |  | 2.0382 | 0.3882 | 5 | Each | 33.4147 | 39.3647 | 51.3368 | LogNormal | 39.3647 | 0.30417 | 1 | 157.4588 |  |  |  | 19.6823 | 0.30417 | 5 | Each | [45 empty] | 1
| D5092.033h |  | D5092.033h | Diesel generator - Capacity: 750 to 1200 kVA - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only | 770 | 900 | 1170 | LogNormal | 931.7787 | 0.16907 | 1 | 1170 |  |  |  | 720 | 0.16907 | 5 | Each | 6800 | 8000 | 10400 | LogNormal | 8264.513 | 0.17133 | 1 | 10400 |  |  |  | 6400 | 0.17133 | 5 | Each | 1020 | 1200 | 1560 | LogNormal | 1239.6767 | 0.17133 | 1 | 1440 |  |  |  | 960 | 0.17133 | 5 | Each | 1020 | 1200 | 1560 | LogNormal | 1239.6767 | 0.17133 | 1 | 1440 |  |  |  | 960 | 0.17133 | 5 | Each | [15 empty] | 1.0191 | 1.1912 | 1.5485 | LogNormal | 1.1912 | 0.3018 | 1 | 1.5486 |  |  |  | 0.95296 | 0.3018 | 5 | Each | 9 | 10.5882 | 13.7647 | LogNormal | 10.5882 | 0.30308 | 1 | 13.7647 |  |  |  | 8.4706 | 0.30308 | 5 | Each | 1.35 | 1.5882 | 2.0647 | LogNormal | 1.5882 | 0.30308 | 1 | 1.9058 |  |  |  | 1.2706 | 0.30308 | 5 | Each | 1.35 | 1.5882 | 2.0647 | LogNormal | 1.5882 | 0.30308 | 1 | 1.9058 |  |  |  | 1.2706 | 0.30308 | 5 | Each | [15 empty] | 1
| D5092.033i |  | D5092.033i | Diesel generator - Capacity: 750 to 1200 kVA - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | 1400 | 2200 | 3100 | Normal | 2233.3322 | 0.29698 | 1 | 2420 |  |  |  | 1980 | 0.29698 | 5 | Each | 324600 | 382400 | 498700 | LogNormal | 395270.8031 | 0.17326 | 1 | 420640 |  |  |  | 344160 | 0.17326 | 5 | Each | 770 | 900 | 1170 | LogNormal | 931.7787 | 0.16907 | 1 | 990 |  |  |  | 810 | 0.16907 | 5 | Each | 6800 | 8000 | 10400 | LogNormal | 8264.513 | 0.17133 | 1 | 8800 |  |  |  | 7200 | 0.17133 | 5 | Each | 1020 | 1200 | 1560 | LogNormal | 1239.6767 | 0.17133 | 1 | 1320 |  |  |  | 1080 | 0.17133 | 5 | Each | 1.5441 | 2.4265 | 3.4191 | Normal | 2.4265 | 0.3882 | 1 | 2.6691 |  |  |  | 2.1839 | 0.3882 | 5 | Each | 35.8015 | 42.1765 | 55.0037 | LogNormal | 42.1765 | 0.30417 | 1 | 84.353 |  |  |  | 21.0882 | 0.30417 | 5 | Each | 0.8493 | 0.9926 | 1.2904 | LogNormal | 0.9926 | 0.3018 | 1 | 1.0919 |  |  |  | 0.89334 | 0.3018 | 5 | Each | 7.5 | 8.8235 | 11.4706 | LogNormal | 8.8235 | 0.30308 | 1 | 9.7059 |  |  |  | 7.9411 | 0.30308 | 5 | Each | 1.125 | 1.3235 | 1.7206 | LogNormal | 1.3235 | 0.30308 | 1 | 1.4559 |  |  |  | 1.1911 | 0.30308 | 5 | Each | 1
| D5092.033j |  | D5092.033j | Diesel generator - Capacity: 1200 to 2000 kVa - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only | 1600 | 2400 | 3400 | LogNormal | 2358.8816 | 0.28852 | 1 | 3120 |  |  |  | 2160 | 0.28852 | 5 | Each | 484100 | 570900 | 743200 | LogNormal | 589568.9572 | 0.1728 | 1 | 742170 |  |  |  | 513810 | 0.1728 | 5 | Each | [45 empty] | 1.6471 | 2.4706 | 3.5 | LogNormal | 2.4706 | 0.38177 | 1 | 3.2118 |  |  |  | 2.2235 | 0.38177 | 5 | Each | 34.8837 | 41.1384 | 53.5541 | LogNormal | 41.1384 | 0.30391 | 1 | 217.4458 |  |  |  | 20.5692 | 0.30391 | 5 | Each | [45 empty] | 1
| D5092.033k |  | D5092.033k | Diesel generator - Capacity: 1200 to 2000 kVa - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only | 1280 | 1500 | 1950 | LogNormal | 1551.6177 | 0.16997 | 1 | 1650 |  |  |  | 1050 | 0.16997 | 5 | Each | 8500 | 10000 | 13000 | LogNormal | 10330.6406 | 0.17133 | 1 | 11000 |  |  |  | 9000 | 0.17133 | 5 | Each | 1020 | 1200 | 1560 | LogNormal | 1239.6767 | 0.17133 | 1 | 1320 |  |  |  | 1080 | 0.17133 | 5 | Each | 1020 | 1200 | 1560 | LogNormal | 1239.6767 | 0.17133 | 1 | 1320 |  |  |  | 1080 | 0.17133 | 5 | Each | [15 empty] | 0.1882 | 0.2206 | 0.2868 | LogNormal | 0.2206 | 0.30231 | 1 | 0.24266 |  |  |  | 0.15442 | 0.30231 | 5 | Each | 1.25 | 1.4706 | 1.9118 | LogNormal | 1.4706 | 0.30308 | 1 | 1.6177 |  |  |  | 1.3235 | 0.30308 | 5 | Each | 0.15 | 0.1765 | 0.2294 | LogNormal | 0.1765 | 0.30308 | 1 | 0.19415 |  |  |  | 0.15885 | 0.30308 | 5 | Each | 0.15 | 0.1765 | 0.2294 | LogNormal | 0.1765 | 0.30308 | 1 | 0.19415 |  |  |  | 0.15885 | 0.30308 | 5 | Each | [15 empty] | 1
| D5092.033l |  | D5092.033l | Diesel generator - Capacity: 1200 to 2000 kVa - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | 1600 | 2400 | 3400 | LogNormal | 2358.8816 | 0.28852 | 1 | 3120 |  |  |  | 2160 | 0.28852 | 5 | Each | 484100 | 570900 | 743200 | LogNormal | 589568.9572 | 0.1728 | 1 | 742170 |  |  |  | 513810 | 0.1728 | 5 | Each | 1280 | 1500 | 1950 | LogNormal | 1551.6177 | 0.16997 | 1 | 1950 |  |  |  | 1350 | 0.16997 | 5 | Each | 8500 | 10000 | 13000 | LogNormal | 10330.6406 | 0.17133 | 1 | 13000 |  |  |  | 9000 | 0.17133 | 5 | Each | 1020 | 1200 | 1560 | LogNormal | 1239.6767 | 0.17133 | 1 | 1560 |  |  |  | 1080 | 0.17133 | 5 | Each | 0.2353 | 0.3529 | 0.5 | LogNormal | 0.3529 | 0.38177 | 1 | 0.45878 |  |  |  | 0.31761 | 0.38177 | 5 | Each | 4.9834 | 5.8769 | 7.6506 | LogNormal | 5.8769 | 0.30391 | 1 | 31.0637 |  |  |  | 2.9385 | 0.30391 | 5 | Each | 0.1882 | 0.2206 | 0.2868 | LogNormal | 0.2206 | 0.30231 | 1 | 0.28678 |  |  |  | 0.19854 | 0.30231 | 5 | Each | 1.25 | 1.4706 | 1.9118 | LogNormal | 1.4706 | 0.30308 | 1 | 1.9118 |  |  |  | 1.3235 | 0.30308 | 5 | Each | 0.15 | 0.1765 | 0.2294 | LogNormal | 0.1765 | 0.30308 | 1 | 0.22944 |  |  |  | 0.15885 | 0.30308 | 5 | Each | 1
| E2022.001 |  | E2022.001 | Modular office work stations. | BY USER | BY USER | BY USER | BY USER | BY USER | BY USER | BY USER | BY USER |  |  |  | BY USER | BY USER | BY USER | BY USER | [60 empty] | BY USER | BY USER | BY USER | BY USER | BY USER | BY USER | BY USER | BY USER |  |  |  | BY USER | BY USER | BY USER | BY USER | [60 empty] | 1
| E2022.010 |  | E2022.010 | Unsecured fragile objects on shelves, unknown restraint | BY USER | BY USER | BY USER | BY USER | BY USER | BY USER | BY USER | BY USER |  |  |  | BY USER | BY USER | BY USER | BY USER | [60 empty] | BY USER | BY USER | BY USER | BY USER | BY USER | BY USER | BY USER | BY USER |  |  |  | BY USER | BY USER | BY USER | BY USER | [60 empty] | 1
| E2022.011 |  | E2022.011 | Fragile contents secured by museum putty, Velcro or other weak but sticky stuff | BY USER | BY USER | BY USER | BY USER | BY USER | BY USER | BY USER | BY USER |  |  |  | BY USER | BY USER | BY USER | BY USER | [60 empty] | BY USER | BY USER | BY USER | BY USER | BY USER | BY USER | BY USER | BY USER |  |  |  | BY USER | BY USER | BY USER | BY USER | [60 empty] | 1
| E2022.012 |  | E2022.012 | Fragile contents on shelves in storage cabinets with latches | BY USER | BY USER | BY USER | BY USER | BY USER | BY USER | BY USER | BY USER |  |  |  | BY USER | BY USER | BY USER | BY USER | [60 empty] | BY USER | BY USER | BY USER | BY USER | BY USER | BY USER | BY USER | BY USER |  |  |  | BY USER | BY USER | BY USER | BY USER | [60 empty] | 1
| E2022.013 |  | E2022.013 | Unsecured fragile objects on shelves, low friction surface | BY USER | BY USER | BY USER | BY USER | BY USER | BY USER | BY USER | BY USER |  |  |  | BY USER | BY USER | BY USER | BY USER | [60 empty] | BY USER | BY USER | BY USER | BY USER | BY USER | BY USER | BY USER | BY USER |  |  |  | BY USER | BY USER | BY USER | BY USER | [60 empty] | 1
| E2022.020 |  | E2022.020 | Home entertainment equipment, unknown installation | BY USER | BY USER | BY USER | BY USER | BY USER | BY USER | BY USER | BY USER |  |  |  | BY USER | BY USER | BY USER | BY USER | [60 empty] | BY USER | BY USER | BY USER | BY USER | BY USER | BY USER | BY USER | BY USER |  |  |  | BY USER | BY USER | BY USER | BY USER | [60 empty] | 1
| E2022.021 |  | E2022.021 | Electronic equipment on wall mount brackets | BY USER | BY USER | BY USER | BY USER | BY USER | BY USER | BY USER | BY USER |  |  |  | BY USER | BY USER | BY USER | BY USER | [60 empty] | BY USER | BY USER | BY USER | BY USER | BY USER | BY USER | BY USER | BY USER |  |  |  | BY USER | BY USER | BY USER | BY USER | [60 empty] | 1
| E2022.022 |  | E2022.022 | Desktop electronics including computers, monitors, stereos, etc on a slip resistant surface | BY USER | BY USER | BY USER | BY USER | BY USER | BY USER | BY USER | BY USER |  |  |  | BY USER | BY USER | BY USER | BY USER | [60 empty] | BY USER | BY USER | BY USER | BY USER | BY USER | BY USER | BY USER | BY USER |  |  |  | BY USER | BY USER | BY USER | BY USER | [60 empty] | 1
| E2022.023 |  | E2022.023 | Desktop electronics including computers, monitors, stereos, etc, smooth surface | BY USER | BY USER | BY USER | BY USER | BY USER | BY USER | BY USER | BY USER |  |  |  | BY USER | BY USER | BY USER | BY USER | [60 empty] | BY USER | BY USER | BY USER | BY USER | BY USER | BY USER | BY USER | BY USER |  |  |  | BY USER | BY USER | BY USER | BY USER | [60 empty] | 1
| E2022.102a |  | E2022.102a | Bookcase, 2 shelves, unanchored laterally | BY USER | BY USER | BY USER | BY USER | BY USER | BY USER | BY USER | BY USER |  |  |  | BY USER | BY USER | BY USER | BY USER | [60 empty] | BY USER | BY USER | BY USER | BY USER | BY USER | BY USER | BY USER | BY USER |  |  |  | BY USER | BY USER | BY USER | BY USER | [60 empty] | 1
| E2022.102b |  | E2022.102b | Bookcase, 2 shelves, anchored laterally | BY USER | BY USER | BY USER | BY USER | BY USER | BY USER | BY USER | BY USER |  |  |  | BY USER | BY USER | BY USER | BY USER | [60 empty] | BY USER | BY USER | BY USER | BY USER | BY USER | BY USER | BY USER | BY USER |  |  |  | BY USER | BY USER | BY USER | BY USER | [60 empty] | 1
| E2022.103a |  | E2022.103a | Bookcase, 3 shelves, unanchored laterally | BY USER | BY USER | BY USER | BY USER | BY USER | BY USER | BY USER | BY USER |  |  |  | BY USER | BY USER | BY USER | BY USER | [60 empty] | BY USER | BY USER | BY USER | BY USER | BY USER | BY USER | BY USER | BY USER |  |  |  | BY USER | BY USER | BY USER | BY USER | [60 empty] | 1
| E2022.103b |  | E2022.103b | Bookcase, 3 shelves, anchored laterally | BY USER | BY USER | BY USER | BY USER | BY USER | BY USER | BY USER | BY USER |  |  |  | BY USER | BY USER | BY USER | BY USER | [60 empty] | BY USER | BY USER | BY USER | BY USER | BY USER | BY USER | BY USER | BY USER |  |  |  | BY USER | BY USER | BY USER | BY USER | [60 empty] | 1
| E2022.104a |  | E2022.104a | Bookcase, 4 shelves, unanchored laterally | BY USER | BY USER | BY USER | BY USER | BY USER | BY USER | BY USER | BY USER |  |  |  | BY USER | BY USER | BY USER | BY USER | [60 empty] | BY USER | BY USER | BY USER | BY USER | BY USER | BY USER | BY USER | BY USER |  |  |  | BY USER | BY USER | BY USER | BY USER | [60 empty] | 1
| E2022.104b |  | E2022.104b | Bookcase, 4 shelves, anchored laterally | BY USER | BY USER | BY USER | BY USER | BY USER | BY USER | BY USER | BY USER |  |  |  | BY USER | BY USER | BY USER | BY USER | [60 empty] | BY USER | BY USER | BY USER | BY USER | BY USER | BY USER | BY USER | BY USER |  |  |  | BY USER | BY USER | BY USER | BY USER | [60 empty] | 1
| E2022.105a |  | E2022.105a | Bookcase, 5 shelves, unanchored laterally | BY USER | BY USER | BY USER | BY USER | BY USER | BY USER | BY USER | BY USER |  |  |  | BY USER | BY USER | BY USER | BY USER | [60 empty] | BY USER | BY USER | BY USER | BY USER | BY USER | BY USER | BY USER | BY USER |  |  |  | BY USER | BY USER | BY USER | BY USER | [60 empty] | 1
| E2022.105b |  | E2022.105b | Bookcase, 5 shelves, anchored laterally | BY USER | BY USER | BY USER | BY USER | BY USER | BY USER | BY USER | BY USER |  |  |  | BY USER | BY USER | BY USER | BY USER | [60 empty] | BY USER | BY USER | BY USER | BY USER | BY USER | BY USER | BY USER | BY USER |  |  |  | BY USER | BY USER | BY USER | BY USER | [60 empty] | 1
| E2022.106a |  | E2022.106a | Bookcase, 6 shelves, unanchored laterally | BY USER | BY USER | BY USER | BY USER | BY USER | BY USER | BY USER | BY USER |  |  |  | BY USER | BY USER | BY USER | BY USER | [60 empty] | BY USER | BY USER | BY USER | BY USER | BY USER | BY USER | BY USER | BY USER |  |  |  | BY USER | BY USER | BY USER | BY USER | [60 empty] | 1
| E2022.106b |  | E2022.106b | Bookcase, 6 shelves, anchored laterally | BY USER | BY USER | BY USER | BY USER | BY USER | BY USER | BY USER | BY USER |  |  |  | BY USER | BY USER | BY USER | BY USER | [60 empty] | BY USER | BY USER | BY USER | BY USER | BY USER | BY USER | BY USER | BY USER |  |  |  | BY USER | BY USER | BY USER | BY USER | [60 empty] | 1
| E2022.112a |  | E2022.112a | Vertical Filing Cabinet, 2 drawer, unanchored laterally | BY USER | BY USER | BY USER | BY USER | BY USER | BY USER | BY USER | BY USER |  |  |  | BY USER | BY USER | BY USER | BY USER | [60 empty] | BY USER | BY USER | BY USER | BY USER | BY USER | BY USER | BY USER | BY USER |  |  |  | BY USER | BY USER | BY USER | BY USER | [60 empty] | 1
| E2022.112b |  | E2022.112b | Vertical Filing Cabinet, 2 drawer, anchored laterally | BY USER | BY USER | BY USER | BY USER | BY USER | BY USER | BY USER | BY USER |  |  |  | BY USER | BY USER | BY USER | BY USER | [60 empty] | BY USER | BY USER | BY USER | BY USER | BY USER | BY USER | BY USER | BY USER |  |  |  | BY USER | BY USER | BY USER | BY USER | [60 empty] | 1
| E2022.114a |  | E2022.114a | Vertical Filing Cabinet, 4 drawer, unanchored laterally | BY USER | BY USER | BY USER | BY USER | BY USER | BY USER | BY USER | BY USER |  |  |  | BY USER | BY USER | BY USER | BY USER | [60 empty] | BY USER | BY USER | BY USER | BY USER | BY USER | BY USER | BY USER | BY USER |  |  |  | BY USER | BY USER | BY USER | BY USER | [60 empty] | 1
| E2022.114b |  | E2022.114b | Vertical Filing Cabinet, 4 drawer, anchored laterally | BY USER | BY USER | BY USER | BY USER | BY USER | BY USER | BY USER | BY USER |  |  |  | BY USER | BY USER | BY USER | BY USER | [60 empty] | BY USER | BY USER | BY USER | BY USER | BY USER | BY USER | BY USER | BY USER |  |  |  | BY USER | BY USER | BY USER | BY USER | [60 empty] | 1
| E2022.124a |  | E2022.124a | Lateral Filing Cabinet, 2 drawer, unanchored laterally | BY USER | BY USER | BY USER | BY USER | BY USER | BY USER | BY USER | BY USER |  |  |  | BY USER | BY USER | BY USER | BY USER | [60 empty] | BY USER | BY USER | BY USER | BY USER | BY USER | BY USER | BY USER | BY USER |  |  |  | BY USER | BY USER | BY USER | BY USER | [60 empty] | 1
| E2022.124b |  | E2022.124b | Lateral Filing Cabinet, 2 drawer, anchored laterally | BY USER | BY USER | BY USER | BY USER | BY USER | BY USER | BY USER | BY USER |  |  |  | BY USER | BY USER | BY USER | BY USER | [60 empty] | BY USER | BY USER | BY USER | BY USER | BY USER | BY USER | BY USER | BY USER |  |  |  | BY USER | BY USER | BY USER | BY USER | [60 empty] | 1
| E2022.125a |  | E2022.125a | Lateral Filing Cabinet, 4 drawer, unanchored laterally | BY USER | BY USER | BY USER | BY USER | BY USER | BY USER | BY USER | BY USER |  |  |  | BY USER | BY USER | BY USER | BY USER | [60 empty] | BY USER | BY USER | BY USER | BY USER | BY USER | BY USER | BY USER | BY USER |  |  |  | BY USER | BY USER | BY USER | BY USER | [60 empty] | 1
| E2022.125b |  | E2022.125b | Lateral Filing Cabinet, 4 drawer, anchored laterally | BY USER | BY USER | BY USER | BY USER | BY USER | BY USER | BY USER | BY USER |  |  |  | BY USER | BY USER | BY USER | BY USER | [60 empty] | BY USER | BY USER | BY USER | BY USER | BY USER | BY USER | BY USER | BY USER |  |  |  | BY USER | BY USER | BY USER | BY USER | [60 empty] | 1
| F1012.001 |  | F1012.001 | Storage racks designed and installed before 2007, big box retail (12' to 15' tall) | 2150 | 3100 | 5200 | LogNormal | 3241.2187 | 0.36217 | 26 | 6200 |  |  |  | 1860 | 0.36217 | 260 | LF 50 | 14250 | 18650 | 28700 | LogNormal | 19609.934 | 0.28811 | 26 | 37300 |  |  |  | 11190 | 0.28811 | 260 | LF 50 | [45 empty] | 2.37 | 3.42 | 5.735 | LogNormal | 3.42 | 0.44007 | 26 | 6.8391 |  |  |  | 2.0524 | 0.44007 | 260 | LF 50 | 15.715 | 20.57 | 31.655 | LogNormal | 20.57 | 0.38146 | 26 | 41.1399 |  |  |  | 12.3421 | 0.38146 | 260 | LF 50 | [45 empty] | 50
| D2021.011a |  | D2021.011a | Cold or Hot Potable - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC A or B, PIPING FRAGILITY | 90 | 290 | 740 | LogNormal | 278.8756 | 0.76369 | 1 | 319 |  |  |  | 261 | 0.76369 | 4 | Each (1000 ft pipe) | 1500 | 2650 | 4350 | LogNormal | 2596.8646 | 0.40537 | 1 | 2915 |  |  |  | 2385 | 0.40537 | 4 | Each (1000 ft pipe) | [45 empty] | 0.0953 | 0.3071 | 0.7835 | LogNormal | 0.3071 | 0.80357 | 1 | 0.33781 |  |  |  | 0.27639 | 0.80357 | 4 | Each (1000 ft pipe) | 0.1588 | 0.2806 | 0.4606 | LogNormal | 0.2806 | 0.47626 | 1 | 0.56119 |  |  |  | 0.1403 | 0.47626 | 4 | Each (1000 ft pipe) | [45 empty] | 1
| D2021.011b |  | D2021.011b | Cold or Hot Potable - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC A or B, BRACING FRAGILITY | 180 | 380 | 830 | LogNormal | 382.9373 | 0.60297 | 1 | 418 |  |  |  | 342 | 0.60297 | 4 | Each (1000 ft pipe) | 3600 | 3800 | 4250 | LogNormal | 3873.9954 | 0.066014 | 1 | 4180 |  |  |  | 3420 | 0.066014 | 4 | Each (1000 ft pipe) | [45 empty] | 0.1906 | 0.4024 | 0.8788 | LogNormal | 0.4024 | 0.65274 | 1 | 0.44264 |  |  |  | 0.36216 | 0.65274 | 4 | Each (1000 ft pipe) | 0.3812 | 0.4024 | 0.45 | LogNormal | 0.4024 | 0.25857 | 1 | 0.80475 |  |  |  | 0.2012 | 0.25857 | 4 | Each (1000 ft pipe) | [45 empty] | 1
| D2021.012a |  | D2021.012a | Cold or Hot Potable - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC C, PIPING FRAGILITY | 90 | 290 | 740 | LogNormal | 278.8756 | 0.76369 | 1 | 319 |  |  |  | 261 | 0.76369 | 4 | Each (1000 ft pipe) | 1500 | 2650 | 4350 | LogNormal | 2596.8646 | 0.40537 | 1 | 2915 |  |  |  | 2385 | 0.40537 | 4 | Each (1000 ft pipe) | [45 empty] | 0.0953 | 0.3071 | 0.7835 | LogNormal | 0.3071 | 0.80357 | 1 | 0.33781 |  |  |  | 0.27639 | 0.80357 | 4 | Each (1000 ft pipe) | 0.1588 | 0.2806 | 0.4606 | LogNormal | 0.2806 | 0.47626 | 1 | 0.56119 |  |  |  | 0.1403 | 0.47626 | 4 | Each (1000 ft pipe) | [45 empty] | 1
| D2021.012b |  | D2021.012b | Cold or Hot Potable - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC C, BRACING FRAGILITY | 180 | 380 | 830 | LogNormal | 382.9373 | 0.60297 | 1 | 418 |  |  |  | 342 | 0.60297 | 4 | Each (1000 ft pipe) | 3600 | 3800 | 4250 | LogNormal | 3873.9954 | 0.066014 | 1 | 4180 |  |  |  | 3420 | 0.066014 | 4 | Each (1000 ft pipe) | [45 empty] | 0.1906 | 0.4024 | 0.8788 | LogNormal | 0.4024 | 0.65274 | 1 | 0.44264 |  |  |  | 0.36216 | 0.65274 | 4 | Each (1000 ft pipe) | 0.3812 | 0.4024 | 0.45 | LogNormal | 0.4024 | 0.25857 | 1 | 0.80475 |  |  |  | 0.2012 | 0.25857 | 4 | Each (1000 ft pipe) | [45 empty] | 1
| D2021.013a |  | D2021.013a | Cold or Hot Potable - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC D, E, or F, PIPING FRAGILITY | 90 | 290 | 740 | LogNormal | 278.8756 | 0.76369 | 3 | 319 |  |  |  | 261 | 0.76369 | 10 | Each (1000 ft pipe) | 1500 | 2650 | 4350 | LogNormal | 2596.8646 | 0.40537 | 3 | 2915 |  |  |  | 2385 | 0.40537 | 10 | Each (1000 ft pipe) | [45 empty] | 0.0953 | 0.3071 | 0.7835 | LogNormal | 0.3071 | 0.80357 | 3 | 0.33781 |  |  |  | 0.27639 | 0.80357 | 10 | Each (1000 ft pipe) | 1.5882 | 2.8059 | 4.6059 | LogNormal | 2.8059 | 0.47626 | 3 | 3.0865 |  |  |  | 2.5253 | 0.47626 | 10 | Each (1000 ft pipe) | [45 empty] | 1
| D2021.013b |  | D2021.013b | Cold or Hot Potable - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC D, E, or F, BRACING FRAGILITY | 180 | 380 | 830 | LogNormal | 382.9373 | 0.60297 | 3 | 418 |  |  |  | 342 | 0.60297 | 10 | Each (1000 ft pipe) | [60 empty] | 0.1906 | 0.4024 | 0.8788 | LogNormal | 0.4024 | 0.65274 | 3 | 0.44264 |  |  |  | 0.36216 | 0.65274 | 10 | Each (1000 ft pipe) | [60 empty] | 1
| D2021.014a |  | D2021.014a | Cold or Hot Potable - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC D, E, or F (OSHPD or sim), PIPING FRAGILITY | 90 | 290 | 740 | LogNormal | 278.8756 | 0.76369 | 3 | 319 |  |  |  | 261 | 0.76369 | 10 | Each (1000 ft pipe) | 1500 | 2650 | 4350 | LogNormal | 2596.8646 | 0.40537 | 3 | 2915 |  |  |  | 2385 | 0.40537 | 10 | Each (1000 ft pipe) | [45 empty] | 0.0953 | 0.3071 | 0.7835 | LogNormal | 0.3071 | 0.80357 | 3 | 0.33781 |  |  |  | 0.27639 | 0.80357 | 10 | Each (1000 ft pipe) | 1.5882 | 2.8059 | 4.6059 | LogNormal | 2.8059 | 0.47626 | 3 | 3.0865 |  |  |  | 2.5253 | 0.47626 | 10 | Each (1000 ft pipe) | [45 empty] | 1
| D2021.014b |  | D2021.014b | Cold or Hot Potable - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC D, E, or F (OSHPD or sim), BRACING FRAGILITY | 180 | 380 | 830 | LogNormal | 382.9373 | 0.60297 | 3 | 418 |  |  |  | 342 | 0.60297 | 10 | Each (1000 ft pipe) | [60 empty] | 0.1906 | 0.4024 | 0.8788 | LogNormal | 0.4024 | 0.65274 | 3 | 0.44264 |  |  |  | 0.36216 | 0.65274 | 10 | Each (1000 ft pipe) | [60 empty] | 1
| D2021.021a |  | D2021.021a | Cold or Hot Potable Water Piping (dia > 2.5 inches), SDC A or B, PIPING FRAGILITY | 150 | 350 | 800 | LogNormal | 348.485 | 0.64877 | 5 | 700 |  |  |  | 210 | 0.64877 | 10 | Each (1000 ft pipe) | 1800 | 3350 | 5350 | LogNormal | 3212.973 | 0.40381 | 5 | 6700 |  |  |  | 2010 | 0.40381 | 10 | Each (1000 ft pipe) | [45 empty] | 0.1588 | 0.3706 | 0.8471 | LogNormal | 0.3706 | 0.69527 | 5 | 0.74119 |  |  |  | 0.22236 | 0.69527 | 10 | Each (1000 ft pipe) | 1.9059 | 3.5471 | 5.6647 | LogNormal | 3.5471 | 0.47493 | 5 | 7.0942 |  |  |  | 2.1283 | 0.47493 | 10 | Each (1000 ft pipe) | [45 empty] | 1
| D2021.022a |  | D2021.022a | Cold or Hot Potable Water Piping (dia > 2.5 inches), SDC C, PIPING FRAGILITY | 150 | 350 | 800 | LogNormal | 348.485 | 0.64877 | 5 | 700 |  |  |  | 210 | 0.64877 | 10 | Each (1000 ft pipe) | 1800 | 3350 | 5350 | LogNormal | 3212.973 | 0.40381 | 5 | 6700 |  |  |  | 2010 | 0.40381 | 10 | Each (1000 ft pipe) | [45 empty] | 0.1588 | 0.3706 | 0.8471 | LogNormal | 0.3706 | 0.69527 | 5 | 0.74119 |  |  |  | 0.22236 | 0.69527 | 10 | Each (1000 ft pipe) | 1.9059 | 3.5471 | 5.6647 | LogNormal | 3.5471 | 0.47493 | 5 | 7.0942 |  |  |  | 2.1283 | 0.47493 | 10 | Each (1000 ft pipe) | [45 empty] | 1
| D2021.023a |  | D2021.023a | Cold or Hot Potable Water Piping (dia > 2.5 inches), SDC D,E,F, PIPING FRAGILITY | 150 | 350 | 800 | LogNormal | 348.485 | 0.64877 | 5 | 700 |  |  |  | 210 | 0.64877 | 10 | Each (1000 ft pipe) | 1800 | 3350 | 5350 | LogNormal | 3212.973 | 0.40381 | 5 | 6700 |  |  |  | 2010 | 0.40381 | 10 | Each (1000 ft pipe) | [45 empty] | 0.1588 | 0.3706 | 0.8471 | LogNormal | 0.3706 | 0.69527 | 5 | 0.74119 |  |  |  | 0.22236 | 0.69527 | 10 | Each (1000 ft pipe) | 1.9059 | 3.5471 | 5.6647 | LogNormal | 3.5471 | 0.47493 | 5 | 7.0942 |  |  |  | 2.1283 | 0.47493 | 10 | Each (1000 ft pipe) | [45 empty] | 1
| D2021.023b |  | D2021.023b | Cold or Hot Potable Water Piping (dia > 2.5 inches), SDC D,E,F, BRACING FRAGILITY | 150 | 350 | 800 | LogNormal | 348.485 | 0.64877 | 5 | 700 |  |  |  | 210 | 0.64877 | 10 | Each (1000 ft pipe) | 150 | 350 | 800 | LogNormal | 348.485 | 0.64877 | 5 | 700 |  |  |  | 210 | 0.64877 | 10 | Each (1000 ft pipe) | [45 empty] | 0.1588 | 0.3706 | 0.8471 | LogNormal | 0.3706 | 0.69527 | 5 | 0.74119 |  |  |  | 0.22236 | 0.69527 | 10 | Each (1000 ft pipe) | 0.1588 | 0.3706 | 0.8471 | LogNormal | 0.3706 | 0.69527 | 5 | 0.74119 |  |  |  | 0.22236 | 0.69527 | 10 | Each (1000 ft pipe) | [45 empty] | 1
| D2021.024a |  | D2021.024a | Cold or Hot Potable Water Piping (dia > 2.5 inches), SDC D,E,F (OSPHD or sim), PIPING FRAGILITY | 150 | 350 | 800 | LogNormal | 348.485 | 0.64877 | 5 | 700 |  |  |  | 210 | 0.64877 | 10 | Each (1000 ft pipe) | 1800 | 3350 | 5350 | LogNormal | 3212.973 | 0.40381 | 5 | 6700 |  |  |  | 2010 | 0.40381 | 10 | Each (1000 ft pipe) | [45 empty] | 0.1588 | 0.3706 | 0.8471 | LogNormal | 0.3706 | 0.69527 | 5 | 0.74119 |  |  |  | 0.22236 | 0.69527 | 10 | Each (1000 ft pipe) | 1.9059 | 3.5471 | 5.6647 | LogNormal | 3.5471 | 0.47493 | 5 | 7.0942 |  |  |  | 2.1283 | 0.47493 | 10 | Each (1000 ft pipe) | [45 empty] | 1
| D2021.024b |  | D2021.024b | Cold or Hot Potable Water Piping (dia > 2.5 inches), SDC D,E,F (OSPHD or sim), BRACING FRAGILITY | 150 | 350 | 800 | LogNormal | 348.485 | 0.64877 | 5 | 700 |  |  |  | 210 | 0.64877 | 10 | Each (1000 ft pipe) | 150 | 350 | 800 | LogNormal | 348.485 | 0.64877 | 5 | 700 |  |  |  | 210 | 0.64877 | 10 | Each (1000 ft pipe) | [45 empty] | 0.1588 | 0.3706 | 0.8471 | LogNormal | 0.3706 | 0.69527 | 5 | 0.74119 |  |  |  | 0.22236 | 0.69527 | 10 | Each (1000 ft pipe) | 0.1588 | 0.3706 | 0.8471 | LogNormal | 0.3706 | 0.69527 | 5 | 0.74119 |  |  |  | 0.22236 | 0.69527 | 10 | Each (1000 ft pipe) | [45 empty] | 1
| D2022.011a |  | D2022.011a | Heating hot Water Piping - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC A or B, PIPING FRAGILITY | 90 | 290 | 740 | LogNormal | 278.8756 | 0.76369 | 1 | 319 |  |  |  | 261 | 0.76369 | 4 | Each (1000 ft pipe) | 1500 | 2650 | 4350 | LogNormal | 2596.8646 | 0.40537 | 1 | 2915 |  |  |  | 2385 | 0.40537 | 4 | Each (1000 ft pipe) | [45 empty] | 0.0953 | 0.3071 | 0.7835 | LogNormal | 0.3071 | 0.80357 | 1 | 0.33781 |  |  |  | 0.27639 | 0.80357 | 4 | Each (1000 ft pipe) | 0.1588 | 0.2806 | 0.4606 | LogNormal | 0.2806 | 0.47626 | 1 | 0.56119 |  |  |  | 0.1403 | 0.47626 | 4 | Each (1000 ft pipe) | [45 empty] | 1
| D2022.011b |  | D2022.011b | Heating hot Water Piping - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC A or B, BRACING FRAGILITY | 180 | 380 | 830 | LogNormal | 382.9373 | 0.60297 | 1 | 418 |  |  |  | 342 | 0.60297 | 4 | Each (1000 ft pipe) | 3600 | 3800 | 4250 | LogNormal | 3873.9954 | 0.066014 | 1 | 4180 |  |  |  | 3420 | 0.066014 | 4 | Each (1000 ft pipe) | [45 empty] | 0.1906 | 0.4024 | 0.8788 | LogNormal | 0.4024 | 0.65274 | 1 | 0.44264 |  |  |  | 0.36216 | 0.65274 | 4 | Each (1000 ft pipe) | 0.3812 | 0.4024 | 0.45 | LogNormal | 0.4024 | 0.25857 | 1 | 0.80475 |  |  |  | 0.2012 | 0.25857 | 4 | Each (1000 ft pipe) | [45 empty] | 1
| D2022.012a |  | D2022.012a | Heating hot Water Piping - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC C, PIPING FRAGILITY | 90 | 290 | 740 | LogNormal | 278.8756 | 0.76369 | 1 | 319 |  |  |  | 261 | 0.76369 | 4 | Each (1000 ft pipe) | 1500 | 2650 | 4350 | LogNormal | 2596.8646 | 0.40537 | 1 | 2915 |  |  |  | 2385 | 0.40537 | 4 | Each (1000 ft pipe) | [45 empty] | 0.0953 | 0.3071 | 0.7835 | LogNormal | 0.3071 | 0.80357 | 1 | 0.33781 |  |  |  | 0.27639 | 0.80357 | 4 | Each (1000 ft pipe) | 0.1588 | 0.2806 | 0.4606 | LogNormal | 0.2806 | 0.47626 | 1 | 0.56119 |  |  |  | 0.1403 | 0.47626 | 4 | Each (1000 ft pipe) | [45 empty] | 1
| D2022.012b |  | D2022.012b | Heating hot Water Piping - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC C, BRACING FRAGILITY | 180 | 380 | 830 | LogNormal | 382.9373 | 0.60297 | 1 | 418 |  |  |  | 342 | 0.60297 | 4 | Each (1000 ft pipe) | 3600 | 3800 | 4250 | LogNormal | 3873.9954 | 0.066014 | 1 | 4180 |  |  |  | 3420 | 0.066014 | 4 | Each (1000 ft pipe) | [45 empty] | 0.1906 | 0.4024 | 0.8788 | LogNormal | 0.4024 | 0.65274 | 1 | 0.44264 |  |  |  | 0.36216 | 0.65274 | 4 | Each (1000 ft pipe) | 0.3812 | 0.4024 | 0.45 | LogNormal | 0.4024 | 0.25857 | 1 | 0.80475 |  |  |  | 0.2012 | 0.25857 | 4 | Each (1000 ft pipe) | [45 empty] | 1
| D2022.013a |  | D2022.013a | Heating hot Water Piping - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC D, E, or F, PIPING FRAGILITY | 90 | 290 | 740 | LogNormal | 278.8756 | 0.76369 | 3 | 319 |  |  |  | 261 | 0.76369 | 10 | Each (1000 ft pipe) | 1500 | 2650 | 4350 | LogNormal | 2596.8646 | 0.40537 | 3 | 2915 |  |  |  | 2385 | 0.40537 | 10 | Each (1000 ft pipe) | [45 empty] | 0.0953 | 0.3071 | 0.7835 | LogNormal | 0.3071 | 0.80357 | 3 | 0.33781 |  |  |  | 0.27639 | 0.80357 | 10 | Each (1000 ft pipe) | 1.5882 | 2.8059 | 4.6059 | LogNormal | 2.8059 | 0.47626 | 3 | 3.0865 |  |  |  | 2.5253 | 0.47626 | 10 | Each (1000 ft pipe) | [45 empty] | 1
| D2022.013b |  | D2022.013b | Heating hot Water Piping - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC D, E, or F, BRACING FRAGILITY | 180 | 380 | 830 | LogNormal | 382.9373 | 0.60297 | 3 | 418 |  |  |  | 342 | 0.60297 | 10 | Each (1000 ft pipe) | [60 empty] | 0.1906 | 0.4024 | 0.8788 | LogNormal | 0.4024 | 0.65274 | 3 | 0.44264 |  |  |  | 0.36216 | 0.65274 | 10 | Each (1000 ft pipe) | [60 empty] | 1
| D2022.014a |  | D2022.014a | Heating hot Water Piping - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC D, E, or F (OSHPD or sim), PIPING FRAGILITY | 90 | 290 | 740 | LogNormal | 278.8756 | 0.76369 | 3 | 319 |  |  |  | 261 | 0.76369 | 10 | Each (1000 ft pipe) | 1500 | 2650 | 4350 | LogNormal | 2596.8646 | 0.40537 | 3 | 2915 |  |  |  | 2385 | 0.40537 | 10 | Each (1000 ft pipe) | [45 empty] | 0.0953 | 0.3071 | 0.7835 | LogNormal | 0.3071 | 0.80357 | 3 | 0.33781 |  |  |  | 0.27639 | 0.80357 | 10 | Each (1000 ft pipe) | 1.5882 | 2.8059 | 4.6059 | LogNormal | 2.8059 | 0.47626 | 3 | 3.0865 |  |  |  | 2.5253 | 0.47626 | 10 | Each (1000 ft pipe) | [45 empty] | 1
| D2022.014b |  | D2022.014b | Heating hot Water Piping - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC D, E, or F (OSHPD or sim), BRACING FRAGILITY | 180 | 380 | 830 | LogNormal | 382.9373 | 0.60297 | 3 | 418 |  |  |  | 342 | 0.60297 | 10 | Each (1000 ft pipe) | [60 empty] | 0.1906 | 0.4024 | 0.8788 | LogNormal | 0.4024 | 0.65274 | 3 | 0.44264 |  |  |  | 0.36216 | 0.65274 | 10 | Each (1000 ft pipe) | [60 empty] | 1
| D2022.021a |  | D2022.021a | Heating hot Water Piping - Large Diameter Welded Steel - (greater than 2.5 inches in diameter), SDC A or B, PIPING FRAGILITY | 150 | 350 | 800 | LogNormal | 348.485 | 0.64877 | 5 | 700 |  |  |  | 210 | 0.64877 | 10 | Each (1000 ft pipe) | 1800 | 3350 | 5350 | LogNormal | 3212.973 | 0.40381 | 5 | 6700 |  |  |  | 2010 | 0.40381 | 10 | Each (1000 ft pipe) | [45 empty] | 0.1588 | 0.3706 | 0.8471 | LogNormal | 0.3706 | 0.69527 | 5 | 0.74119 |  |  |  | 0.22236 | 0.69527 | 10 | Each (1000 ft pipe) | 1.9059 | 3.5471 | 5.6647 | LogNormal | 3.5471 | 0.47493 | 5 | 7.0942 |  |  |  | 2.1283 | 0.47493 | 10 | Each (1000 ft pipe) | [45 empty] | 1
| D2022.022a |  | D2022.022a | Heating hot Water Piping - Large Diameter Welded Steel - (greater than 2.5 inches in diameter), SDC C, PIPING FRAGILITY | 150 | 350 | 800 | LogNormal | 348.485 | 0.64877 | 5 | 700 |  |  |  | 210 | 0.64877 | 10 | Each (1000 ft pipe) | 1800 | 3350 | 5350 | LogNormal | 3212.973 | 0.40381 | 5 | 6700 |  |  |  | 2010 | 0.40381 | 10 | Each (1000 ft pipe) | [45 empty] | 0.1588 | 0.3706 | 0.8471 | LogNormal | 0.3706 | 0.69527 | 5 | 0.74119 |  |  |  | 0.22236 | 0.69527 | 10 | Each (1000 ft pipe) | 1.9059 | 3.5471 | 5.6647 | LogNormal | 3.5471 | 0.47493 | 5 | 7.0942 |  |  |  | 2.1283 | 0.47493 | 10 | Each (1000 ft pipe) | [45 empty] | 1
| D2022.023a |  | D2022.023a | Heating hot Water Piping - Large Diameter Welded Steel - (greater than 2.5 inches in diameter), SDC D, E, or F, PIPING FRAGILITY | 150 | 350 | 800 | LogNormal | 348.485 | 0.64877 | 5 | 700 |  |  |  | 210 | 0.64877 | 10 | Each (1000 ft pipe) | 1800 | 3350 | 5350 | LogNormal | 3212.973 | 0.40381 | 5 | 6700 |  |  |  | 2010 | 0.40381 | 10 | Each (1000 ft pipe) | [45 empty] | 0.1588 | 0.3706 | 0.8471 | LogNormal | 0.3706 | 0.69527 | 5 | 0.74119 |  |  |  | 0.22236 | 0.69527 | 10 | Each (1000 ft pipe) | 1.9059 | 3.5471 | 5.6647 | LogNormal | 3.5471 | 0.47493 | 5 | 7.0942 |  |  |  | 2.1283 | 0.47493 | 10 | Each (1000 ft pipe) | [45 empty] | 1
| D2022.023b |  | D2022.023b | Heating hot Water Piping - Large Diameter Welded Steel - (greater than 2.5 inches in diameter), SDC D, E, or F, BRACING FRAGILITY | 150 | 350 | 800 | LogNormal | 348.485 | 0.64877 | 5 | 700 |  |  |  | 210 | 0.64877 | 10 | Each (1000 ft pipe) | 150 | 350 | 800 | LogNormal | 348.485 | 0.64877 | 5 | 700 |  |  |  | 210 | 0.64877 | 10 | Each (1000 ft pipe) | [45 empty] | 0.1588 | 0.3706 | 0.8471 | LogNormal | 0.3706 | 0.69527 | 5 | 0.74119 |  |  |  | 0.22236 | 0.69527 | 10 | Each (1000 ft pipe) | 0.1588 | 0.3706 | 0.8471 | LogNormal | 0.3706 | 0.69527 | 5 | 0.74119 |  |  |  | 0.22236 | 0.69527 | 10 | Each (1000 ft pipe) | [45 empty] | 1
| D2022.024a |  | D2022.024a | Heating hot Water Piping - Large Diameter Welded Steel - (greater than 2.5 inches in diameter), SDC D, E, or F (OSHPD or sim), PIPING FRAGILITY | 150 | 350 | 800 | LogNormal | 348.485 | 0.64877 | 5 | 700 |  |  |  | 210 | 0.64877 | 10 | Each (1000 ft pipe) | 1800 | 3350 | 5350 | LogNormal | 3212.973 | 0.40381 | 5 | 6700 |  |  |  | 2010 | 0.40381 | 10 | Each (1000 ft pipe) | [45 empty] | 0.1588 | 0.3706 | 0.8471 | LogNormal | 0.3706 | 0.69527 | 5 | 0.74119 |  |  |  | 0.22236 | 0.69527 | 10 | Each (1000 ft pipe) | 1.9059 | 3.5471 | 5.6647 | LogNormal | 3.5471 | 0.47493 | 5 | 7.0942 |  |  |  | 2.1283 | 0.47493 | 10 | Each (1000 ft pipe) | [45 empty] | 1
| D2022.024b |  | D2022.024b | Heating hot Water Piping - Large Diameter Welded Steel - (greater than 2.5 inches in diameter), SDC D, E, or F (OSHPD or sim), BRACING FRAGILITY | 150 | 350 | 800 | LogNormal | 348.485 | 0.64877 | 5 | 700 |  |  |  | 210 | 0.64877 | 10 | Each (1000 ft pipe) | 150 | 350 | 800 | LogNormal | 348.485 | 0.64877 | 5 | 700 |  |  |  | 210 | 0.64877 | 10 | Each (1000 ft pipe) | [45 empty] | 0.1588 | 0.3706 | 0.8471 | LogNormal | 0.3706 | 0.69527 | 5 | 0.74119 |  |  |  | 0.22236 | 0.69527 | 10 | Each (1000 ft pipe) | 0.1588 | 0.3706 | 0.8471 | LogNormal | 0.3706 | 0.69527 | 5 | 0.74119 |  |  |  | 0.22236 | 0.69527 | 10 | Each (1000 ft pipe) | [45 empty] | 1
| D2031.011b |  | D2031.011b | Sanitary Waste Piping - Cast Iron w/flexible couplings, SDC A,B, BRACING FRAGILITY | 200 | 400 | 850 | LogNormal | 405.744 | 0.57578 | 5 | 800 |  |  |  | 240 | 0.57578 | 10 | Each (1000 ft pipe) | 1800 | 2850 | 4350 | LogNormal | 2819.6028 | 0.34009 | 5 | 5700 |  |  |  | 1710 | 0.34009 | 10 | Each (1000 ft pipe) | [45 empty] | 0.2118 | 0.4235 | 0.9 | LogNormal | 0.4235 | 0.62772 | 5 | 0.84703 |  |  |  | 0.25409 | 0.62772 | 10 | Each (1000 ft pipe) | 1.9059 | 3.0176 | 4.6059 | LogNormal | 3.0176 | 0.42209 | 5 | 6.0352 |  |  |  | 1.8105 | 0.42209 | 10 | Each (1000 ft pipe) | [45 empty] | 1
| D2031.012b |  | D2031.012b | Sanitary Waste Piping - Cast Iron w/flexible couplings, SDC C, BRACING FRAGILITY | 200 | 400 | 850 | LogNormal | 405.744 | 0.57578 | 5 | 800 |  |  |  | 240 | 0.57578 | 10 | Each (1000 ft pipe) | 1800 | 2850 | 4350 | LogNormal | 2819.6028 | 0.34009 | 5 | 5700 |  |  |  | 1710 | 0.34009 | 10 | Each (1000 ft pipe) | [45 empty] | 0.2118 | 0.4235 | 0.9 | LogNormal | 0.4235 | 0.62772 | 5 | 0.84703 |  |  |  | 0.25409 | 0.62772 | 10 | Each (1000 ft pipe) | 1.9059 | 3.0176 | 4.6059 | LogNormal | 3.0176 | 0.42209 | 5 | 6.0352 |  |  |  | 1.8105 | 0.42209 | 10 | Each (1000 ft pipe) | [45 empty] | 1
| D2031.013b |  | D2031.013b | Sanitary Waste Piping - Cast Iron w/flexible couplings, SDC D,E,F, BRACING FRAGILITY | 200 | 400 | 850 | LogNormal | 405.744 | 0.57578 | 5 | 800 |  |  |  | 240 | 0.57578 | 10 | Each (1000 ft pipe) | [60 empty] | 0.2118 | 0.4235 | 0.9 | LogNormal | 0.4235 | 0.62772 | 5 | 0.84703 |  |  |  | 0.25409 | 0.62772 | 10 | Each (1000 ft pipe) | [60 empty] | 1
| D2031.014b |  | D2031.014b | Sanitary Waste Piping - Cast Iron w/flexible couplings, SDC D,E,F (OSHPD or sim), BRACING FRAGILITY | 200 | 400 | 850 | LogNormal | 405.744 | 0.57578 | 5 | 800 |  |  |  | 240 | 0.57578 | 10 | Each (1000 ft pipe) | [60 empty] | 0.2118 | 0.4235 | 0.9 | LogNormal | 0.4235 | 0.62772 | 5 | 0.84703 |  |  |  | 0.25409 | 0.62772 | 10 | Each (1000 ft pipe) | [60 empty] | 1
| D2031.021a |  | D2031.021a | Sanitary Waste Piping - Cast Iron w/bell and spigot couplings, SDC A,B, PIPING FRAGILITY | 1800 | 3350 | 4350 | Normal | 3166.6624 | 0.31418 | 5 | 6700 |  |  |  | 2010 | 0.31418 | 10 | Each (1000 ft pipe) | [60 empty] | 1.9059 | 3.5471 | 4.6059 | Normal | 3.5471 | 0.40151 | 5 | 7.0942 |  |  |  | 2.1283 | 0.40151 | 10 | Each (1000 ft pipe) | [60 empty] | 1
| D2031.021b |  | D2031.021b | Sanitary Waste Piping - Cast Iron w/bell and spigot couplings, SDC A,B, BRACING FRAGILITY | 200 | 400 | 1050 | LogNormal | 423.2063 | 0.70555 | 5 | 800 |  |  |  | 240 | 0.70555 | 10 | Each (1000 ft pipe) | 1800 | 4350 | 4350 | Normal | 3499.9912 | 0.28425 | 5 | 8700 |  |  |  | 2610 | 0.28425 | 10 | Each (1000 ft pipe) | [45 empty] | 0.2118 | 0.4235 | 1.1118 | LogNormal | 0.4235 | 0.74853 | 5 | 0.84703 |  |  |  | 0.25409 | 0.74853 | 10 | Each (1000 ft pipe) | 1.9059 | 4.6059 | 4.6059 | Normal | 4.6059 | 0.37855 | 5 | 9.2118 |  |  |  | 2.7635 | 0.37855 | 10 | Each (1000 ft pipe) | [45 empty] | 1
| D2031.022a |  | D2031.022a | Sanitary Waste Piping - Cast Iron w/bell and spigot couplings, SDC C, PIPING FRAGILITY | 1800 | 3350 | 4350 | Normal | 3166.6624 | 0.31418 | 5 | 6700 |  |  |  | 2010 | 0.31418 | 10 | Each (1000 ft pipe) | [60 empty] | 1.9059 | 3.5471 | 4.6059 | Normal | 3.5471 | 0.40151 | 5 | 7.0942 |  |  |  | 2.1283 | 0.40151 | 10 | Each (1000 ft pipe) | [60 empty] | 1
| D2031.022b |  | D2031.022b | Sanitary Waste Piping - Cast Iron w/bell and spigot couplings, SDC C, BRACING FRAGILITY | 200 | 400 | 1050 | LogNormal | 423.2063 | 0.70555 | 5 | 800 |  |  |  | 240 | 0.70555 | 10 | Each (1000 ft pipe) | 1800 | 4350 | 4350 | Normal | 3499.9912 | 0.28425 | 5 | 8700 |  |  |  | 2610 | 0.28425 | 10 | Each (1000 ft pipe) | [45 empty] | 0.2118 | 0.4235 | 1.1118 | LogNormal | 0.4235 | 0.74853 | 5 | 0.84703 |  |  |  | 0.25409 | 0.74853 | 10 | Each (1000 ft pipe) | 1.9059 | 4.6059 | 4.6059 | Normal | 4.6059 | 0.37855 | 5 | 9.2118 |  |  |  | 2.7635 | 0.37855 | 10 | Each (1000 ft pipe) | [45 empty] | 1
| D2031.023a |  | D2031.023a | Sanitary Waste Piping - Cast Iron w/bell and spigot couplings, SDC D,E,F, PIPING FRAGILITY | 1800 | 3350 | 4350 | Normal | 3166.6624 | 0.31418 | 5 | 6700 |  |  |  | 2010 | 0.31418 | 10 | Each (1000 ft pipe) | [60 empty] | 1.9059 | 3.5471 | 4.6059 | Normal | 3.5471 | 0.40151 | 5 | 7.0942 |  |  |  | 2.1283 | 0.40151 | 10 | Each (1000 ft pipe) | [60 empty] | 1
| D2031.023b |  | D2031.023b | Sanitary Waste Piping - Cast Iron w/bell and spigot couplings, SDC D,E,F, BRACING FRAGILITY | 200 | 400 | 1050 | LogNormal | 423.2063 | 0.70555 | 5 | 800 |  |  |  | 240 | 0.70555 | 10 | Each (1000 ft pipe) | [60 empty] | 0.2118 | 0.4235 | 1.1118 | LogNormal | 0.4235 | 0.74853 | 5 | 0.84703 |  |  |  | 0.25409 | 0.74853 | 10 | Each (1000 ft pipe) | [60 empty] | 1
| D2031.024a |  | D2031.024a | Sanitary Waste Piping - Cast Iron w/bell and spigot couplings, SDC D,E,F (OSHPD or sim), PIPING FRAGILITY | 1800 | 3350 | 4350 | Normal | 3166.6624 | 0.31418 | 5 | 6700 |  |  |  | 2010 | 0.31418 | 10 | Each (1000 ft pipe) | [60 empty] | 1.9059 | 3.5471 | 4.6059 | Normal | 3.5471 | 0.40151 | 5 | 7.0942 |  |  |  | 2.1283 | 0.40151 | 10 | Each (1000 ft pipe) | [60 empty] | 1
| D2031.024b |  | D2031.024b | Sanitary Waste Piping - Cast Iron w/bell and spigot couplings, SDC D,E,F (OSHPD or sim), BRACING FRAGILITY | 200 | 400 | 1050 | LogNormal | 423.2063 | 0.70555 | 5 | 800 |  |  |  | 240 | 0.70555 | 10 | Each (1000 ft pipe) | [60 empty] | 0.2118 | 0.4235 | 1.1118 | LogNormal | 0.4235 | 0.74853 | 5 | 0.84703 |  |  |  | 0.25409 | 0.74853 | 10 | Each (1000 ft pipe) | [60 empty] | 1
| D2051.011a |  | D2051.011a | Chilled Water Piping - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC A or B, PIPING FRAGILITY | 90 | 290 | 740 | LogNormal | 278.8756 | 0.76369 | 5 | 319 |  |  |  | 261 | 0.76369 | 10 | Each (1000 ft pipe) | 1500 | 2650 | 4350 | LogNormal | 2596.8646 | 0.40537 | 5 | 2915 |  |  |  | 2385 | 0.40537 | 10 | Each (1000 ft pipe) | [45 empty] | 0.0953 | 0.3071 | 0.7835 | LogNormal | 0.3071 | 0.80357 | 5 | 0.33781 |  |  |  | 0.27639 | 0.80357 | 10 | Each (1000 ft pipe) | 0.1588 | 0.2806 | 0.4606 | LogNormal | 0.2806 | 0.47626 | 5 | 0.56119 |  |  |  | 0.1403 | 0.47626 | 10 | Each (1000 ft pipe) | [45 empty] | 1
| D2051.011b |  | D2051.011b | Chilled Water Piping - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC A or B, BRACING FRAGILITY | 180 | 380 | 830 | LogNormal | 382.9373 | 0.60297 | 5 | 418 |  |  |  | 342 | 0.60297 | 10 | Each (1000 ft pipe) | 3600 | 3800 | 4250 | LogNormal | 3873.9954 | 0.066014 | 5 | 4180 |  |  |  | 3420 | 0.066014 | 10 | Each (1000 ft pipe) | [45 empty] | 0.1906 | 0.4024 | 0.8788 | LogNormal | 0.4024 | 0.65274 | 5 | 0.44264 |  |  |  | 0.36216 | 0.65274 | 10 | Each (1000 ft pipe) | 0.3812 | 0.4024 | 0.45 | LogNormal | 0.4024 | 0.25857 | 5 | 0.80475 |  |  |  | 0.2012 | 0.25857 | 10 | Each (1000 ft pipe) | [45 empty] | 1
| D2051.012a |  | D2051.012a | Chilled Water Piping - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC C, PIPING FRAGILITY | 90 | 290 | 740 | LogNormal | 278.8756 | 0.76369 | 5 | 319 |  |  |  | 261 | 0.76369 | 10 | Each (1000 ft pipe) | 1500 | 2650 | 4350 | LogNormal | 2596.8646 | 0.40537 | 5 | 2915 |  |  |  | 2385 | 0.40537 | 10 | Each (1000 ft pipe) | [45 empty] | 0.0953 | 0.3071 | 0.7835 | LogNormal | 0.3071 | 0.80357 | 5 | 0.33781 |  |  |  | 0.27639 | 0.80357 | 10 | Each (1000 ft pipe) | 0.1588 | 0.2806 | 0.4606 | LogNormal | 0.2806 | 0.47626 | 5 | 0.56119 |  |  |  | 0.1403 | 0.47626 | 10 | Each (1000 ft pipe) | [45 empty] | 1
| D2051.012b |  | D2051.012b | Chilled Water Piping - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC C, BRACING FRAGILITY | 180 | 380 | 830 | LogNormal | 382.9373 | 0.60297 | 5 | 418 |  |  |  | 342 | 0.60297 | 10 | Each (1000 ft pipe) | 3600 | 3800 | 4250 | LogNormal | 3873.9954 | 0.066014 | 5 | 4180 |  |  |  | 3420 | 0.066014 | 10 | Each (1000 ft pipe) | [45 empty] | 0.1906 | 0.4024 | 0.8788 | LogNormal | 0.4024 | 0.65274 | 5 | 0.44264 |  |  |  | 0.36216 | 0.65274 | 10 | Each (1000 ft pipe) | 0.3812 | 0.4024 | 0.45 | LogNormal | 0.4024 | 0.25857 | 5 | 0.80475 |  |  |  | 0.2012 | 0.25857 | 10 | Each (1000 ft pipe) | [45 empty] | 1
| D2051.013a |  | D2051.013a | Chilled Water Piping - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC D, E, or F, PIPING FRAGILITY | 90 | 290 | 740 | LogNormal | 278.8756 | 0.76369 | 5 | 319 |  |  |  | 261 | 0.76369 | 10 | Each (1000 ft pipe) | 1500 | 2650 | 4350 | LogNormal | 2596.8646 | 0.40537 | 5 | 2915 |  |  |  | 2385 | 0.40537 | 10 | Each (1000 ft pipe) | [45 empty] | 0.0953 | 0.3071 | 0.7835 | LogNormal | 0.3071 | 0.80357 | 5 | 0.33781 |  |  |  | 0.27639 | 0.80357 | 10 | Each (1000 ft pipe) | 1.5882 | 2.8059 | 4.6059 | LogNormal | 2.8059 | 0.47626 | 5 | 3.0865 |  |  |  | 2.5253 | 0.47626 | 10 | Each (1000 ft pipe) | [45 empty] | 1
| D2051.013b |  | D2051.013b | Chilled Water Piping - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC D, E, or F, BRACING FRAGILITY | 180 | 380 | 830 | LogNormal | 382.9373 | 0.60297 | 5 | 418 |  |  |  | 342 | 0.60297 | 10 | Each (1000 ft pipe) | [60 empty] | 0.1906 | 0.4024 | 0.8788 | LogNormal | 0.4024 | 0.65274 | 5 | 0.44264 |  |  |  | 0.36216 | 0.65274 | 10 | Each (1000 ft pipe) | [60 empty] | 1
| D2051.014a |  | D2051.014a | Chilled Water Piping - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC D, E, or F (OSHPD or sim), PIPING FRAGILITY | 90 | 290 | 740 | LogNormal | 278.8756 | 0.76369 | 5 | 319 |  |  |  | 261 | 0.76369 | 10 | Each (1000 ft pipe) | 1500 | 2650 | 4350 | LogNormal | 2596.8646 | 0.40537 | 5 | 2915 |  |  |  | 2385 | 0.40537 | 10 | Each (1000 ft pipe) | [45 empty] | 0.0953 | 0.3071 | 0.7835 | LogNormal | 0.3071 | 0.80357 | 5 | 0.33781 |  |  |  | 0.27639 | 0.80357 | 10 | Each (1000 ft pipe) | 1.5882 | 2.8059 | 4.6059 | LogNormal | 2.8059 | 0.47626 | 5 | 3.0865 |  |  |  | 2.5253 | 0.47626 | 10 | Each (1000 ft pipe) | [45 empty] | 1
| D2051.014b |  | D2051.014b | Chilled Water Piping - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC D, E, or F (OSHPD or sim), BRACING FRAGILITY | 180 | 380 | 830 | LogNormal | 382.9373 | 0.60297 | 5 | 418 |  |  |  | 342 | 0.60297 | 10 | Each (1000 ft pipe) | [60 empty] | 0.1906 | 0.4024 | 0.8788 | LogNormal | 0.4024 | 0.65274 | 5 | 0.44264 |  |  |  | 0.36216 | 0.65274 | 10 | Each (1000 ft pipe) | [60 empty] | 1
| D2051.021a |  | D2051.021a | Chilled Water Piping - Large Diameter Welded Steel - (greater than 2.5 inches in diameter), SDC A or B, PIPING FRAGILITY | 150 | 350 | 800 | LogNormal | 348.485 | 0.64877 | 5 | 700 |  |  |  | 210 | 0.64877 | 10 | Each (1000 ft pipe) | 1800 | 3350 | 5350 | LogNormal | 3212.973 | 0.40381 | 5 | 6700 |  |  |  | 2010 | 0.40381 | 10 | Each (1000 ft pipe) | [45 empty] | 0.1588 | 0.3706 | 0.8471 | LogNormal | 0.3706 | 0.69527 | 5 | 0.74119 |  |  |  | 0.22236 | 0.69527 | 10 | Each (1000 ft pipe) | 1.9059 | 3.5471 | 5.6647 | LogNormal | 3.5471 | 0.47493 | 5 | 7.0942 |  |  |  | 2.1283 | 0.47493 | 10 | Each (1000 ft pipe) | [45 empty] | 1
| D2051.021b |  | D2051.021b | Chilled Water Piping - Large Diameter Welded Steel - (greater than 2.5 inches in diameter), SDC A or B, BRACING FRAGILITY | 150 | 350 | 800 | LogNormal | 348.485 | 0.64877 | 5 | 700 |  |  |  | 210 | 0.64877 | 10 | Each (1000 ft pipe) | [60 empty] | 0.1588 | 0.3706 | 0.8471 | LogNormal | 0.3706 | 0.69527 | 5 | 0.74119 |  |  |  | 0.22236 | 0.69527 | 10 | Each (1000 ft pipe) | [60 empty] | 1
| D2051.022a |  | D2051.022a | Chilled Water Piping - Large Diameter Welded Steel - (greater than 2.5 inches in diameter), SDC C, PIPING FRAGILITY | 150 | 350 | 800 | LogNormal | 348.485 | 0.64877 | 5 | 700 |  |  |  | 210 | 0.64877 | 10 | Each (1000 ft pipe) | 1800 | 3350 | 5350 | LogNormal | 3212.973 | 0.40381 | 5 | 6700 |  |  |  | 2010 | 0.40381 | 10 | Each (1000 ft pipe) | [45 empty] | 0.1588 | 0.3706 | 0.8471 | LogNormal | 0.3706 | 0.69527 | 5 | 0.74119 |  |  |  | 0.22236 | 0.69527 | 10 | Each (1000 ft pipe) | 1.9059 | 3.5471 | 5.6647 | LogNormal | 3.5471 | 0.47493 | 5 | 7.0942 |  |  |  | 2.1283 | 0.47493 | 10 | Each (1000 ft pipe) | [45 empty] | 1
| D2051.023a |  | D2051.023a | Chilled Water Piping - Large Diameter Welded Steel - (greater than 2.5 inches in diameter), SDC D, E, or F, PIPING FRAGILITY | 150 | 350 | 800 | LogNormal | 348.485 | 0.64877 | 5 | 700 |  |  |  | 210 | 0.64877 | 10 | Each (1000 ft pipe) | 1800 | 3350 | 5350 | LogNormal | 3212.973 | 0.40381 | 5 | 6700 |  |  |  | 2010 | 0.40381 | 10 | Each (1000 ft pipe) | [45 empty] | 0.1588 | 0.3706 | 0.8471 | LogNormal | 0.3706 | 0.69527 | 5 | 0.74119 |  |  |  | 0.22236 | 0.69527 | 10 | Each (1000 ft pipe) | 1.9059 | 3.5471 | 5.6647 | LogNormal | 3.5471 | 0.47493 | 5 | 7.0942 |  |  |  | 2.1283 | 0.47493 | 10 | Each (1000 ft pipe) | [45 empty] | 1
| D2051.023b |  | D2051.023b | Chilled Water Piping - Large Diameter Welded Steel - (greater than 2.5 inches in diameter), SDC D, E, or F, BRACING FRAGILITY | 150 | 350 | 800 | LogNormal | 348.485 | 0.64877 | 5 | 700 |  |  |  | 210 | 0.64877 | 10 | Each (1000 ft pipe) | 150 | 350 | 800 | LogNormal | 348.485 | 0.64877 | 5 | 700 |  |  |  | 210 | 0.64877 | 10 | Each (1000 ft pipe) | [45 empty] | 0.1588 | 0.3706 | 0.8471 | LogNormal | 0.3706 | 0.69527 | 5 | 0.74119 |  |  |  | 0.22236 | 0.69527 | 10 | Each (1000 ft pipe) | 0.1588 | 0.3706 | 0.8471 | LogNormal | 0.3706 | 0.69527 | 5 | 0.74119 |  |  |  | 0.22236 | 0.69527 | 10 | Each (1000 ft pipe) | [45 empty] | 1
| D2051.024a |  | D2051.024a | Chilled Water Piping - Large Diameter Welded Steel - (greater than 2.5 inches in diameter), SDC D, E, or F (OSHPD or sim), PIPING FRAGILITY | 150 | 350 | 800 | LogNormal | 348.485 | 0.64877 | 5 | 700 |  |  |  | 210 | 0.64877 | 10 | Each (1000 ft pipe) | 1800 | 3350 | 5350 | LogNormal | 3212.973 | 0.40381 | 5 | 6700 |  |  |  | 2010 | 0.40381 | 10 | Each (1000 ft pipe) | [45 empty] | 0.1588 | 0.3706 | 0.8471 | LogNormal | 0.3706 | 0.69527 | 5 | 0.74119 |  |  |  | 0.22236 | 0.69527 | 10 | Each (1000 ft pipe) | 1.9059 | 3.5471 | 5.6647 | LogNormal | 3.5471 | 0.47493 | 5 | 7.0942 |  |  |  | 2.1283 | 0.47493 | 10 | Each (1000 ft pipe) | [45 empty] | 1
| D2051.024b |  | D2051.024b | Chilled Water Piping - Large Diameter Welded Steel - (greater than 2.5 inches in diameter), SDC D, E, or F (OSHPD or sim), BRACING FRAGILITY | 150 | 350 | 800 | LogNormal | 348.485 | 0.64877 | 5 | 700 |  |  |  | 210 | 0.64877 | 10 | Each (1000 ft pipe) | 150 | 350 | 800 | LogNormal | 348.485 | 0.64877 | 5 | 700 |  |  |  | 210 | 0.64877 | 10 | Each (1000 ft pipe) | [45 empty] | 0.1588 | 0.3706 | 0.8471 | LogNormal | 0.3706 | 0.69527 | 5 | 0.74119 |  |  |  | 0.22236 | 0.69527 | 10 | Each (1000 ft pipe) | 0.1588 | 0.3706 | 0.8471 | LogNormal | 0.3706 | 0.69527 | 5 | 0.74119 |  |  |  | 0.22236 | 0.69527 | 10 | Each (1000 ft pipe) | [45 empty] | 1
| D2061.011a |  | D2061.011a | Steam Piping - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC A or B, PIPING FRAGILITY | 90 | 290 | 740 | LogNormal | 278.8756 | 0.76369 | 5 | 319 |  |  |  | 261 | 0.76369 | 10 | Each (1000 ft pipe) | 1500 | 2650 | 4350 | LogNormal | 2596.8646 | 0.40537 | 5 | 2915 |  |  |  | 2385 | 0.40537 | 10 | Each (1000 ft pipe) | [45 empty] | 0.0953 | 0.3071 | 0.7835 | LogNormal | 0.3071 | 0.80357 | 5 | 0.33781 |  |  |  | 0.27639 | 0.80357 | 10 | Each (1000 ft pipe) | 0.1588 | 0.2806 | 0.4606 | LogNormal | 0.2806 | 0.47626 | 5 | 0.56119 |  |  |  | 0.1403 | 0.47626 | 10 | Each (1000 ft pipe) | [45 empty] | 1
| D2061.011b |  | D2061.011b | Steam Piping - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC A or B, BRACING FRAGILITY | 180 | 380 | 830 | LogNormal | 382.9373 | 0.60297 | 5 | 418 |  |  |  | 342 | 0.60297 | 10 | Each (1000 ft pipe) | 3600 | 3800 | 4250 | LogNormal | 3873.9954 | 0.066014 | 5 | 4180 |  |  |  | 3420 | 0.066014 | 10 | Each (1000 ft pipe) | [45 empty] | 0.1906 | 0.4024 | 0.8788 | LogNormal | 0.4024 | 0.65274 | 5 | 0.44264 |  |  |  | 0.36216 | 0.65274 | 10 | Each (1000 ft pipe) | 0.3812 | 0.4024 | 0.45 | LogNormal | 0.4024 | 0.25857 | 5 | 0.80475 |  |  |  | 0.2012 | 0.25857 | 10 | Each (1000 ft pipe) | [45 empty] | 1
| D2061.012a |  | D2061.012a | Steam Piping - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC C, PIPING FRAGILITY | 90 | 290 | 740 | LogNormal | 278.8756 | 0.76369 | 5 | 319 |  |  |  | 261 | 0.76369 | 10 | Each (1000 ft pipe) | 1500 | 2650 | 4350 | LogNormal | 2596.8646 | 0.40537 | 5 | 2915 |  |  |  | 2385 | 0.40537 | 10 | Each (1000 ft pipe) | [45 empty] | 0.0953 | 0.3071 | 0.7835 | LogNormal | 0.3071 | 0.80357 | 5 | 0.33781 |  |  |  | 0.27639 | 0.80357 | 10 | Each (1000 ft pipe) | 0.1588 | 0.2806 | 0.4606 | LogNormal | 0.2806 | 0.47626 | 5 | 0.56119 |  |  |  | 0.1403 | 0.47626 | 10 | Each (1000 ft pipe) | [45 empty] | 1
| D2061.012b |  | D2061.012b | Steam Piping - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC C, BRACING FRAGILITY | 180 | 380 | 830 | LogNormal | 382.9373 | 0.60297 | 5 | 418 |  |  |  | 342 | 0.60297 | 10 | Each (1000 ft pipe) | 3600 | 3800 | 4250 | LogNormal | 3873.9954 | 0.066014 | 5 | 4180 |  |  |  | 3420 | 0.066014 | 10 | Each (1000 ft pipe) | [45 empty] | 0.1906 | 0.4024 | 0.8788 | LogNormal | 0.4024 | 0.65274 | 5 | 0.44264 |  |  |  | 0.36216 | 0.65274 | 10 | Each (1000 ft pipe) | 0.3812 | 0.4024 | 0.45 | LogNormal | 0.4024 | 0.25857 | 5 | 0.80475 |  |  |  | 0.2012 | 0.25857 | 10 | Each (1000 ft pipe) | [45 empty] | 1
| D2061.013a |  | D2061.013a | Steam Piping - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC D, E, or F, PIPING FRAGILITY | 90 | 290 | 740 | LogNormal | 278.8756 | 0.76369 | 5 | 319 |  |  |  | 261 | 0.76369 | 10 | Each (1000 ft pipe) | 1500 | 2650 | 4350 | LogNormal | 2596.8646 | 0.40537 | 5 | 2915 |  |  |  | 2385 | 0.40537 | 10 | Each (1000 ft pipe) | [45 empty] | 0.0953 | 0.3071 | 0.7835 | LogNormal | 0.3071 | 0.80357 | 5 | 0.33781 |  |  |  | 0.27639 | 0.80357 | 10 | Each (1000 ft pipe) | 1.5882 | 2.8059 | 4.6059 | LogNormal | 2.8059 | 0.47626 | 5 | 3.0865 |  |  |  | 2.5253 | 0.47626 | 10 | Each (1000 ft pipe) | [45 empty] | 1
| D2061.013b |  | D2061.013b | Steam Piping - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC D, E, or F, BRACING FRAGILITY | 180 | 380 | 830 | LogNormal | 382.9373 | 0.60297 | 5 | 418 |  |  |  | 342 | 0.60297 | 10 | Each (1000 ft pipe) | [60 empty] | 0.1906 | 0.4024 | 0.8788 | LogNormal | 0.4024 | 0.65274 | 5 | 0.44264 |  |  |  | 0.36216 | 0.65274 | 10 | Each (1000 ft pipe) | [60 empty] | 1
| D2061.014a |  | D2061.014a | Steam Piping - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC D, E, or F (OSHPD or sim), PIPING FRAGILITY | 90 | 290 | 740 | LogNormal | 278.8756 | 0.76369 | 5 | 319 |  |  |  | 261 | 0.76369 | 10 | Each (1000 ft pipe) | 1500 | 2650 | 4350 | LogNormal | 2596.8646 | 0.40537 | 5 | 2915 |  |  |  | 2385 | 0.40537 | 10 | Each (1000 ft pipe) | [45 empty] | 0.0953 | 0.3071 | 0.7835 | LogNormal | 0.3071 | 0.80357 | 5 | 0.33781 |  |  |  | 0.27639 | 0.80357 | 10 | Each (1000 ft pipe) | 1.5882 | 2.8059 | 4.6059 | LogNormal | 2.8059 | 0.47626 | 5 | 3.0865 |  |  |  | 2.5253 | 0.47626 | 10 | Each (1000 ft pipe) | [45 empty] | 1
| D2061.014b |  | D2061.014b | Steam Piping - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC D, E, or F (OSHPD or sim), BRACING FRAGILITY | 180 | 380 | 830 | LogNormal | 382.9373 | 0.60297 | 5 | 418 |  |  |  | 342 | 0.60297 | 10 | Each (1000 ft pipe) | [60 empty] | 0.1906 | 0.4024 | 0.8788 | LogNormal | 0.4024 | 0.65274 | 5 | 0.44264 |  |  |  | 0.36216 | 0.65274 | 10 | Each (1000 ft pipe) | [60 empty] | 1
| D2061.021a |  | D2061.021a | Steam Piping - Large Diameter Welded Steel - (greater than 2.5 inches in diameter), SDC A or B, PIPING FRAGILITY | 150 | 350 | 800 | LogNormal | 348.485 | 0.64877 | 5 | 700 |  |  |  | 210 | 0.64877 | 10 | Each (1000 ft pipe) | 1800 | 3350 | 5350 | LogNormal | 3212.973 | 0.40381 | 5 | 6700 |  |  |  | 2010 | 0.40381 | 10 | Each (1000 ft pipe) | [45 empty] | 0.1588 | 0.3706 | 0.8471 | LogNormal | 0.3706 | 0.69527 | 5 | 0.74119 |  |  |  | 0.22236 | 0.69527 | 10 | Each (1000 ft pipe) | 1.9059 | 3.5471 | 5.6647 | LogNormal | 3.5471 | 0.47493 | 5 | 7.0942 |  |  |  | 2.1283 | 0.47493 | 10 | Each (1000 ft pipe) | [45 empty] | 1
| D2061.022a |  | D2061.022a | Steam Piping - Large Diameter Welded Steel - (greater than 2.5 inches in diameter), SDC C, PIPING FRAGILITY | 150 | 350 | 800 | LogNormal | 348.485 | 0.64877 | 5 | 700 |  |  |  | 210 | 0.64877 | 10 | Each (1000 ft pipe) | 1800 | 3350 | 5350 | LogNormal | 3212.973 | 0.40381 | 5 | 6700 |  |  |  | 2010 | 0.40381 | 10 | Each (1000 ft pipe) | [45 empty] | 0.1588 | 0.3706 | 0.8471 | LogNormal | 0.3706 | 0.69527 | 5 | 0.74119 |  |  |  | 0.22236 | 0.69527 | 10 | Each (1000 ft pipe) | 1.9059 | 3.5471 | 5.6647 | LogNormal | 3.5471 | 0.47493 | 5 | 7.0942 |  |  |  | 2.1283 | 0.47493 | 10 | Each (1000 ft pipe) | [45 empty] | 1
0
0 |  | 0
0 |  | 0
0 |  | 0
0 |  | 0
0 |  | 0
0 |  | 0
0 |  | 0
0 |  | 0
0 |  | 0
0 |  | 0
0 |  | 0
0 |  | 0
0 |  | 0
0 |  | 0
0 |  | 0
0 |  | 0
0 |  | 0
0 |  | 0
0 |  | 0
0 |  | 0
0 |  | 0
0 |  | 0
0 |  | 0
0 |  | 0
0 |  | 0
0 |  | 0
0 |  | 0
0 |  | 0
0 |  | 0
0 |  | 0
0 |  | 0
0 |  | 0
0 |  | 0
0 |  | 0
0 |  | 0
0 |  | 0
0 |  | 0
0 |  | 0
0 |  | 0
0 |  | 0
0 |  | 0

## Env Summary
This sheet provides the environmental consequence data for use by PACT.
2019-01-27
NISTIR | NISTIR Classification | Component Name | DS1 Embodied Carbon (kg CO2eq) | DS1 Best Fit | DS1 CV or Beta | DS2 Embodied Carbon (kg CO2eq) | DS2 Best Fit | DS2 CV or Beta | DS3 Embodied Carbon (kg CO2eq) | DS3 Best Fit | DS3 CV or Beta | DS4 Embodied Carbon (kg CO2eq) | DS4 Best Fit | DS4 CV or Beta | DS5 Embodied Carbon (kg CO2eq) | DS5 Best Fit | DS5 CV or Beta | DS1 Embodied Energy (MJ) | DS1 Best Fit | DS1 CV or Beta | DS2 Embodied Energy (MJ) | DS2 Best Fit | DS2 CV or Beta | DS3 Embodied Energy (MJ) | DS3 Best Fit | DS3 CV or Beta | DS4 Embodied Energy (MJ) | DS4 Best Fit | DS4 CV or Beta | DS5 Embodied Energy (MJ) | DS5 Best Fit | DS5 CV or Beta
B1031.001 | B1031.001 | Bolted shear tab gravity connections | 0 | LogNormal | 0.35355 | 1400.98 | Normal | 0.44704 | 1425.07 | Normal | 0.45394 | 1848.35 | Normal | 0.45787 |  |  |  | 0 | LogNormal | 0.35355 | 19347.06 | Normal | 0.44704 | 20086.33 | Normal | 0.45394 | 32234.95 | Normal | 0.45787
B1031.011a | B1031.011a | Steel Column Base Plates, Column W < 150 plf | 0 | LogNormal | 0.35355 | 4188.93 | LogNormal | 0.47762 | 5905.11 | LogNormal | 0.4436 | 10066.43 | LogNormal | 0.42477 |  |  |  | 0 | LogNormal | 0.35355 | 55561.99 | LogNormal | 0.47762 | 104179.01 | LogNormal | 0.4436 | 150387.51 | LogNormal | 0.42477
B1031.011b | B1031.011b | Steel Column Base Plates, Column 150 plf < W < 300 plf | 0 | LogNormal | 0.35355 | 4266.02 | LogNormal | 0.46456 | 192.73 | LogNormal | 0.42345 | 385.45 | LogNormal | 0.39496 |  |  |  | 0 | LogNormal | 0.35355 | 57927.64 | LogNormal | 0.46456 | 5914.11 | LogNormal | 0.42345 | 11828.22 | LogNormal | 0.39496
B1031.011c | B1031.011c | Steel Column Base Plates, Column W > 300 plf | 0 | LogNormal | 0.35355 | 4381.66 | LogNormal | 0.44695 | 481.82 | LogNormal | 0.39857 | 867.27 | LogNormal | 0.36717 |  |  |  | 0 | LogNormal | 0.35355 | 61476.11 | LogNormal | 0.44695 | 14785.28 | LogNormal | 0.39857 | 26613.5 | LogNormal | 0.36717
B1031.021a | B1031.021a | Welded column splices, Column W < 150 plf | 0 | LogNormal | 0.35355 | 1018.18 | Normal | 0.40984 | 1018.18 | LogNormal | 0.39208 | [6 empty] | 0 | LogNormal | 0.35355 | 16516.66 | Normal | 0.40984 | 16516.66 | LogNormal | 0.39208
B1031.021b | B1031.021b | Welded column splices, Column 150 plf < W < 300 plf | 0 | LogNormal | 0.35355 | 77.09 | Normal | 0.39005 | 192.73 | Normal | 0.36703 | [6 empty] | 0 | LogNormal | 0.35355 | 2365.64 | Normal | 0.39005 | 5914.11 | Normal | 0.36703
B1031.021c | B1031.021c | Welded column splices, Column W > 300 plf | 0 | LogNormal | 0.35355 | 192.73 | Normal | 0.36651 | 481.82 | Normal | 0.34384 | [6 empty] | 0 | LogNormal | 0.35355 | 5914.11 | Normal | 0.36651 | 14785.28 | Normal | 0.34384
B1033.001a | B1033.001a | Special Concentric Braced Frame w WF braces, balanced design criteria, Chevron Brace, Brace w < 40 PLF | 6967.05 | Normal | 0.41248 | 8260.75 | Normal | 0.4056 | 8260.75 | Normal | 0.40131 | [6 empty] | 87499.61 | Normal | 0.41248 | 125200.75 | Normal | 0.4056 | 125200.75 | Normal | 0.40131
B1033.001b | B1033.001b | Special Concentric Braced Frame w WF braces, balanced design criteria, Chevron Brace, Brace 41 PLF < w < 99 PLF | 6967.05 | Normal | 0.41248 | 10808.47 | Normal | 0.39053 | 10808.47 | Normal | 0.38546 | [6 empty] | 87499.61 | Normal | 0.41248 | 199446.8 | Normal | 0.39053 | 199446.8 | Normal | 0.38546
B1033.001c | B1033.001c | Special Concentric Braced Frame w WF braces, balanced design criteria, Chevron Brace, Brace w > 100 PLF | 6967.05 | Normal | 0.41248 | 14061.7 | Normal | 0.37904 | 14061.7 | Normal | 0.37399 | [6 empty] | 87499.61 | Normal | 0.41248 | 294252.53 | Normal | 0.37904 | 294252.53 | Normal | 0.37399
B1033.002a | B1033.002a | Special Concentric Braced Frame w WF braces, balanced design criteria, Single Diagonal Brace, Brace w < 40 PLF | 6967.05 | Normal | 0.41444 | 7845.12 | Normal | 0.40619 | 7570.86 | Normal | 0.40526 | [6 empty] | 87499.61 | Normal | 0.41444 | 113088.5 | Normal | 0.40619 | 105095.87 | Normal | 0.40526
B1033.002b | B1033.002b | Special Concentric Braced Frame w WF braces, balanced design criteria, Single Diagonal Brace, 41 PLF < w < 99 PLF | 6967.05 | Normal | 0.41444 | 9290.15 | Normal | 0.39621 | 9290.15 | Normal | 0.3909 | [6 empty] | 87499.61 | Normal | 0.41444 | 155199.63 | Normal | 0.39621 | 155199.63 | Normal | 0.3909
B1033.002c | B1033.002c | Special Concentric Braced Frame w WF braces, balanced design criteria, Single Diagonal Brace, Brace w > 100 PLF | 6967.05 | Normal | 0.41444 | 11484.97 | Normal | 0.38711 | 11484.97 | Normal | 0.38025 | [6 empty] | 87499.61 | Normal | 0.41444 | 219161.44 | Normal | 0.38711 | 219161.44 | Normal | 0.38025
B1033.003a | B1033.003a | Special Concentric Braced Frame w WF braces, balanced design criteria, X Brace, Brace w < 40 PLF | 6967.05 | Normal | 0.40985 | 9271.72 | Normal | 0.39733 | 9271.72 | Normal | 0.39542 | [6 empty] | 87499.61 | Normal | 0.40985 | 154662.63 | Normal | 0.39733 | 154662.63 | Normal | 0.39542
B1033.003b | B1033.003b | Special Concentric Braced Frame w WF braces, balanced design criteria, X Brace, 41 PLF < w < 99 PLF | 6967.05 | Normal | 0.40985 | 12984.57 | Normal | 0.38138 | 12984.57 | Normal | 0.37818 | [6 empty] | 87499.61 | Normal | 0.40985 | 262862.78 | Normal | 0.38138 | 262862.78 | Normal | 0.37818
B1033.003c | B1033.003c | Special Concentric Braced Frame w WF braces, balanced design criteria, X Brace, Brace w > 100 PLF | 6967.05 | Normal | 0.40985 | 17739.9 | Normal | 0.37033 | 17739.9 | Normal | 0.36691 | [6 empty] | 87499.61 | Normal | 0.40985 | 401443.23 | Normal | 0.37033 | 401443.23 | Normal | 0.36691
B1033.011a | B1033.011a | Special Concentric Braced Frame w HSS braces, balanced design criteria, Chevron Brace, Brace w < 40 PLF | 6692.79 | Normal | 0.41442 | 8503.97 | Normal | 0.40238 | 8503.97 | Normal | 0.39836 | [6 empty] | 79506.99 | Normal | 0.41442 | 132288.58 | Normal | 0.40238 | 132288.58 | Normal | 0.39836
B1033.011b | B1033.011b | Special Concentric Braced Frame w HSS braces, balanced design criteria, Chevron Brace, Brace 41 PLF < w < 99 PLF | 6692.79 | Normal | 0.41442 | 11686.81 | Normal | 0.38682 | 11686.81 | Normal | 0.38233 | [6 empty] | 79506.99 | Normal | 0.41442 | 225043.38 | Normal | 0.38682 | 225043.38 | Normal | 0.38233
B1033.011c | B1033.011c | Special Concentric Braced Frame w HSS braces, balanced design criteria, Chevron Brace, Brace w > 100 PLF | 6692.79 | Normal | 0.41442 | 15583.09 | Normal | 0.37478 | 15583.09 | Normal | 0.37092 | [6 empty] | 79506.99 | Normal | 0.41442 | 338589.1 | Normal | 0.37478 | 338589.1 | Normal | 0.37092
B1033.012a | B1033.012a | Special Concentric Braced Frame w HSS braces, balanced design criteria, Single Diagonal Brace, Brace w < 40 PLF | 6692.79 | Normal | 0.41649 | 7922.09 | Normal | 0.40592 | 7739.25 | Normal | 0.40346 | [6 empty] | 79506.99 | Normal | 0.41649 | 115331.43 | Normal | 0.40592 | 110003.01 | Normal | 0.40346
B1033.012b | B1033.012b | Special Concentric Braced Frame w HSS braces, balanced design criteria, Single Diagonal Brace, Brace 41 PLF < w < 99 PLF | 6692.79 | Normal | 0.41649 | 9890.27 | Normal | 0.39479 | 9890.27 | Normal | 0.389 | [6 empty] | 79506.99 | Normal | 0.41649 | 172688.49 | Normal | 0.39479 | 172688.49 | Normal | 0.389
B1033.012c | B1033.012c | Special Concentric Braced Frame w HSS braces, balanced design criteria, Single Diagonal Brace, Brace w > 100 PLF | 6692.79 | Normal | 0.41649 | 12524.21 | Normal | 0.38323 | 12524.21 | Normal | 0.37725 | [6 empty] | 79506.99 | Normal | 0.41649 | 249446.83 | Normal | 0.38323 | 249446.83 | Normal | 0.37725
B1033.013a | B1033.013a | Special Concentric Braced Frame w HSS braces, balanced design criteria, X Brace, Brace w < 40 PLF | 6692.79 | Normal | 0.41166 | 9517.07 | Normal | 0.39613 | 9517.07 | Normal | 0.39337 | [6 empty] | 79506.99 | Normal | 0.41166 | 161812.7 | Normal | 0.39613 | 161812.7 | Normal | 0.39337
B1033.013b | B1033.013b | Special Concentric Braced Frame w HSS braces, balanced design criteria, X Brace, Brace 41 PLF < w < 99 PLF | 6692.79 | Normal | 0.41166 | 14075.11 | Normal | 0.37871 | 14075.11 | Normal | 0.37539 | [6 empty] | 79506.99 | Normal | 0.41166 | 294643.45 | Normal | 0.37871 | 294643.45 | Normal | 0.37539
B1033.013c | B1033.013c | Special Concentric Braced Frame w HSS braces, balanced design criteria, X Brace, Brace w > 100 PLF | 6692.79 | Normal | 0.41166 | 19635.52 | Normal | 0.36747 | 19635.52 | Normal | 0.36456 | [6 empty] | 79506.99 | Normal | 0.41166 | 456685.58 | Normal | 0.36747 | 456685.58 | Normal | 0.36456
B1033.021a | B1033.021a | Special Concentric Braced Frame w HSS braces, tapered gusset plates & design to AISC minimum standard, Chevron Brace, Brace w < 40 PLF | 6857.34 | Normal | 0.41228 | 8668.52 | Normal | 0.40072 | 8668.52 | Normal | 0.39685 | [6 empty] | 84302.56 | Normal | 0.41228 | 137084.15 | Normal | 0.40072 | 137084.15 | Normal | 0.39685
B1033.021b | B1033.021b | Special Concentric Braced Frame w HSS braces, tapered gusset plates & design to AISC minimum standard, Chevron Brace, Brace 41 PLF < w < 99 PLF | 6857.34 | Normal | 0.41228 | 12015.93 | Normal | 0.38595 | 12015.93 | Normal | 0.38163 | [6 empty] | 84302.56 | Normal | 0.41228 | 234634.53 | Normal | 0.38595 | 234634.53 | Normal | 0.38163
B1033.021c | B1033.021c | Special Concentric Braced Frame w HSS braces, tapered gusset plates & design to AISC minimum standard, Chevron Brace, Brace w > 100 PLF | 6857.34 | Normal | 0.41228 | 15912.2 | Normal | 0.3743 | 15912.2 | Normal | 0.37056 | [6 empty] | 84302.56 | Normal | 0.41228 | 348180.25 | Normal | 0.3743 | 348180.25 | Normal | 0.37056
B1033.022a | B1033.022a | Special Concentric Braced Frame w HSS braces, tapered gusset plates & design to AISC minimum standard Single Diagonal Brace, Brace w < 40 PLF | 6857.34 | Normal | 0.41426 | 8086.65 | Normal | 0.40413 | 7848.95 | Normal | 0.40308 | [6 empty] | 84302.56 | Normal | 0.41426 | 120127 | Normal | 0.40413 | 113200.06 | Normal | 0.40308
B1033.022b | B1033.022b | Special Concentric Braced Frame w HSS braces, tapered gusset plates & design to AISC minimum standard, Single Diagonal Brace, Brace 41 PLF < w < 99 PLF | 6857.34 | Normal | 0.41426 | 10109.68 | Normal | 0.3933 | 10109.68 | Normal | 0.38773 | [6 empty] | 84302.56 | Normal | 0.41426 | 179082.59 | Normal | 0.3933 | 179082.59 | Normal | 0.38773
B1033.022c | B1033.022c | Special Concentric Braced Frame w HSS braces, tapered gusset plates & design to AISC minimum standard, Single Diagonal Brace, Brace w > 100 PLF | 6857.34 | Normal | 0.41426 | 12743.62 | Normal | 0.38216 | 12743.62 | Normal | 0.37637 | [6 empty] | 84302.56 | Normal | 0.41426 | 255840.93 | Normal | 0.38216 | 255840.93 | Normal | 0.37637
B1033.023a | B1033.023a | Special Concentric Braced Frame w HSS braces, tapered gusset plates & design to AISC minimum standard, X Brace, Brace w < 40 PLF | 6857.34 | Normal | 0.40963 | 9791.34 | Normal | 0.39501 | 9791.34 | Normal | 0.39236 | [6 empty] | 84302.56 | Normal | 0.40963 | 169805.32 | Normal | 0.39501 | 169805.32 | Normal | 0.39236
B1033.023b | B1033.023b | Special Concentric Braced Frame w HSS braces, tapered gusset plates & design to AISC minimum standard, X Brace, Brace 41 PLF < w < 99 PLF | 6857.34 | Normal | 0.40963 | 14623.64 | Normal | 0.37723 | 14623.64 | Normal | 0.37411 | [6 empty] | 84302.56 | Normal | 0.40963 | 310628.7 | Normal | 0.37723 | 310628.7 | Normal | 0.37411
B1033.023c | B1033.023c | Special Concentric Braced Frame w HSS braces, tapered gusset plates & design to AISC minimum standard, X Brace, Brace w > 100 PLF | 6857.34 | Normal | 0.40963 | 20184.05 | Normal | 0.36663 | 20184.05 | Normal | 0.36384 | [6 empty] | 84302.56 | Normal | 0.40963 | 472670.83 | Normal | 0.36663 | 472670.83 | Normal | 0.36384
B1033.031a | B1033.031a | Special Concentric Braced Frame, design to AISC minimum standards, Chevron Brace, Brace w < 40 PLF | 6857.34 | Normal | 0.41228 | 8668.52 | Normal | 0.40072 | 8668.52 | Normal | 0.39685 | [6 empty] | 84302.56 | Normal | 0.41228 | 137084.15 | Normal | 0.40072 | 137084.15 | Normal | 0.39685
B1033.031b | B1033.031b | Special Concentric Braced Frame, design to AISC minimum standards, Chevron Brace, Brace 41 PLF < w < 99 PLF | 6857.34 | Normal | 0.41228 | 12015.93 | Normal | 0.38595 | 12015.93 | Normal | 0.38163 | [6 empty] | 84302.56 | Normal | 0.41228 | 234634.53 | Normal | 0.38595 | 234634.53 | Normal | 0.38163
B1033.031c | B1033.031c | Special Concentric Braced Frame, design to AISC minimum standards, Chevron Brace, Brace w > 100 PLF | 6857.34 | Normal | 0.41228 | 15912.2 | Normal | 0.3743 | 15912.2 | Normal | 0.37056 | [6 empty] | 84302.56 | Normal | 0.41228 | 348180.25 | Normal | 0.3743 | 348180.25 | Normal | 0.37056
B1033.032a | B1033.032a | Special Concentric Braced Frame, design to AISC minimum standards, Single Diagonal Brace, Brace w < 40 PLF | 6857.34 | Normal | 0.41426 | 8086.65 | Normal | 0.40413 | 7848.95 | Normal | 0.40308 | [6 empty] | 84302.56 | Normal | 0.41426 | 120127 | Normal | 0.40413 | 113200.06 | Normal | 0.40308
B1033.032b | B1033.032b | Special Concentric Braced Frame, design to AISC minimum standards, Single Diagonal Brace, Brace 41 PLF < w < 99 PLF | 6857.34 | Normal | 0.41426 | 10109.68 | Normal | 0.3933 | 10109.68 | Normal | 0.38773 | [6 empty] | 84302.56 | Normal | 0.41426 | 179082.59 | Normal | 0.3933 | 179082.59 | Normal | 0.38773
B1033.032c | B1033.032c | Special Concentric Braced Frame, design to AISC minimum standards, Single Diagonal Brace, Brace w > 100 PLF | 6857.34 | Normal | 0.41426 | 12743.62 | Normal | 0.38216 | 12743.62 | Normal | 0.37637 | [6 empty] | 84302.56 | Normal | 0.41426 | 255840.93 | Normal | 0.38216 | 255840.93 | Normal | 0.37637
B1033.033a | B1033.033a | Special Concentric Braced Frame, design to AISC minimum standards, X Brace, Brace w < 40 PLF | 6857.34 | Normal | 0.40963 | 9791.34 | Normal | 0.39501 | 9791.34 | Normal | 0.39236 | [6 empty] | 84302.56 | Normal | 0.40963 | 169805.32 | Normal | 0.39501 | 169805.32 | Normal | 0.39236
B1033.033b | B1033.033b | Special Concentric Braced Frame, design to AISC minimum standards, X Brace, Brace 41 PLF < w < 99 PLF | 6857.34 | Normal | 0.40963 | 14623.64 | Normal | 0.37723 | 14623.64 | Normal | 0.37411 | [6 empty] | 84302.56 | Normal | 0.40963 | 310628.7 | Normal | 0.37723 | 310628.7 | Normal | 0.37411
B1033.033c | B1033.033c | Special Concentric Braced Frame, design to AISC minimum standards, X Brace, Brace w > 100 PLF | 6857.34 | Normal | 0.40963 | 20184.05 | Normal | 0.36663 | 20184.05 | Normal | 0.36384 | [6 empty] | 84302.56 | Normal | 0.40963 | 472670.83 | Normal | 0.36663 | 472670.83 | Normal | 0.36384
B1033.041a | B1033.041a | Special Concentric Braced Frame w double angle braces, Chevron Brace, Brace w < 40 PLF | 6857.34 | Normal | 0.41228 | 8927.26 | Normal | 0.4 | 8927.26 | Normal | 0.39619 | [6 empty] | 84302.56 | Normal | 0.41228 | 144624.38 | Normal | 0.4 | 144624.38 | Normal | 0.39619
B1033.041b | B1033.041b | Special Concentric Braced Frame w double angle braces, Chevron Brace, Brace 41 PLF < w < 99 PLF | 6857.34 | Normal | 0.41228 | 12619.65 | Normal | 0.38314 | 12619.65 | Normal | 0.3792 | [6 empty] | 84302.56 | Normal | 0.41228 | 252228.4 | Normal | 0.38314 | 252228.4 | Normal | 0.3792
B1033.041c | B1033.041c | Special Concentric Braced Frame w double angle braces, Chevron Brace, Brace w > 100 PLF | 6857.34 | Normal | 0.41228 | 16947.16 | Normal | 0.37201 | 16947.16 | Normal | 0.36865 | [6 empty] | 84302.56 | Normal | 0.41228 | 378341.16 | Normal | 0.37201 | 378341.16 | Normal | 0.36865
B1033.042a | B1033.042a | Special Concentric Braced Frame w double angle braces, Single Diagonal Brace, Brace w < 40 PLF | 6857.34 | Normal | 0.41426 | 8262.26 | Normal | 0.40298 | 8024.57 | Normal | 0.40197 | [6 empty] | 84302.56 | Normal | 0.41426 | 125244.78 | Normal | 0.40298 | 118317.84 | Normal | 0.40197
B1033.042b | B1033.042b | Special Concentric Braced Frame w double angle braces, Single Diagonal Brace, Brace 41 PLF < w < 99 PLF | 6857.34 | Normal | 0.41426 | 10519.45 | Normal | 0.39154 | 10519.45 | Normal | 0.38629 | [6 empty] | 84302.56 | Normal | 0.41426 | 191024.07 | Normal | 0.39154 | 191024.07 | Normal | 0.38629
B1033.042c | B1033.042c | Special Concentric Braced Frame w double angle braces, Single Diagonal Brace, Brace w > 100 PLF | 6857.34 | Normal | 0.41426 | 13446.07 | Normal | 0.38029 | 13446.07 | Normal | 0.37493 | [6 empty] | 84302.56 | Normal | 0.41426 | 276312.03 | Normal | 0.38029 | 276312.03 | Normal | 0.37493
B1033.043a | B1033.043a | Special Concentric Braced Frame w double angle braces, X Brace, Brace w < 40 PLF | 6857.34 | Normal | 0.40963 | 10142.57 | Normal | 0.39425 | 10142.57 | Normal | 0.3917 | [6 empty] | 84302.56 | Normal | 0.40963 | 180040.88 | Normal | 0.39425 | 180040.88 | Normal | 0.3917
B1033.043b | B1033.043b | Special Concentric Braced Frame w double angle braces, X Brace, Brace 41 PLF < w < 99 PLF | 6857.34 | Normal | 0.40963 | 15443.17 | Normal | 0.37565 | 15443.17 | Normal | 0.37275 | [6 empty] | 84302.56 | Normal | 0.40963 | 334511.66 | Normal | 0.37565 | 334511.66 | Normal | 0.37275
B1033.043c | B1033.043c | Special Concentric Braced Frame w double angle braces, X Brace, Brace w > 100 PLF | 6857.34 | Normal | 0.40963 | 21588.97 | Normal | 0.36427 | 21588.97 | Normal | 0.36182 | [6 empty] | 84302.56 | Normal | 0.40963 | 513613.05 | Normal | 0.36427 | 513613.05 | Normal | 0.36182
B1033.051a | B1033.051a | Ordinary Concentric Braced Frame w compact braces, Chevron Brace, Brace w < 40 PLF | 6692.79 | Normal | 0.41442 | 8503.97 | Normal | 0.40238 | 8503.97 | Normal | 0.39836 | [6 empty] | 79506.99 | Normal | 0.41442 | 132288.58 | Normal | 0.40238 | 132288.58 | Normal | 0.39836
B1033.051b | B1033.051b | Ordinary Concentric Braced Frame w compact braces, Chevron Brace, Brace w, 41 PLF < w < 99 PLF | 6692.79 | Normal | 0.41442 | 11686.81 | Normal | 0.38682 | 11686.81 | Normal | 0.38233 | [6 empty] | 79506.99 | Normal | 0.41442 | 225043.38 | Normal | 0.38682 | 225043.38 | Normal | 0.38233
B1033.051c | B1033.051c | Ordinary Concentric Braced Frame w compact braces, Chevron Brace, Brace w > 100 PLF | 6692.79 | Normal | 0.41442 | 15583.09 | Normal | 0.37478 | 15583.09 | Normal | 0.37092 | [6 empty] | 79506.99 | Normal | 0.41442 | 338589.1 | Normal | 0.37478 | 338589.1 | Normal | 0.37092
B1033.052a | B1033.052a | Ordinary Concentric Braced Frame w compact braces, Single Diagonal Brace, Brace w < 40 PLF | 6692.79 | Normal | 0.41649 | 7922.09 | Normal | 0.40592 | 7739.25 | Normal | 0.40346 | [6 empty] | 79506.99 | Normal | 0.41649 | 115331.43 | Normal | 0.40592 | 110003.01 | Normal | 0.40346
B1033.052b | B1033.052b | Ordinary Concentric Braced Frame w compact braces, Single Diagonal Brace, Brace w, 41 PLF < w < 99 PLF | 6692.79 | Normal | 0.41649 | 9890.27 | Normal | 0.39479 | 9890.27 | Normal | 0.389 | [6 empty] | 79506.99 | Normal | 0.41649 | 172688.49 | Normal | 0.39479 | 172688.49 | Normal | 0.389
B1033.052c | B1033.052c | Ordinary Concentric Braced Frame w compact braces, Single Diagonal Brace, Brace w > 100 PLF | 6692.79 | Normal | 0.41649 | 12524.21 | Normal | 0.38323 | 12524.21 | Normal | 0.37725 | [6 empty] | 79506.99 | Normal | 0.41649 | 249446.83 | Normal | 0.38323 | 249446.83 | Normal | 0.37725
B1033.053a | B1033.053a | Ordinary Concentric Braced Frame w compact braces, X Brace, Brace w < 40 PLF | 6692.79 | Normal | 0.41166 | 9517.07 | Normal | 0.39613 | 9517.07 | Normal | 0.39337 | [6 empty] | 79506.99 | Normal | 0.41166 | 161812.7 | Normal | 0.39613 | 161812.7 | Normal | 0.39337
B1033.053b | B1033.053b | Ordinary Concentric Braced Frame w compact braces, X Brace, Brace w, 41 PLF < w < 99 PLF | 6692.79 | Normal | 0.41166 | 14075.11 | Normal | 0.37871 | 14075.11 | Normal | 0.37539 | [6 empty] | 79506.99 | Normal | 0.41166 | 294643.45 | Normal | 0.37871 | 294643.45 | Normal | 0.37539
B1033.053c | B1033.053c | Ordinary Concentric Braced Frame w compact braces, X Brace, Brace w > 100 PLF | 6692.79 | Normal | 0.41166 | 19635.52 | Normal | 0.36747 | 19635.52 | Normal | 0.36456 | [6 empty] | 79506.99 | Normal | 0.41166 | 456685.58 | Normal | 0.36747 | 456685.58 | Normal | 0.36456
B1033.061a | B1033.061a | Ordinary Concentric Braced Frame, braces design to ductile slenderness limits, Chevron Brace, Brace w < 40 PLF | 6857.34 | Normal | 0.41228 | 8668.52 | Normal | 0.40072 | 8668.52 | Normal | 0.39685 | [6 empty] | 84302.56 | Normal | 0.41228 | 137084.15 | Normal | 0.40072 | 137084.15 | Normal | 0.39685
B1033.061b | B1033.061b | Ordinary Concentric Braced Frame, braces design to ductile slenderness limits, Chevron Brace, Brace 41 PLF < w < 99 PLF | 6857.34 | Normal | 0.41228 | 12015.93 | Normal | 0.38595 | 12015.93 | Normal | 0.38163 | [6 empty] | 84302.56 | Normal | 0.41228 | 234634.53 | Normal | 0.38595 | 234634.53 | Normal | 0.38163
B1033.061c | B1033.061c | Ordinary Concentric Braced Frame, braces design to ductile slenderness limits, Chevron Brace, Brace w > 100 PLF | 6857.34 | Normal | 0.41228 | 15912.2 | Normal | 0.3743 | 15912.2 | Normal | 0.37056 | [6 empty] | 84302.56 | Normal | 0.41228 | 348180.25 | Normal | 0.3743 | 348180.25 | Normal | 0.37056
B1033.062a | B1033.062a | Ordinary Concentric Braced Frame, braces design to ductile slenderness limits, Single Diagonal Brace, Brace w < 40 PLF | 6857.34 | Normal | 0.41426 | 8086.65 | Normal | 0.40413 | 7848.95 | Normal | 0.40308 | [6 empty] | 84302.56 | Normal | 0.41426 | 120127 | Normal | 0.40413 | 113200.06 | Normal | 0.40308
B1033.062b | B1033.062b | Ordinary Concentric Braced Frame, braces design to ductile slenderness limits, Single Diagonal Brace, Brace 41 PLF < w < 99 PLF | 6857.34 | Normal | 0.41426 | 10109.68 | Normal | 0.3933 | 10109.68 | Normal | 0.38773 | [6 empty] | 84302.56 | Normal | 0.41426 | 179082.59 | Normal | 0.3933 | 179082.59 | Normal | 0.38773
B1033.062c | B1033.062c | Ordinary Concentric Braced Frame, braces design to ductile slenderness limits, Single Diagonal Brace, Brace w > 100 PLF | 6857.34 | Normal | 0.41426 | 12743.62 | Normal | 0.38216 | 12743.62 | Normal | 0.37637 | [6 empty] | 84302.56 | Normal | 0.41426 | 255840.93 | Normal | 0.38216 | 255840.93 | Normal | 0.37637
B1033.063a | B1033.063a | Ordinary Concentric Braced Frame, braces design to ductile slenderness limits, X Brace, Brace w < 40 PLF | 6857.34 | Normal | 0.40963 | 9791.34 | Normal | 0.39501 | 9791.34 | Normal | 0.39236 | [6 empty] | 84302.56 | Normal | 0.40963 | 169805.32 | Normal | 0.39501 | 169805.32 | Normal | 0.39236
B1033.063b | B1033.063b | Ordinary Concentric Braced Frame, braces design to ductile slenderness limits, X Brace, Brace 41 PLF < w < 99 PLF | 6857.34 | Normal | 0.40963 | 14623.64 | Normal | 0.37723 | 14623.64 | Normal | 0.37411 | [6 empty] | 84302.56 | Normal | 0.40963 | 310628.7 | Normal | 0.37723 | 310628.7 | Normal | 0.37411
B1033.063c | B1033.063c | Ordinary Concentric Braced Frame, braces design to ductile slenderness limits, X Brace, Brace w > 100 PLF | 6857.34 | Normal | 0.40963 | 20184.05 | Normal | 0.36663 | 20184.05 | Normal | 0.36384 | [6 empty] | 84302.56 | Normal | 0.40963 | 472670.83 | Normal | 0.36663 | 472670.83 | Normal | 0.36384
B1033.071a | B1033.071a | Braced frame, design for factored loads, no additional seismic detailing, Chevron Brace, Brace w < 40 PLF | 8668.52 | Normal | 0.40072 | [12 empty] | 137084.15 | Normal | 0.40072
B1033.071b | B1033.071b | Braced frame, design for factored loads, no additional seismic detailing, Chevron Brace, 41 PLF < w < 99 PLF | 12015.93 | Normal | 0.38595 | [12 empty] | 234634.53 | Normal | 0.38595
B1033.071c | B1033.071c | Braced frame, design for factored loads, no additional seismic detailing, Chevron Brace, Brace w > 100 PLF | 15912.2 | Normal | 0.37431 | [12 empty] | 348180.25 | Normal | 0.37431
B1033.072a | B1033.072a | Braced frame, design for factored loads, no additional seismic detailing, Single Diagonal Brace, Brace w < 40 PLF | 8086.65 | Normal | 0.40413 | [12 empty] | 120127 | Normal | 0.40413
B1033.072b | B1033.072b | Braced frame, design for factored loads, no additional seismic detailing, Single Diagonal Brace, 41 PLF < w < 99 PLF | 10109.68 | Normal | 0.3933 | [12 empty] | 179082.59 | Normal | 0.3933
B1033.072c | B1033.072c | Braced frame, design for factored loads, no additional seismic detailing, Single Diagonal Brace, Brace w > 100 PLF | 12743.62 | Normal | 0.38215 | [12 empty] | 255840.93 | Normal | 0.38215
B1033.073a | B1033.073a | Braced frame, design for factored loads, no additional seismic detailing, X Brace, Brace w < 40 PLF | 9791.34 | Normal | 0.39501 | [12 empty] | 169805.32 | Normal | 0.39501
B1033.073b | B1033.073b | Braced frame, design for factored loads, no additional seismic detailing, X Brace, Brace 41 PLF < w < 99 PLF | 14623.64 | Normal | 0.37722 | [12 empty] | 310628.7 | Normal | 0.37722
B1033.073c | B1033.073c | Braced frame, design for factored loads, no additional seismic detailing, X Brace, Brace w > 100 PLF | 20184.05 | Normal | 0.36663 | [12 empty] | 472670.83 | Normal | 0.36663
B1033.101a | B1033.101a | Steel Buckling Restrained Brace (BRB), Chevron Brace, Weight of brace < 40 plf. | 10071.93 | Normal | 0.39453 | [12 empty] | 177982.34 | Normal | 0.39453
B1033.101b | B1033.101b | Steel Buckling Restrained Brace (BRB), Chevron brace, Weight of brace > 41 plf and < 99 plf. | 15034.56 | Normal | 0.37654 | [12 empty] | 322603.85 | Normal | 0.37654
B1033.101c | B1033.101c | Steel Buckling Restrained Brace (BRB), Chevron Brace, Weight of brace > 100 plf. | 21306.41 | Normal | 0.3645 | [12 empty] | 505378.9 | Normal | 0.3645
B1033.111a | B1033.111a | Steel Buckling Restrained Brace (BRB), Single Diagonal Brace, Weight of brace < 40 plf. | 8800.16 | Normal | 0.39967 | [12 empty] | 140920.31 | Normal | 0.39967
B1033.111b | B1033.111b | Steel Buckling Restrained Brace (BRB), Single Diagonal brace, Weight of brace > 41 plf and < 99 plf. | 12158.52 | Normal | 0.38385 | [12 empty] | 238789.99 | Normal | 0.38385
B1033.111c | B1033.111c | Steel Buckling Restrained Brace (BRB), Single Diagonal Brace, Weight of brace > 100 plf. | 16402.18 | Normal | 0.37355 | [12 empty] | 362459.2 | Normal | 0.37355
B1035.001 | B1035.001 | Post-Northridge RBS connection with welded web, beam one side of column only, beam depth <= W27 | 3049.47 | Normal | 0.43244 | 7991.65 | Normal | 0.39468 | 7991.65 | Normal | 0.39468 | [6 empty] | 33086.21 | Normal | 0.43244 | 127850.77 | Normal | 0.39468 | 127850.77 | Normal | 0.39468
B1035.002 | B1035.002 | Post-Northridge RBS connection with welded web, beam one side of column only, beam depth >= W30 | 3049.47 | Normal | 0.4157 | 8846.65 | Normal | 0.3784 | 8846.65 | Normal | 0.3784 | [6 empty] | 33086.21 | Normal | 0.4157 | 152886.41 | Normal | 0.3784 | 152886.41 | Normal | 0.3784
B1035.011 | B1035.011 | Post-Northridge RBS connection with welded web, beams both sides of column, beam depth <= W27 | 5718.52 | Normal | 0.41201 | 15827.31 | Normal | 0.37271 | 15827.31 | Normal | 0.37271 | [6 empty] | 60737.7 | Normal | 0.41201 | 252404.18 | Normal | 0.37271 | 252404.18 | Normal | 0.37271
B1035.012 | B1035.012 | Post-Northridge RBS connection with welded web, beams both sides of column, beam depth >= W30 | 5718.52 | Normal | 0.39792 | 17537.31 | Normal | 0.35209 | 17537.31 | Normal | 0.35209 | [6 empty] | 60737.7 | Normal | 0.39792 | 302475.45 | Normal | 0.35209 | 302475.45 | Normal | 0.35209
B1035.021 | B1035.021 | Post-Northridge welded steel moment connection other than RBS, beam one side, beam depth <= W27 | 3049.47 | Normal | 0.43244 | 7991.65 | Normal | 0.39468 | 7991.65 | Normal | 0.39468 | [6 empty] | 33086.21 | Normal | 0.43244 | 127850.77 | Normal | 0.39468 | 127850.77 | Normal | 0.39468
B1035.022 | B1035.022 | Post-Northridge welded steel moment connection other than RBS, beam one side, beam depth >= W30 | 3049.47 | Normal | 0.4157 | 8846.65 | Normal | 0.3784 | 8846.65 | Normal | 0.3784 | [6 empty] | 33086.21 | Normal | 0.4157 | 152886.41 | Normal | 0.3784 | 152886.41 | Normal | 0.3784
B1035.031 | B1035.031 | Post-Northridge welded steel moment connection other than RBS, beams both sides, beam depth <= W27 | 5718.52 | Normal | 0.42521 | 15827.31 | Normal | 0.37271 | 15827.31 | Normal | 0.37271 | [6 empty] | 60737.7 | Normal | 0.42521 | 252404.18 | Normal | 0.37271 | 252404.18 | Normal | 0.37271
B1035.032 | B1035.032 | Post-Northridge welded steel moment connection other than RBS, beams both sides, beam depth >= W30 | 5718.52 | Normal | 0.42521 | 17537.31 | Normal | 0.35209 | 17537.31 | Normal | 0.35209 | [6 empty] | 60737.7 | Normal | 0.42521 | 302475.45 | Normal | 0.35209 | 302475.45 | Normal | 0.35209
B1035.041 | B1035.041 | Pre-Northridge WUF-B beam-column joint, beam one side of column, beam depth <= W27 | 1416.43 | Normal | 0.43152 | 2698.01 | Normal | 0.43146 | 5817.36 | LogNormal | 0.40601 | 5478.66 | LogNormal | 0.44554 | 1416.43 | LogNormal | 0.41886 | 19988.22 | Normal | 0.43152 | 36103.25 | Normal | 0.43146 | 81126.06 | LogNormal | 0.40601 | 75095.19 | LogNormal | 0.44554 | 19988.22 | LogNormal | 0.41886
B1035.042 | B1035.042 | Pre-Northridge WUF-B beam-column joint, beam one side of column, beam depth >= W30 | 1464.61 | Normal | 0.43669 | 3173.39 | Normal | 0.44037 | 4241.6 | Normal | 0.44772 | 5478.66 | LogNormal | 0.44554 | 1416.43 | LogNormal | 0.41886 | 21466.75 | Normal | 0.43669 | 42953.46 | Normal | 0.44037 | 60449.59 | Normal | 0.44772 | 75095.19 | LogNormal | 0.44554 | 19988.22 | LogNormal | 0.41886
B1035.051 | B1035.051 | Pre-Northridge WUF-B beam-column joint, beam both sides of column, beam depth <= W27 | 2616.76 | Normal | 0.43702 | 3898.35 | Normal | 0.43647 | 8132.34 | Normal | 0.39364 | 6698.2 | Normal | 0.40447 | 2616.76 | Normal | 0.41116 | 35380.39 | Normal | 0.43702 | 51495.42 | Normal | 0.43647 | 112223.61 | Normal | 0.39364 | 91048.59 | Normal | 0.40447 | 35380.39 | Normal | 0.41116
B1035.052 | B1035.052 | Pre-Northridge WUF-B beam-column joint, beam both sides of column, beam depth >= W30 | 2616.76 | Normal | 0.43702 | 3898.35 | Normal | 0.43647 | 5393.76 | Normal | 0.42934 | 6698.2 | Normal | 0.42316 | 4659.59 | Normal | 0.41448 | 35380.39 | Normal | 0.43702 | 51495.42 | Normal | 0.43647 | 74363.23 | Normal | 0.42934 | 91048.59 | Normal | 0.42316 | 55186.83 | Normal | 0.41448
B1035.061a | B1035.061a | EBF Shear Link, no floor beams, link w < 100 PLF | 26496.05 | Normal | 0.3967 | 26754.1 | Normal | 0.37507 | 32548.81 | Normal | 0.33129 | [6 empty] | 313446.87 | Normal | 0.3967 | 316566.36 | Normal | 0.37507 | 490921.99 | Normal | 0.33129
B1035.061b | B1035.061b | EBF Shear Link, no floor beams, link w < 200 PLF | 26496.05 | Normal | 0.3967 | 26754.1 | Normal | 0.36762 | 37734.89 | Normal | 0.317 | [6 empty] | 313446.87 | Normal | 0.3967 | 316566.36 | Normal | 0.36762 | 642055.27 | Normal | 0.317
B1035.062a | B1035.062a | EBF Shear Link, with floor beams, link w < 100 PLF | 26496.05 | Normal | 0.3967 | 26754.1 | Normal | 0.37507 | 34351.09 | Normal | 0.32434 | [6 empty] | 313446.87 | Normal | 0.3967 | 316566.36 | Normal | 0.37507 | 544161.94 | Normal | 0.32434
B1035.062b | B1035.062b | EBF Shear Link, with floor beams, link w < 200 PLF | 26496.05 | Normal | 0.3967 | 26754.1 | Normal | 0.36762 | 40833.69 | Normal | 0.31644 | [6 empty] | 313446.87 | Normal | 0.3967 | 316566.36 | Normal | 0.36762 | 733078.53 | Normal | 0.31644
B1041.001a | B1041.001a | ACI 318 SMF , Conc Col & Bm = 24" x 24", Beam one side | 4893.36 | Normal | 0.46403 | 7789.54 | Normal | 0.40477 | 9379.2 | Normal | 0.39239 | 7789.54 | Normal | 0.40477 |  |  |  | 72535.39 | Normal | 0.46403 | 111157.79 | Normal | 0.40477 | 161198.78 | Normal | 0.39239 | 111157.79 | Normal | 0.40477
B1041.001b | B1041.001b | ACI 318 SMF , Conc Col & Bm = 24" x 24", Beam both sides | 4893.36 | Normal | 0.46403 | 7789.54 | Normal | 0.40477 | 9379.2 | Normal | 0.39239 | 7789.54 | Normal | 0.40477 |  |  |  | 72535.39 | Normal | 0.46403 | 111157.79 | Normal | 0.40477 | 161198.78 | Normal | 0.39239 | 111157.79 | Normal | 0.40477
B1041.002a | B1041.002a | ACI 318 SMF , Conc Col & Bm = 24" x 36", Beam one side | 4893.36 | Normal | 0.46403 | 8269.16 | Normal | 0.39478 | 9613.79 | Normal | 0.38654 | 8269.16 | Normal | 0.39478 |  |  |  | 72535.39 | Normal | 0.46403 | 118002.06 | Normal | 0.39478 | 165230.57 | Normal | 0.38654 | 118002.06 | Normal | 0.39478
B1041.002b | B1041.002b | ACI 318 SMF , Conc Col & Bm = 24" x 36", Beam both sides | 4893.36 | Normal | 0.46403 | 8269.16 | Normal | 0.39478 | 9613.79 | Normal | 0.38654 | 8269.16 | Normal | 0.39478 |  |  |  | 72535.39 | Normal | 0.46403 | 118002.06 | Normal | 0.39478 | 165230.57 | Normal | 0.38654 | 118002.06 | Normal | 0.39478
B1041.003a | B1041.003a | ACI 318 SMF , Conc Col & Bm = 36" x 36", Beam one side | 4893.36 | Normal | 0.46403 | 8269.16 | Normal | 0.39478 | 9613.79 | Normal | 0.38654 | 8269.16 | Normal | 0.39478 |  |  |  | 72535.39 | Normal | 0.46403 | 118002.06 | Normal | 0.39478 | 165230.57 | Normal | 0.38654 | 118002.06 | Normal | 0.39478
B1041.003b | B1041.003b | ACI 318 SMF , Conc Col & Bm = 36" x 36", Beam both sides | 4893.36 | Normal | 0.46403 | 8269.16 | Normal | 0.39478 | 9613.79 | Normal | 0.38654 | 8269.16 | Normal | 0.39478 |  |  |  | 72535.39 | Normal | 0.46403 | 118002.06 | Normal | 0.39478 | 165230.57 | Normal | 0.38654 | 118002.06 | Normal | 0.39478
B1041.011a | B1041.011a | MF with SMF-conforming beam and column flexural and confinement reinforcement but weak joints , Conc Col & Bm = 24" x 24", Beam one side | 4893.36 | Normal | 0.46403 | 7789.54 | Normal | 0.40477 | 9379.2 | Normal | 0.39239 | 7789.54 | Normal | 0.40477 |  |  |  | 72535.39 | Normal | 0.46403 | 111157.79 | Normal | 0.40477 | 161198.78 | Normal | 0.39239 | 111157.79 | Normal | 0.40477
B1041.011b | B1041.011b | MF with SMF-conforming beam and column flexural and confinement reinforcement but weak joints , Conc Col & Bm = 24" x 24", Beam both sides | 4893.36 | Normal | 0.46403 | 7789.54 | Normal | 0.40477 | 9379.2 | Normal | 0.39239 | 7789.54 | Normal | 0.40477 |  |  |  | 72535.39 | Normal | 0.46403 | 111157.79 | Normal | 0.40477 | 161198.78 | Normal | 0.39239 | 111157.79 | Normal | 0.40477
B1041.012a | B1041.012a | MF with SMF-conforming beam and column flexural and confinement reinforcement but weak joints , Conc Col & Bm = 24" x 36", Beam one side | 4893.36 | Normal | 0.46403 | 8269.16 | Normal | 0.39478 | 9613.79 | Normal | 0.38654 | 8269.16 | Normal | 0.39478 |  |  |  | 72535.39 | Normal | 0.46403 | 118002.06 | Normal | 0.39478 | 165230.57 | Normal | 0.38654 | 118002.06 | Normal | 0.39478
B1041.012b | B1041.012b | MF with SMF-conforming beam and column flexural and confinement reinforcement but weak joints , Conc Col & Bm = 24" x 36", Beam both sides | 4893.36 | Normal | 0.46403 | 8269.16 | Normal | 0.39478 | 9613.79 | Normal | 0.38654 | 8269.16 | Normal | 0.39478 |  |  |  | 72535.39 | Normal | 0.46403 | 118002.06 | Normal | 0.39478 | 165230.57 | Normal | 0.38654 | 118002.06 | Normal | 0.39478
B1041.013a | B1041.013a | MF with SMF-conforming beam and column flexural and confinement reinforcement but weak joints , Conc Col & Bm = 36" x 36", Beam one side | 4893.36 | Normal | 0.46403 | 8269.16 | Normal | 0.39478 | 9613.79 | Normal | 0.38654 | 8269.16 | Normal | 0.39478 |  |  |  | 72535.39 | Normal | 0.46403 | 118002.06 | Normal | 0.39478 | 165230.57 | Normal | 0.38654 | 118002.06 | Normal | 0.39478
B1041.013b | B1041.013b | MF with SMF-conforming beam and column flexural and confinement reinforcement but weak joints , Conc Col & Bm = 36" x 36", Beam both sides | 4893.36 | Normal | 0.46403 | 8269.16 | Normal | 0.39478 | 9613.79 | Normal | 0.38654 | 8269.16 | Normal | 0.39478 |  |  |  | 72535.39 | Normal | 0.46403 | 118002.06 | Normal | 0.39478 | 165230.57 | Normal | 0.38654 | 118002.06 | Normal | 0.39478
B1041.021a | B1041.021a | ACI 318 IMF, Conc Col & Bm = 24" x 24", Beam one side | 4893.36 | Normal | 0.46403 | 7789.54 | Normal | 0.40477 | 9379.2 | Normal | 0.39239 | 7789.54 | Normal | 0.40477 |  |  |  | 72535.39 | Normal | 0.46403 | 111157.79 | Normal | 0.40477 | 161198.78 | Normal | 0.39239 | 111157.79 | Normal | 0.40477
B1041.021b | B1041.021b | ACI 318 IMF, Conc Col & Bm = 24" x 24", Beam both sides | 4893.36 | Normal | 0.46403 | 7789.54 | Normal | 0.40477 | 9379.2 | Normal | 0.39239 | 7789.54 | Normal | 0.40477 |  |  |  | 72535.39 | Normal | 0.46403 | 111157.79 | Normal | 0.40477 | 161198.78 | Normal | 0.39239 | 111157.79 | Normal | 0.40477
B1041.022a | B1041.022a | ACI 318 IMF, Conc Col & Bm = 24" x 36", Beam one side | 4893.36 | Normal | 0.46403 | 8269.16 | Normal | 0.39478 | 9613.79 | Normal | 0.38654 | 8269.16 | Normal | 0.39478 |  |  |  | 72535.39 | Normal | 0.46403 | 118002.06 | Normal | 0.39478 | 165230.57 | Normal | 0.38654 | 118002.06 | Normal | 0.39478
B1041.022b | B1041.022b | ACI 318 IMF, Conc Col & Bm = 24" x 36", Beam both sides | 4893.36 | Normal | 0.46403 | 8269.16 | Normal | 0.39478 | 9613.79 | Normal | 0.38654 | 8269.16 | Normal | 0.39478 |  |  |  | 72535.39 | Normal | 0.46403 | 118002.06 | Normal | 0.39478 | 165230.57 | Normal | 0.38654 | 118002.06 | Normal | 0.39478
B1041.023a | B1041.023a | ACI 318 IMF, Conc Col & Bm = 36" x 36", Beam one side | 4893.36 | Normal | 0.46403 | 8269.16 | Normal | 0.39478 | 9613.79 | Normal | 0.38654 | 8269.16 | Normal | 0.39478 |  |  |  | 72535.39 | Normal | 0.46403 | 118002.06 | Normal | 0.39478 | 165230.57 | Normal | 0.38654 | 118002.06 | Normal | 0.39478
B1041.023b | B1041.023b | ACI 318 IMF, Conc Col & Bm = 36" x 36", Beam both sides | 4893.36 | Normal | 0.46403 | 8269.16 | Normal | 0.39478 | 9613.79 | Normal | 0.38654 | 8269.16 | Normal | 0.39478 |  |  |  | 72535.39 | Normal | 0.46403 | 118002.06 | Normal | 0.39478 | 165230.57 | Normal | 0.38654 | 118002.06 | Normal | 0.39478
B1041.031a | B1041.031a | ACI 318 OMF with weak joints and beam flexural response, Conc Col & Bm = 24" x 24", Beam one side | 4893.36 | Normal | 0.46403 | 7789.54 | Normal | 0.40477 | 9379.2 | Normal | 0.39239 | [6 empty] | 72535.39 | Normal | 0.46403 | 111157.79 | Normal | 0.40477 | 161198.78 | Normal | 0.39239
B1041.031b | B1041.031b | ACI 318 OMF with weak joints and beam flexural response, Conc Col & Bm = 24" x 24", Beam both sides | 4893.36 | Normal | 0.46403 | 7789.54 | Normal | 0.40477 | 9379.2 | Normal | 0.39239 | [6 empty] | 72535.39 | Normal | 0.46403 | 111157.79 | Normal | 0.40477 | 161198.78 | Normal | 0.39239
B1041.032a | B1041.032a | ACI 318 OMF with weak joints and beam flexural response, Conc Col & Bm = 24" x 36", Beam one side | 4893.36 | Normal | 0.46403 | 8269.16 | Normal | 0.39478 | 9613.79 | Normal | 0.38654 | [6 empty] | 72535.39 | Normal | 0.46403 | 118002.06 | Normal | 0.39478 | 165230.57 | Normal | 0.38654
B1041.032b | B1041.032b | ACI 318 OMF with weak joints and beam flexural response, Conc Col & Bm = 24" x 36", Beam both sides | 4893.36 | Normal | 0.46403 | 8269.16 | Normal | 0.39478 | 9613.79 | Normal | 0.38654 | [6 empty] | 72535.39 | Normal | 0.46403 | 118002.06 | Normal | 0.39478 | 165230.57 | Normal | 0.38654
B1041.033a | B1041.033a | ACI 318 OMF with weak joints and beam flexural response, Conc Col & Bm = 36" x 36", Beam one side | 4893.36 | Normal | 0.46403 | 8269.16 | Normal | 0.39478 | 9613.79 | Normal | 0.38654 | [6 empty] | 72535.39 | Normal | 0.46403 | 118002.06 | Normal | 0.39478 | 165230.57 | Normal | 0.38654
B1041.033b | B1041.033b | ACI 318 OMF with weak joints and beam flexural response, Conc Col & Bm = 36" x 36", Beam both sides | 4893.36 | Normal | 0.46403 | 8269.16 | Normal | 0.39478 | 9613.79 | Normal | 0.38654 | [6 empty] | 72535.39 | Normal | 0.46403 | 118002.06 | Normal | 0.39478 | 165230.57 | Normal | 0.38654
B1041.041a | B1041.041a | ACI 318 OMF with weak joints and column flexural response, Conc Col & Bm = 24" x 24", Beam one side | 4893.36 | Normal | 0.46403 | 7789.54 | Normal | 0.40477 | 9379.2 | Normal | 0.39239 | [6 empty] | 72535.39 | Normal | 0.46403 | 111157.79 | Normal | 0.40477 | 161198.78 | Normal | 0.39239
B1041.041b | B1041.041b | ACI 318 OMF with weak joints and column flexural response, Conc Col & Bm = 24" x 24", Beam both sides | 4893.36 | Normal | 0.46403 | 7789.54 | Normal | 0.40477 | 9379.2 | Normal | 0.39239 | [6 empty] | 72535.39 | Normal | 0.46403 | 111157.79 | Normal | 0.40477 | 161198.78 | Normal | 0.39239
B1041.042a | B1041.042a | ACI 318 OMF with weak joints and column flexural response, Conc Col & Bm = 24" x 36", Beam one side | 4893.36 | Normal | 0.46403 | 8269.16 | Normal | 0.39478 | 9613.79 | Normal | 0.38654 | [6 empty] | 72535.39 | Normal | 0.46403 | 118002.06 | Normal | 0.39478 | 165230.57 | Normal | 0.38654
B1041.042b | B1041.042b | ACI 318 OMF with weak joints and column flexural response, Conc Col & Bm = 24" x 36", Beam both sides | 4893.36 | Normal | 0.46403 | 8269.16 | Normal | 0.39478 | 9613.79 | Normal | 0.38654 | [6 empty] | 72535.39 | Normal | 0.46403 | 118002.06 | Normal | 0.39478 | 165230.57 | Normal | 0.38654
B1041.043a | B1041.043a | ACI 318 OMF with weak joints and column flexural response, Conc Col & Bm = 36" x 36", Beam one side | 4893.36 | Normal | 0.46403 | 8269.16 | Normal | 0.39478 | 9613.79 | Normal | 0.38654 | [6 empty] | 72535.39 | Normal | 0.46403 | 118002.06 | Normal | 0.39478 | 165230.57 | Normal | 0.38654
B1041.043b | B1041.043b | ACI 318 OMF with weak joints and column flexural response, Conc Col & Bm = 36" x 36", Beam both sides | 4893.36 | Normal | 0.46403 | 8269.16 | Normal | 0.39478 | 9613.79 | Normal | 0.38654 | [6 empty] | 72535.39 | Normal | 0.46403 | 118002.06 | Normal | 0.39478 | 165230.57 | Normal | 0.38654
B1041.051a | B1041.051a | ACI 318 OMF with weak beams and weak joints, beam flexural or shear response, Conc Col & Bm = 24" x 24", Beam one side | 4893.36 | Normal | 0.46403 | 7789.54 | Normal | 0.40477 | 9379.2 | Normal | 0.39239 | [6 empty] | 72535.39 | Normal | 0.46403 | 111157.79 | Normal | 0.40477 | 161198.78 | Normal | 0.39239
B1041.051b | B1041.051b | ACI 318 OMF with weak beams and weak joints, beam flexural or shear response, Conc Col & Bm = 24" x 24", Beam both sides | 4893.36 | Normal | 0.46403 | 7789.54 | Normal | 0.40477 | 9379.2 | Normal | 0.39239 | [6 empty] | 72535.39 | Normal | 0.46403 | 111157.79 | Normal | 0.40477 | 161198.78 | Normal | 0.39239
B1041.052a | B1041.052a | ACI 318 OMF with weak beams and weak joints, beam flexural or shear response, Conc Col & Bm = 24" x 36", Beam one side | 4893.36 | Normal | 0.46403 | 8269.16 | Normal | 0.39478 | 9613.79 | Normal | 0.38654 | [6 empty] | 72535.39 | Normal | 0.46403 | 118002.06 | Normal | 0.39478 | 165230.57 | Normal | 0.38654
B1041.052b | B1041.052b | ACI 318 OMF with weak beams and weak joints, beam flexural or shear response, Conc Col & Bm = 24" x 36", Beam both sides | 4893.36 | Normal | 0.46403 | 8269.16 | Normal | 0.39478 | 9613.79 | Normal | 0.38654 | [6 empty] | 72535.39 | Normal | 0.46403 | 118002.06 | Normal | 0.39478 | 165230.57 | Normal | 0.38654
B1041.053a | B1041.053a | ACI 318 OMF with weak beams and weak joints, beam flexural or shear response, Conc Col & Bm = 36" x 36", Beam one side | 4893.36 | Normal | 0.46403 | 8269.16 | Normal | 0.39478 | 9613.79 | Normal | 0.38654 | [6 empty] | 72535.39 | Normal | 0.46403 | 118002.06 | Normal | 0.39478 | 165230.57 | Normal | 0.38654
B1041.053b | B1041.053b | ACI 318 OMF with weak beams and weak joints, beam flexural or shear response, Conc Col & Bm = 36" x 36", Beam both sides | 4893.36 | Normal | 0.46403 | 8269.16 | Normal | 0.39478 | 9613.79 | Normal | 0.38654 | [6 empty] | 72535.39 | Normal | 0.46403 | 118002.06 | Normal | 0.39478 | 165230.57 | Normal | 0.38654
B1041.061a | B1041.061a | ACI 318 OMF with weak columns, Conc Col & Bm = 24" x 24", Beam one side | 4893.36 | Normal | 0.46403 | 7789.54 | Normal | 0.40477 | 9379.2 | Normal | 0.39239 | [6 empty] | 72535.39 | Normal | 0.46403 | 111157.79 | Normal | 0.40477 | 161198.78 | Normal | 0.39239
B1041.061b | B1041.061b | ACI 318 OMF with weak columns, Conc Col & Bm = 24" x 24", Beam both sides | 4893.36 | Normal | 0.46403 | 7789.54 | Normal | 0.40477 | 9379.2 | Normal | 0.39239 | [6 empty] | 72535.39 | Normal | 0.46403 | 111157.79 | Normal | 0.40477 | 161198.78 | Normal | 0.39239
B1041.062a | B1041.062a | ACI 318 OMF with weak columns, Conc Col & Bm = 24" x 36", Beam one side | 4893.36 | Normal | 0.46403 | 8269.16 | Normal | 0.39478 | 9613.79 | Normal | 0.38654 | [6 empty] | 72535.39 | Normal | 0.46403 | 118002.06 | Normal | 0.39478 | 165230.57 | Normal | 0.38654
B1041.062b | B1041.062b | ACI 318 OMF with weak columns, Conc Col & Bm = 24" x 36", Beam both sides | 4893.36 | Normal | 0.46403 | 8269.16 | Normal | 0.39478 | 9613.79 | Normal | 0.38654 | [6 empty] | 72535.39 | Normal | 0.46403 | 118002.06 | Normal | 0.39478 | 165230.57 | Normal | 0.38654
B1041.063a | B1041.063a | ACI 318 OMF with weak columns, Conc Col & Bm = 36" x 36", Beam one side | 4893.36 | Normal | 0.46403 | 8269.16 | Normal | 0.39478 | 9613.79 | Normal | 0.38654 | [6 empty] | 72535.39 | Normal | 0.46403 | 118002.06 | Normal | 0.39478 | 165230.57 | Normal | 0.38654
B1041.063b | B1041.063b | ACI 318 OMF with weak columns, Conc Col & Bm = 36" x 36", Beam both sides | 4893.36 | Normal | 0.46403 | 8269.16 | Normal | 0.39478 | 9613.79 | Normal | 0.38654 | [6 empty] | 72535.39 | Normal | 0.46403 | 118002.06 | Normal | 0.39478 | 165230.57 | Normal | 0.38654
B1041.071a | B1041.071a | ACI 318 OMF weak columns w/ high axial load, Conc Col & Bm = 24" x 24", Beam one side | 4893.36 | Normal | 0.46403 | 7789.54 | Normal | 0.40477 | [9 empty] | 72535.39 | Normal | 0.46403 | 111157.79 | Normal | 0.40477
B1041.071b | B1041.071b | ACI 318 OMF weak columns w/ high axial load, Conc Col & Bm = 24" x 24", Beam both sides | 4893.36 | Normal | 0.46403 | 7789.54 | Normal | 0.40477 | [9 empty] | 72535.39 | Normal | 0.46403 | 111157.79 | Normal | 0.40477
B1041.072a | B1041.072a | ACI 318 OMF weak columns w/ high axial load, Conc Col & Bm = 24" x 36", Beam one side | 4893.36 | Normal | 0.46403 | 8269.16 | Normal | 0.39478 | [9 empty] | 72535.39 | Normal | 0.46403 | 118002.06 | Normal | 0.39478
B1041.072b | B1041.072b | ACI 318 OMF weak columns w/ high axial load, Conc Col & Bm = 24" x 36", Beam both sides | 4893.36 | Normal | 0.46403 | 8269.16 | Normal | 0.39478 | [9 empty] | 72535.39 | Normal | 0.46403 | 118002.06 | Normal | 0.39478
B1041.073a | B1041.073a | ACI 318 OMF weak columns w/ high axial load, Conc Col & Bm = 36" x 36", Beam one side | 4893.36 | Normal | 0.46403 | 8269.16 | Normal | 0.39478 | [9 empty] | 72535.39 | Normal | 0.46403 | 118002.06 | Normal | 0.39478
B1041.073b | B1041.073b | ACI 318 OMF weak columns w/ high axial load, Conc Col & Bm = 36" x 36", Beam both sides | 4893.36 | Normal | 0.46403 | 8269.16 | Normal | 0.39478 | [9 empty] | 72535.39 | Normal | 0.46403 | 118002.06 | Normal | 0.39478
B1041.081a | B1041.081a | Non-conforming MF with weak joints and beam flexural response, Conc Col & Bm = 24" x 24", Beam one side | 4893.36 | Normal | 0.46403 | 7789.54 | Normal | 0.40477 | 9379.2 | Normal | 0.39239 | [6 empty] | 72535.39 | Normal | 0.46403 | 111157.79 | Normal | 0.40477 | 161198.78 | Normal | 0.39239
B1041.081b | B1041.081b | Non-conforming MF with weak joints and beam flexural response, Conc Col & Bm = 24" x 24", Beam both sides | 4893.36 | Normal | 0.46403 | 7789.54 | Normal | 0.40477 | 9379.2 | Normal | 0.39239 | [6 empty] | 72535.39 | Normal | 0.46403 | 111157.79 | Normal | 0.40477 | 161198.78 | Normal | 0.39239
B1041.082a | B1041.082a | Non-conforming MF with weak joints and beam flexural response, Conc Col & Bm = 24" x 36", Beam one side | 4893.36 | Normal | 0.46403 | 8269.16 | Normal | 0.39478 | 9613.79 | Normal | 0.38654 | [6 empty] | 72535.39 | Normal | 0.46403 | 118002.06 | Normal | 0.39478 | 165230.57 | Normal | 0.38654
B1041.082b | B1041.082b | Non-conforming MF with weak joints and beam flexural response, Conc Col & Bm = 24" x 36", Beam both sides | 4893.36 | Normal | 0.46403 | 8269.16 | Normal | 0.39478 | 9613.79 | Normal | 0.38654 | [6 empty] | 72535.39 | Normal | 0.46403 | 118002.06 | Normal | 0.39478 | 165230.57 | Normal | 0.38654
B1041.083a | B1041.083a | Non-conforming MF with weak joints and beam flexural response, Conc Col & Bm = 36" x 36", Beam one side | 4893.36 | Normal | 0.46403 | 8269.16 | Normal | 0.39478 | 9613.79 | Normal | 0.38654 | [6 empty] | 72535.39 | Normal | 0.46403 | 118002.06 | Normal | 0.39478 | 165230.57 | Normal | 0.38654
B1041.083b | B1041.083b | Non-conforming MF with weak joints and beam flexural response, Conc Col & Bm = 36" x 36", Beam both sides | 4893.36 | Normal | 0.46403 | 8269.16 | Normal | 0.39478 | 9613.79 | Normal | 0.38654 | [6 empty] | 72535.39 | Normal | 0.46403 | 118002.06 | Normal | 0.39478 | 165230.57 | Normal | 0.38654
B1041.091a | B1041.091a | Non-conforming MF with weak joints and column flexural response, Conc Col & Bm = 24" x 24", Beam one side | 4893.36 | Normal | 0.46403 | 7789.54 | Normal | 0.40477 | 9379.2 | Normal | 0.39239 | [6 empty] | 72535.39 | Normal | 0.46403 | 111157.79 | Normal | 0.40477 | 161198.78 | Normal | 0.39239
B1041.091b | B1041.091b | Non-conforming MF with weak joints and column flexural response, Conc Col & Bm = 24" x 24", Beam both sides | 4893.36 | Normal | 0.46403 | 7789.54 | Normal | 0.40477 | 9379.2 | Normal | 0.39239 | [6 empty] | 72535.39 | Normal | 0.46403 | 111157.79 | Normal | 0.40477 | 161198.78 | Normal | 0.39239
B1041.092a | B1041.092a | Non-conforming MF with weak joints and column flexural response, Conc Col & Bm = 24" x 36", Beam one side | 4893.36 | Normal | 0.46403 | 8269.16 | Normal | 0.39478 | 9613.79 | Normal | 0.38654 | [6 empty] | 72535.39 | Normal | 0.46403 | 118002.06 | Normal | 0.39478 | 165230.57 | Normal | 0.38654
B1041.092b | B1041.092b | Non-conforming MF with weak joints and column flexural response, Conc Col & Bm = 24" x 36", Beam both sides | 4893.36 | Normal | 0.46403 | 8269.16 | Normal | 0.39478 | 9613.79 | Normal | 0.38654 | [6 empty] | 72535.39 | Normal | 0.46403 | 118002.06 | Normal | 0.39478 | 165230.57 | Normal | 0.38654
B1041.093a | B1041.093a | Non-conforming MF with weak joints and column flexural response, Conc Col & Bm = 36" x 36", Beam one side | 4893.36 | Normal | 0.46403 | 8269.16 | Normal | 0.39478 | 9613.79 | Normal | 0.38654 | [6 empty] | 72535.39 | Normal | 0.46403 | 118002.06 | Normal | 0.39478 | 165230.57 | Normal | 0.38654
B1041.093b | B1041.093b | Non-conforming MF with weak joints and column flexural response, Conc Col & Bm = 36" x 36", Beam both sides | 4893.36 | Normal | 0.46403 | 8269.16 | Normal | 0.39478 | 9613.79 | Normal | 0.38654 | [6 empty] | 72535.39 | Normal | 0.46403 | 118002.06 | Normal | 0.39478 | 165230.57 | Normal | 0.38654
B1041.101a | B1041.101a | Non-conforming MF, weak beams and strong joints, Conc Col & Bm = 24" x 24", Beam one side | 4893.36 | Normal | 0.46403 | 7789.54 | Normal | 0.40477 | 9379.2 | Normal | 0.39239 | [6 empty] | 72535.39 | Normal | 0.46403 | 111157.79 | Normal | 0.40477 | 161198.78 | Normal | 0.39239
B1041.101b | B1041.101b | Non-conforming MF, weak beams and strong joints, Conc Col & Bm = 24" x 24", Beam both sides | 4893.36 | Normal | 0.46403 | 7789.54 | Normal | 0.40477 | 9379.2 | Normal | 0.39239 | [6 empty] | 72535.39 | Normal | 0.46403 | 111157.79 | Normal | 0.40477 | 161198.78 | Normal | 0.39239
B1041.102a | B1041.102a | Non-conforming MF, weak beams and strong joints, Conc Col & Bm = 24" x 36", Beam one side | 4893.36 | Normal | 0.46403 | 8269.16 | Normal | 0.39478 | 9613.79 | Normal | 0.38654 | [6 empty] | 72535.39 | Normal | 0.46403 | 118002.06 | Normal | 0.39478 | 165230.57 | Normal | 0.38654
B1041.102b | B1041.102b | Non-conforming MF, weak beams and strong joints, Conc Col & Bm = 24" x 36", Beam both sides | 4893.36 | Normal | 0.46403 | 8269.16 | Normal | 0.39478 | 9613.79 | Normal | 0.38654 | [6 empty] | 72535.39 | Normal | 0.46403 | 118002.06 | Normal | 0.39478 | 165230.57 | Normal | 0.38654
B1041.103a | B1041.103a | Non-conforming MF, weak beams and strong joints, Conc Col & Bm = 36" x 36", Beam one side | 4893.36 | Normal | 0.46403 | 8269.16 | Normal | 0.39478 | 9613.79 | Normal | 0.38654 | [6 empty] | 72535.39 | Normal | 0.46403 | 118002.06 | Normal | 0.39478 | 165230.57 | Normal | 0.38654
B1041.103b | B1041.103b | Non-conforming MF, weak beams and strong joints, Conc Col & Bm = 36" x 36", Beam both sides | 4893.36 | Normal | 0.46403 | 8269.16 | Normal | 0.39478 | 9613.79 | Normal | 0.38654 | [6 empty] | 72535.39 | Normal | 0.46403 | 118002.06 | Normal | 0.39478 | 165230.57 | Normal | 0.38654
B1041.111a | B1041.111a | Non-conforming MF, weak columns, Conc Col & Bm = 24" x 24", Beam one side | 4893.36 | Normal | 0.46403 | 7789.54 | Normal | 0.40477 | 9379.2 | Normal | 0.39239 | [6 empty] | 72535.39 | Normal | 0.46403 | 111157.79 | Normal | 0.40477 | 161198.78 | Normal | 0.39239
B1041.111b | B1041.111b | Non-conforming MF, weak columns, Conc Col & Bm = 24" x 24", Beam both sides | 4893.36 | Normal | 0.46403 | 7789.54 | Normal | 0.40477 | 9379.2 | Normal | 0.39239 | [6 empty] | 72535.39 | Normal | 0.46403 | 111157.79 | Normal | 0.40477 | 161198.78 | Normal | 0.39239
B1041.112a | B1041.112a | Non-conforming MF, weak columns, Conc Col & Bm = 24" x 36", Beam one side | 4893.36 | Normal | 0.46403 | 8269.16 | Normal | 0.39478 | 9613.79 | Normal | 0.38654 | [6 empty] | 72535.39 | Normal | 0.46403 | 118002.06 | Normal | 0.39478 | 165230.57 | Normal | 0.38654
B1041.112b | B1041.112b | Non-conforming MF, weak columns, Conc Col & Bm = 24" x 36", Beam both sides | 4893.36 | Normal | 0.46403 | 8269.16 | Normal | 0.39478 | 9613.79 | Normal | 0.38654 | [6 empty] | 72535.39 | Normal | 0.46403 | 118002.06 | Normal | 0.39478 | 165230.57 | Normal | 0.38654
B1041.113a | B1041.113a | Non-conforming MF, weak columns, Conc Col & Bm = 36" x 36", Beam one side | 4893.36 | Normal | 0.46403 | 8269.16 | Normal | 0.39478 | 9613.79 | Normal | 0.38654 | [6 empty] | 72535.39 | Normal | 0.46403 | 118002.06 | Normal | 0.39478 | 165230.57 | Normal | 0.38654
B1041.113b | B1041.113b | Non-conforming MF, weak columns, Conc Col & Bm = 36" x 36", Beam both sides | 4893.36 | Normal | 0.46403 | 8269.16 | Normal | 0.39478 | 9613.79 | Normal | 0.38654 | [6 empty] | 72535.39 | Normal | 0.46403 | 118002.06 | Normal | 0.39478 | 165230.57 | Normal | 0.38654
B1041.121a | B1041.121a | Non-conforming MF, weak columns and strong joints, Conc Col & Bm = 24" x 24", Beam both sides | 4893.36 | Normal | 0.46403 | 9708.03 | Normal | 0.37999 | [9 empty] | 72535.39 | Normal | 0.46403 | 138534.87 | Normal | 0.37999
B1041.121b | B1041.121b | Non-conforming MF, weak columns and strong joints, Conc Col & Bm = 24" x 24", Beam one side | 4893.36 | Normal | 0.46403 | 9708.03 | Normal | 0.37999 | [9 empty] | 72535.39 | Normal | 0.46403 | 138534.87 | Normal | 0.37999
B1041.122a | B1041.122a | Non-conforming MF, weak columns and strong joints, Conc Col & Bm = 24" x 36", Beam one side | 4893.36 | Normal | 0.46403 | 9947.84 | Normal | 0.37469 | [9 empty] | 72535.39 | Normal | 0.46403 | 141957 | Normal | 0.37469
B1041.122b | B1041.122b | Non-conforming MF, weak columns and strong joints, Conc Col & Bm = 24" x 36", Beam both sides | 4893.36 | Normal | 0.46403 | 9947.84 | Normal | 0.37469 | [9 empty] | 72535.39 | Normal | 0.46403 | 141957 | Normal | 0.37469
B1041.123a | B1041.123a | Non-conforming MF, weak columns and strong joints, Conc Col & Bm = 36" x 36", Beam one side | 4893.36 | Normal | 0.46403 | 9947.84 | Normal | 0.37469 | [9 empty] | 72535.39 | Normal | 0.46403 | 141957 | Normal | 0.37469
B1041.123b | B1041.123b | Non-conforming MF, weak columns and strong joints, Conc Col & Bm = 36" x 36", Beam both sides | 4893.36 | Normal | 0.46403 | 9947.84 | Normal | 0.37469 | [9 empty] | 72535.39 | Normal | 0.46403 | 141957 | Normal | 0.37469
B1041.131a | B1041.131a | Non-conforming MF with inadequate development of reinforcing, Conc Col & Bm = 24" x 24", Beam one side | 4893.36 | Normal | 0.46403 | 9708.03 | Normal | 0.37999 | [9 empty] | 72535.39 | Normal | 0.46403 | 138534.87 | Normal | 0.37999
B1041.131b | B1041.131b | Non-conforming MF with inadequate development of reinforcing, Conc Col & Bm = 24" x 24", Beam both sides | 4893.36 | Normal | 0.46403 | 9708.03 | Normal | 0.37999 | [9 empty] | 72535.39 | Normal | 0.46403 | 138534.87 | Normal | 0.37999
B1041.132a | B1041.132a | Non-conforming MF with inadequate development of reinforcing, Conc Col & Bm = 24" x 36", Beam one side | 4893.36 | Normal | 0.46403 | 9947.84 | Normal | 0.37469 | [9 empty] | 72535.39 | Normal | 0.46403 | 141957 | Normal | 0.37469
B1041.132b | B1041.132b | Non-conforming MF with inadequate development of reinforcing, Conc Col & Bm = 24" x 36", Beam both sides | 4893.36 | Normal | 0.46403 | 9947.84 | Normal | 0.37469 | [9 empty] | 72535.39 | Normal | 0.46403 | 141957 | Normal | 0.37469
B1041.133a | B1041.133a | Non-conforming MF with inadequate development of reinforcing, Conc Col & Bm = 36" x 36", Beam one side | 4893.36 | Normal | 0.46403 | 9947.84 | Normal | 0.37469 | [9 empty] | 72535.39 | Normal | 0.46403 | 141957 | Normal | 0.37469
B1041.133b | B1041.133b | Non-conforming MF with inadequate development of reinforcing, Conc Col & Bm = 36" x 36", Beam both sides | 4893.36 | Normal | 0.46403 | 9947.84 | Normal | 0.37469 | [9 empty] | 72535.39 | Normal | 0.46403 | 141957 | Normal | 0.37469
B1044.001 | B1044.001 | Rectangular low aspect ratio concrete walls 8" or less thick single curtain up to 15' high | 1480.32 | LogNormal | 0.30816 | 4033.44 | LogNormal | 0.29767 | 5734.08 | LogNormal | 0.28944 | [6 empty] | 34886.88 | LogNormal | 0.30816 | 77496.48 | LogNormal | 0.29767 | 112569.12 | LogNormal | 0.28944
B1044.002 | B1044.002 | Rectangular low aspect ratio concrete walls 8" or less thick single curtain 16' high to 24' high | 4112 | LogNormal | 0.27828 | 12544 | LogNormal | 0.27725 | 15652 | LogNormal | 0.29044 | [6 empty] | 96768 | LogNormal | 0.27828 | 255948 | LogNormal | 0.27725 | 297868 | LogNormal | 0.29044
B1044.003 | B1044.003 | Rectangular low aspect ratio concrete walls 8" or less thick single curtain 25' high to 40' high | 9144 | LogNormal | 0.27623 | 27513 | LogNormal | 0.26488 | 32616 | LogNormal | 0.29368 | [6 empty] | 215253 | LogNormal | 0.27623 | 556173 | LogNormal | 0.26488 | 600156 | LogNormal | 0.29368
B1044.011 | B1044.011 | Rectangular low aspect ratio concrete walls 8"-16" double curtain; with heights of up to 15' | 1830.24 | LogNormal | 0.29432 | 5194.08 | LogNormal | 0.28085 | 8091.36 | LogNormal | 0.27514 | [6 empty] | 43171.2 | LogNormal | 0.29432 | 105858.72 | LogNormal | 0.28085 | 161380.8 | LogNormal | 0.27514
B1044.012 | B1044.012 | Rectangular low aspect ratio concrete walls 8"-16" double curtain; with heights of 16' to 24' | 5084 | LogNormal | 0.27185 | 14208 | LogNormal | 0.27043 | 21160 | LogNormal | 0.27333 | [6 empty] | 119780 | LogNormal | 0.27185 | 286804 | LogNormal | 0.27043 | 408112 | LogNormal | 0.27333
B1044.013 | B1044.013 | Rectangular low aspect ratio concrete walls 8"-16" double curtain; with heights of 24' to 40' | 11331 | LogNormal | 0.26993 | 31257 | LogNormal | 0.26133 | 43515 | LogNormal | 0.27643 | [6 empty] | 267030 | LogNormal | 0.26993 | 625590 | LogNormal | 0.26133 | 796869 | LogNormal | 0.27643
B1044.021 | B1044.021 | Rectangular low aspect ratio concrete walls 18"-24" thick with double curtain and heights up to 15' | 2704.32 | LogNormal | 0.2754 | 6465.6 | LogNormal | 0.27867 | 11587.68 | LogNormal | 0.26655 | [6 empty] | 63882.72 | LogNormal | 0.2754 | 131297.76 | LogNormal | 0.27867 | 212364 | LogNormal | 0.26655
B1044.022 | B1044.022 | Rectangular low aspect ratio concrete walls 18"-24" thick with double curtain and heights 16' - 24' | 7512 | LogNormal | 0.26284 | 17740 | LogNormal | 0.26416 | 30816 | LogNormal | 0.26591 | [6 empty] | 177312 | LogNormal | 0.26284 | 357476 | LogNormal | 0.26416 | 548536 | LogNormal | 0.26591
B1044.023 | B1044.023 | Rectangular low aspect ratio concrete walls 18"-24" thick with double curtain and heights 25' - 40' | 16794 | LogNormal | 0.26138 | 39204 | LogNormal | 0.25768 | 64341 | LogNormal | 0.28393 | [6 empty] | 396477 | LogNormal | 0.26138 | 784593 | LogNormal | 0.25768 | 1098360 | LogNormal | 0.28393
B1044.031 | B1044.031 | Low-rise reinforced concrete walls with return flanges, less than 8" thick up to 15' high | 4502.88 | LogNormal | 0.28471 | 5734.08 | LogNormal | 0.30666 | [9 empty] | 92547.36 | LogNormal | 0.28471 | 112569.12 | LogNormal | 0.30666
B1044.032 | B1044.032 | Low-rise reinforced concrete walls with return flanges, less than 8" thick, 16' to 24' high | 12284 | LogNormal | 0.27719 | 15652 | LogNormal | 0.30183 | [9 empty] | 249808 | LogNormal | 0.27719 | 297868 | LogNormal | 0.30183
B1044.033 | B1044.033 | Low-rise reinforced concrete walls with return flanges, less than 8" thick, 25' to 40' high | 26928 | LogNormal | 0.26541 | 32616 | LogNormal | 0.29657 | [9 empty] | 542367 | LogNormal | 0.26541 | 600156 | LogNormal | 0.29657
B1044.041 | B1044.041 | Low-rise reinforced concrete walls with return flanges, 8" to 16" thick up to 15' high | 5077.44 | LogNormal | 0.2773 | 8091.36 | LogNormal | 0.2862 | [9 empty] | 103098.24 | LogNormal | 0.2773 | 161380.8 | LogNormal | 0.2862
B1044.042 | B1044.042 | Low-rise reinforced concrete walls with return flanges, 8" to 16" thick, 16' to 24' high | 13884 | LogNormal | 0.27118 | 21900 | LogNormal | 0.29292 | [9 empty] | 279132 | LogNormal | 0.27118 | 430824 | LogNormal | 0.29292
B1044.043 | B1044.043 | Low-rise reinforced concrete walls with return flanges, 8" to 16" thick, 25' to 40' high | 30528 | LogNormal | 0.26178 | 45180 | Normal | 0.29003 | [9 empty] | 608328 | LogNormal | 0.26178 | 847962 | Normal | 0.29003
B1044.051 | B1044.051 | Low-rise reinforced concrete walls with return flanges, 17" to 24" thick" up to 15' high | 6289.92 | LogNormal | 0.26931 | 11587.68 | LogNormal | 0.27802 | [9 empty] | 127156.32 | LogNormal | 0.26931 | 212364 | LogNormal | 0.27802
B1044.052 | B1044.052 | Low-rise reinforced concrete walls with return flanges, 17" to 24" thick, 16' to 24' high | 17256 | LogNormal | 0.26481 | 31556 | LogNormal | 0.27808 | [9 empty] | 345968 | LogNormal | 0.26481 | 571244 | LogNormal | 0.27808
B1044.053 | B1044.053 | Low-rise reinforced concrete walls with return flanges, 17" to 24" thick, 25' to 40' high | 38106 | LogNormal | 0.25805 | 66006 | Normal | 0.28696 | [9 empty] | 758700 | LogNormal | 0.25805 | 1149453 | Normal | 0.28696
B1044.061 | B1044.061 | Low rise reinforced concrete walls with boundary columns, less than 8" thick, height <15' | 4502.88 | LogNormal | 0.28471 | 5734.08 | LogNormal | 0.30666 | [9 empty] | 92547.36 | LogNormal | 0.28471 | 112569.12 | LogNormal | 0.30666
B1044.062 | B1044.062 | Low rise reinforced concrete walls with boundary columns, less than 8" thick, height between 16'-24' | 12284 | LogNormal | 0.27719 | 15652 | LogNormal | 0.30183 | [9 empty] | 249808 | LogNormal | 0.27719 | 297868 | LogNormal | 0.30183
B1044.063 | B1044.063 | Low rise reinforced concrete walls with boundary columns, less than 8" thick, height between 24'-40' | 26928 | LogNormal | 0.26541 | 32616 | LogNormal | 0.29657 | [9 empty] | 542367 | LogNormal | 0.26541 | 600156 | LogNormal | 0.29657
B1044.071 | B1044.071 | Low rise reinforced concrete walls with boundary columns, 8" to 16" thick, height <15' | 5077.44 | LogNormal | 0.2773 | 8690.4 | LogNormal | 0.29282 | [9 empty] | 103098.24 | LogNormal | 0.2773 | 194140.8 | LogNormal | 0.29282
B1044.072 | B1044.072 | Low rise reinforced concrete walls with boundary columns, 8" to 16" thick, height between 16'-24' | 13884 | LogNormal | 0.27118 | 21900 | LogNormal | 0.29292 | [9 empty] | 279132 | LogNormal | 0.27118 | 430824 | LogNormal | 0.29292
B1044.073 | B1044.073 | Low rise reinforced concrete walls with boundary columns, 8" to 16" thick, height between 24'-40' | 30528 | LogNormal | 0.26178 | 45180 | Normal | 0.29003 | [9 empty] | 608328 | LogNormal | 0.26178 | 847962 | Normal | 0.29003
B1044.081 | B1044.081 | Low rise reinforced concrete walls with boundary columns, 17"-24" thick, height <15' | 6289.92 | LogNormal | 0.26931 | 11088 | LogNormal | 0.28714 | [9 empty] | 127156.32 | LogNormal | 0.26931 | 209769.12 | LogNormal | 0.28714
B1044.082 | B1044.082 | Low rise reinforced concrete walls with boundary columns, 17"-24" thick, height between 16'-24' | 17256 | LogNormal | 0.26481 | 31556 | LogNormal | 0.27808 | [9 empty] | 345968 | LogNormal | 0.26481 | 571244 | LogNormal | 0.27808
B1044.083 | B1044.083 | Low rise reinforced concrete walls with boundary columns, 17"-24" thick, height between 24'-40' | 38106 | LogNormal | 0.25805 | 66006 | Normal | 0.28606 | [9 empty] | 758700 | LogNormal | 0.25805 | 1149453 | Normal | 0.28606
B1044.091 | B1044.091 | Slender Concrete Wall, 12" thick, 12' high, 15' long | 1487.52 | LogNormal | 0.42735 | 8519.04 | LogNormal | 0.34821 | 8020.8 | LogNormal | 0.29662 | [6 empty] | 35071.2 | LogNormal | 0.42735 | 173583.36 | LogNormal | 0.34821 | 162470.88 | LogNormal | 0.29662
B1044.092 | B1044.092 | Slender Concrete Wall, 12" thick, 12' high, 20' long | 1471.68 | LogNormal | 0.4001 | 6779.52 | LogNormal | 0.34459 | 7912.8 | LogNormal | 0.28946 | [6 empty] | 34747.2 | LogNormal | 0.4001 | 139459.68 | LogNormal | 0.34459 | 160328.16 | LogNormal | 0.28946
B1044.093 | B1044.093 | Slender Concrete Wall, 12" thick, 12' high, 30' long | 1455.84 | LogNormal | 0.36908 | 4625.28 | LogNormal | 0.34358 | 8153.28 | LogNormal | 0.28228 | [6 empty] | 34421.76 | LogNormal | 0.36908 | 92577.6 | LogNormal | 0.34358 | 166469.76 | LogNormal | 0.28228
B1044.101 | B1044.101 | Slender Concrete Wall, 18" thick, 12' high, 15' long | 2711.52 | LogNormal | 0.37793 | 12022.56 | Normal | 0.3279 | 10385.28 | LogNormal | 0.29455 | [6 empty] | 64067.04 | LogNormal | 0.37793 | 256435.2 | Normal | 0.3279 | 203626.08 | LogNormal | 0.29455
B1044.102 | B1044.102 | Slender Concrete Wall, 18" thick, 12' high, 20' long | 2695.68 | LogNormal | 0.35896 | 9744.48 | Normal | 0.325 | 10275.84 | LogNormal | 0.28807 | [6 empty] | 63741.6 | LogNormal | 0.35896 | 209571.84 | Normal | 0.325 | 201481.92 | LogNormal | 0.28807
B1044.103 | B1044.103 | Slender Concrete Wall, 18" thick, 12' high, 30' long | 2679.84 | LogNormal | 0.33874 | 7466.4 | Normal | 0.32049 | 10203.84 | LogNormal | 0.28158 | [6 empty] | 63417.6 | LogNormal | 0.33874 | 162708.48 | Normal | 0.32049 | 199962.72 | LogNormal | 0.28158
B1044.111 | B1044.111 | Slender Concrete Wall, 30" thick, 12' high, 15' long | 4459.68 | LogNormal | 0.34831 | 18122.4 | Normal | 0.31528 | 15184.8 | LogNormal | 0.29136 | [6 empty] | 105488.64 | LogNormal | 0.34831 | 369233.28 | Normal | 0.31528 | 287182.08 | LogNormal | 0.29136
B1044.112 | B1044.112 | Slender Concrete Wall, 30" thick, 12' high, 20' long | 4443.84 | LogNormal | 0.33549 | 14800.32 | Normal | 0.31323 | 15058.08 | LogNormal | 0.28595 | [6 empty] | 105164.64 | LogNormal | 0.33549 | 305560.8 | Normal | 0.31323 | 284726.88 | LogNormal | 0.28595
B1044.113 | B1044.113 | Slender Concrete Wall, 30" thick, 12' high, 30' long | 4428 | LogNormal | 0.3223 | 11478.24 | Normal | 0.31017 | 14967.36 | LogNormal | 0.28054 | [6 empty] | 104839.2 | LogNormal | 0.3223 | 241889.76 | Normal | 0.31017 | 282895.2 | LogNormal | 0.28054
B1049.001a | B1049.001a | Reinforced concrete flat slabs- columns without shear reinforcing 0<Vg/Vo<.2, no continuity reinf | 4450.67 | Normal | 0.4281 | 6292.68 | LogNormal | 0.40709 | [9 empty] | 96009.03 | Normal | 0.4281 | 96114.98 | LogNormal | 0.40709
B1049.001b | B1049.001b | Reinforced concrete flat slabs- columns without shear reinforcing 0<Vg/Vo<.2, with continuity reinf | 4450.67 | Normal | 0.4281 | 7148.84 | Normal | 0.41127 | [9 empty] | 96009.03 | Normal | 0.4281 | 178806.6 | Normal | 0.41127
B1049.002a | B1049.002a | Reinforced concrete flat slabs- columns without shear reinforcing .2<Vg/Vo<.4, no continuity reinf | 4450.67 | Normal | 0.4281 | 6292.68 | LogNormal | 0.40709 | [9 empty] | 96009.03 | Normal | 0.4281 | 96114.98 | LogNormal | 0.40709
B1049.002b | B1049.002b | Reinforced concrete flat slabs- columns without shear reinforcing .2<Vg/Vo<.4, with continuity reinf | 4450.67 | Normal | 0.4281 | 7148.84 | Normal | 0.41127 | [9 empty] | 96009.03 | Normal | 0.4281 | 178806.6 | Normal | 0.41127
B1049.003a | B1049.003a | Reinforced concrete flat slabs- columns without shear reinforcing .4<Vg/Vo<.6, no continuity reinf | 4693.48 | Normal | 0.42342 | 6292.68 | LogNormal | 0.40709 | [9 empty] | 101762.12 | Normal | 0.42342 | 96114.98 | LogNormal | 0.40709
B1049.003b | B1049.003b | Reinforced concrete flat slabs- columns without shear reinforcing .4<Vg/Vo<.6, with continuity reinf | 4693.48 | Normal | 0.42342 | 7391.65 | Normal | 0.40746 | [9 empty] | 101762.12 | Normal | 0.42342 | 184559.69 | Normal | 0.40746
B1049.011 | B1049.011 | Reinforced concrete flat slabs- columns with shear reinforcing 0.2<Vg/Vo<0.4 | 4936.29 | Normal | 0.41892 | 7634.46 | Normal | 0.40378 | [9 empty] | 107515.21 | Normal | 0.41892 | 190312.78 | Normal | 0.40378
B1049.012 | B1049.012 | Reinforced concrete flat slabs- columns with shear reinforcing 0.4<Vg/Vo<.6 | 5179.1 | Normal | 0.41459 | 7877.27 | Normal | 0.40023 | [9 empty] | 113268.3 | Normal | 0.41459 | 196065.86 | Normal | 0.40023
B1049.021a | B1049.021a | Post-tensioned concrete flat slabs- columns without shear reinforcing 0.2<Vg/Vo<.0.4, no continuity reinf | 4207.86 | Normal | 0.43297 | 6292.68 | LogNormal | 0.40709 | [9 empty] | 90255.94 | Normal | 0.43297 | 96114.98 | LogNormal | 0.40709
B1049.021b | B1049.021b | Post-tensioned concrete flat slabs- columns without shear reinforcing 0.2<Vg/Vo<.0.4, with continuity reinf | 4207.86 | Normal | 0.43297 | 6906.03 | Normal | 0.41521 | [9 empty] | 90255.94 | Normal | 0.43297 | 173053.51 | Normal | 0.41521
B1049.022a | B1049.022a | Post-tensioned concrete flat slabs- columns without shear reinforcing 0.4<Vg/Vo<.0.6, no continuity reinf | 4450.67 | Normal | 0.4281 | 6292.68 | LogNormal | 0.40709 | [9 empty] | 96009.03 | Normal | 0.4281 | 96114.98 | LogNormal | 0.40709
B1049.022b | B1049.022b | Post-tensioned concrete flat slabs- columns without shear reinforcing 0.4<Vg/Vo<.0.6, with continuity reinf | 4450.67 | Normal | 0.4281 | 7148.84 | Normal | 0.41127 | [9 empty] | 96009.03 | Normal | 0.4281 | 178806.6 | Normal | 0.41127
B1049.031 | B1049.031 | Post-tensioned concrete flat slabs- columns with shear reinforcing 0<Vg/Vo<.0.4 | 4531.6 | Normal | 0.42652 | 7229.78 | Normal | 0.40998 | [9 empty] | 97926.73 | Normal | 0.42652 | 180724.3 | Normal | 0.40998
B1049.032 | B1049.032 | Post-tensioned concrete flat slabs- columns with shear reinforcing 0.4<Vg/Vo<.0.6 | 4774.41 | Normal | 0.4219 | 7472.59 | Normal | 0.40622 | [9 empty] | 103679.82 | Normal | 0.4219 | 186477.38 | Normal | 0.40622
B1049.041a | B1049.041a | Reinforced concrete flat slabs drop panel or drop capital- columns without shear reinforcing 0<Vg/Vo<0.4, no continuity reinf | 4450.67 | Normal | 0.4281 | 6292.68 | LogNormal | 0.40709 | [9 empty] | 96009.03 | Normal | 0.4281 | 96114.98 | LogNormal | 0.40709
B1049.041b | B1049.041b | Reinforced concrete flat slabs drop panel or drop capital- columns without shear reinforcing 0<Vg/Vo<0.4, with continuity reinf | 4450.67 | Normal | 0.4281 | 7148.84 | Normal | 0.41127 | [9 empty] | 96009.03 | Normal | 0.4281 | 178806.6 | Normal | 0.41127
B1049.042a | B1049.042a | Reinforced concrete flat slabs drop panel or drop capital- columns without shear reinforcing 0.4<Vg/Vo<0.6, no continuity reinf | 4693.48 | Normal | 0.42342 | 6292.68 | LogNormal | 0.40709 | [9 empty] | 101762.12 | Normal | 0.42342 | 96114.98 | LogNormal | 0.40709
B1049.042b | B1049.042b | Reinforced concrete flat slabs drop panel or drop capital- columns without shear reinforcing 0.4<Vg/Vo<0.6, with continuity reinf | 4693.48 | Normal | 0.42342 | 7391.65 | Normal | 0.40746 | [9 empty] | 101762.12 | Normal | 0.42342 | 184559.69 | Normal | 0.40746
B1042.001a | B1042.001a | Concrete link beam, diagonally reinforced, aspect ratio between 1.0 and 2.0, beam < 16" wide and depth < 30" | 1338.55 | LogNormal | 0.5047 | 5260.54 | Normal | 0.44208 | 9761.67 | Normal | 0.42715 | [6 empty] | 31773.75 | LogNormal | 0.5047 | 72425.13 | Normal | 0.44208 | 173751.93 | Normal | 0.42715
B1042.001b | B1042.001b | Concrete link beam, diagonally reinforced, aspect ratio between 2.0 and 4.0, beam < 16" wide and depth < 30" | 810.12 | LogNormal | 0.57317 | 5254.77 | Normal | 0.44431 | 8457.52 | Normal | 0.45273 | [6 empty] | 19219.92 | LogNormal | 0.57317 | 72256.77 | Normal | 0.44431 | 154504.78 | Normal | 0.45273
B1042.002a | B1042.002a | Concrete link beam, conventionally reinforced, aspect ratio between 1.0 and 2.0, beam < 16" wide and depth < 30" | 1338.55 | LogNormal | 0.5047 | 5260.54 | Normal | 0.44208 | 9761.67 | Normal | 0.42715 | [6 empty] | 31773.75 | LogNormal | 0.5047 | 72425.13 | Normal | 0.44208 | 173751.93 | Normal | 0.42715
B1042.002b | B1042.002b | Concrete link beam, conventionally reinforced, aspect ratio between 2.0 and 4.0, beam < 16" wide and depth < 30" | 810.12 | LogNormal | 0.57317 | 5254.77 | Normal | 0.44431 | 8457.52 | Normal | 0.45273 | [6 empty] | 19219.92 | LogNormal | 0.57317 | 72256.77 | Normal | 0.44431 | 154504.78 | Normal | 0.45273
B1042.011a | B1042.011a | Concrete link beam, diagonally reinforced, apsect ratio between 1.0 and 2.0, beam > 16" wide and depth < 30" | 1338.55 | LogNormal | 0.5047 | 5445.51 | Normal | 0.43147 | 9981.57 | Normal | 0.42067 | [6 empty] | 31773.75 | LogNormal | 0.5047 | 74971.73 | Normal | 0.43147 | 177666.14 | Normal | 0.42067
B1042.011b | B1042.011b | Concrete link beam, diagonally reinforced, apsect ratio between 2.0 and 4.0, beam > 16" wide and depth < 30" | 810.12 | LogNormal | 0.57317 | 5443.52 | Normal | 0.43352 | 8660.97 | Normal | 0.44512 | [6 empty] | 19219.92 | LogNormal | 0.57317 | 74852.2 | Normal | 0.43352 | 158221.52 | Normal | 0.44512
B1042.012a | B1042.012a | Concrete link beam, conventionally reinforced, apsect ratio between 1.0 and 2.0, beam > 16" wide and depth < 30" | 1338.55 | LogNormal | 0.5047 | 5445.51 | Normal | 0.43147 | 9981.57 | Normal | 0.42067 | [6 empty] | 31773.75 | LogNormal | 0.5047 | 74971.73 | Normal | 0.43147 | 177666.14 | Normal | 0.42067
B1042.012b | B1042.012b | Concrete link beam, conventionally reinforced, apsect ratio between 2.0 and 4.0, beam > 16" wide and depth < 30" | 810.12 | LogNormal | 0.57317 | 5443.52 | Normal | 0.43352 | 8660.97 | Normal | 0.44512 | [6 empty] | 19219.92 | LogNormal | 0.57317 | 74852.2 | Normal | 0.43352 | 158221.52 | Normal | 0.44512
B1042.021a | B1042.021a | Concrete link beam, diagonally reinforced, aspect ratio between 1.0 and 2.0, beam > 24" wide and depth < 30" | 1338.55 | LogNormal | 0.5047 | 5445.51 | Normal | 0.43147 | 10201.48 | Normal | 0.41858 | [6 empty] | 31773.75 | LogNormal | 0.5047 | 74971.73 | Normal | 0.43147 | 181580.36 | Normal | 0.41858
B1042.021b | B1042.021b | Concrete link beam, diagonally reinforced, aspect ratio between 2.0 and 4.0, beam > 24" wide and depth < 30" | 810.12 | LogNormal | 0.57317 | 5443.52 | Normal | 0.43352 | 8864.42 | Normal | 0.44268 | [6 empty] | 19219.92 | LogNormal | 0.57317 | 74852.2 | Normal | 0.43352 | 161938.26 | Normal | 0.44268
B1042.022a | B1042.022a | Concrete link beam, conventionally reinforced, aspect ratio between 1.0 and 2.0, beam > 24" wide and depth < 30" | 1338.55 | LogNormal | 0.5047 | 5445.51 | Normal | 0.43147 | 10201.48 | Normal | 0.41858 | [6 empty] | 31773.75 | LogNormal | 0.5047 | 74971.73 | Normal | 0.43147 | 181580.36 | Normal | 0.41858
B1042.022b | B1042.022b | Concrete link beam, conventionally reinforced, aspect ratio between 2.0 and 4.0, beam > 24" wide and depth < 30" | 810.12 | LogNormal | 0.57317 | 5443.52 | Normal | 0.43352 | 8864.42 | Normal | 0.44268 | [6 empty] | 19219.92 | LogNormal | 0.57317 | 74852.2 | Normal | 0.43352 | 161938.26 | Normal | 0.44268
B1051.001 | B1051.001 | Ordinary reinforced masonry walls with partially grouted cells, shear dominated, 4" to 6"' thick, up to 12 foot tall | 501 | Normal | 0.27116 | 1289 | Normal | 0.28715 | [9 empty] | 11754 | Normal | 0.27116 | 26406 | Normal | 0.28715
B1051.002 | B1051.002 | Ordinary reinforced masonry walls with partially grouted cells, shear dominated, 4" to 6"' thick, greater than 12 foot tall | 1077.75 | LogNormal | 0.26273 | 4349.25 | Normal | 0.28117 | [9 empty] | 25384.5 | LogNormal | 0.26273 | 65315.25 | Normal | 0.28117
B1051.003 | B1051.003 | Ordinary reinforced masonry walls with partially grouted cells, 4" to 6" thick, flexure dominated up to 12' tall | 118 | LogNormal | 0.437 | 501 | Normal | 0.27116 | 1289 | Normal | 0.28715 | [6 empty] | 2794 | LogNormal | 0.437 | 11754 | Normal | 0.27116 | 26406 | Normal | 0.28715
B1051.004 | B1051.004 | Ordinary reinforced masonry walls with partially grouted cells, 4" to 6" thick, flexure dominated greater than 12' tall | 265.5 | LogNormal | 0.437 | 1077.75 | LogNormal | 0.26273 | 4349.25 | Normal | 0.28117 | [6 empty] | 6286.5 | LogNormal | 0.437 | 25384.5 | LogNormal | 0.26273 | 65315.25 | Normal | 0.28117
B1051.011 | B1051.011 | Ordinary reinforced masonry walls with partially grouted cells, shear dominated, 8" to 12"' thick, up to 12 foot tall | 562 | Normal | 0.26978 | 3124 | Normal | 0.28634 | [9 empty] | 13192 | Normal | 0.26978 | 46080 | Normal | 0.28634
B1051.012 | B1051.012 | Ordinary reinforced masonry walls with partially grouted cells, shear dominated, 8" to 12"' thick, greater than 12 foot tall | 1215 | LogNormal | 0.26177 | 6979.5 | Normal | 0.27993 | [9 empty] | 28620 | LogNormal | 0.26177 | 102615.75 | Normal | 0.27993
B1051.013 | B1051.013 | Ordinary reinforced masonry walls with partially grouted cells, 8" to 12" thick, flexure dominated up to 12' tall | 118 | LogNormal | 0.437 | 562 | Normal | 0.26978 | 3124 | Normal | 0.28634 | [6 empty] | 2794 | LogNormal | 0.437 | 13192 | Normal | 0.26978 | 46080 | Normal | 0.28634
B1051.014 | B1051.014 | Ordinary reinforced masonry walls with partially grouted cells, 8" to 12" thick, flexure dominated greater than 12' tall | 265.5 | LogNormal | 0.437 | 1215 | LogNormal | 0.26177 | 6979.5 | Normal | 0.27993 | [6 empty] | 6286.5 | LogNormal | 0.437 | 28620 | LogNormal | 0.26177 | 102615.75 | Normal | 0.27993
B1051.021 | B1051.021 | Ordinary reinforced masonry walls with partially grouted cells, shear dominated, 16" thick, up to 12 foot tall | 623 | Normal | 0.26853 | 3852 | Normal | 0.27961 | [9 empty] | 14631 | Normal | 0.26853 | 56354 | Normal | 0.27961
B1051.022 | B1051.022 | Ordinary reinforced masonry walls with partially grouted cells, shear dominated,16"' thick, greater than 12 foot tall | 1350 | LogNormal | 0.26154 | 8617.5 | Normal | 0.27455 | [9 empty] | 31855.5 | LogNormal | 0.26154 | 125732.25 | Normal | 0.27455
B1051.023 | B1051.023 | Ordinary reinforced masonry walls with partially grouted cells, 16" thick, flexure dominated up to 12' tall | 118 | LogNormal | 0.437 | 623 | Normal | 0.26853 | 3852 | Normal | 0.27961 | [6 empty] | 2794 | LogNormal | 0.437 | 14631 | Normal | 0.26853 | 56354 | Normal | 0.27961
B1051.024 | B1051.024 | Ordinary reinforced masonry walls with partially grouted cells, 16" thick, flexure dominated greater than 12' tall | 265.5 | LogNormal | 0.437 | 1350 | LogNormal | 0.26154 | 8617.5 | Normal | 0.27455 | [6 empty] | 6286.5 | LogNormal | 0.437 | 31855.5 | LogNormal | 0.26154 | 125732.25 | Normal | 0.27455
B1052.001 | B1052.001 | Special reinforced masonry walls with fully grouted cells, 8" or 12" thick, shear dominated, up t o12' tall | 461 | Normal | 0.27379 | 3416 | Normal | 0.28091 | [9 empty] | 10795 | Normal | 0.27379 | 50189 | Normal | 0.28091
B1052.002 | B1052.002 | Special reinforced masonry walls with fully grouted cells, 8" or 12" thick, shear dominated, greater than 12' tall | 987.75 | LogNormal | 0.26462 | 7634.25 | Normal | 0.27828 | [9 empty] | 23226.75 | LogNormal | 0.26462 | 111863.25 | Normal | 0.27828
B1052.003 | B1052.003 | Special reinforced masonry walls with fully grouted cells, 8" to 12" thick, flexure dominated up to 12' tall | 118 | LogNormal | 0.437 | 461 | Normal | 0.27379 | 3416 | Normal | 0.28091 | [6 empty] | 2794 | LogNormal | 0.437 | 10795 | Normal | 0.27379 | 50189 | Normal | 0.28091
B1052.004 | B1052.004 | Special reinforced masonry walls with fully grouted cells, 8" to 12" thick, flexure dominated greater than 12' tall | 265.5 | LogNormal | 0.437 | 987.75 | LogNormal | 0.26462 | 7634.25 | Normal | 0.27828 | [6 empty] | 6286.5 | LogNormal | 0.437 | 23226.75 | LogNormal | 0.26462 | 111863.25 | Normal | 0.27828
B1052.011 | B1052.011 | Special reinforced masonry walls with fully grouted cells, 16" thick, shear dominated, up to 12' tall | 521 | Normal | 0.27215 | 4289 | Normal | 0.27467 | [9 empty] | 12234 | Normal | 0.27215 | 62518 | Normal | 0.27467
B1052.012 | B1052.012 | Special reinforced masonry walls with fully grouted cells, 16" thick, shear dominated, greater than 12' tall | 1122.75 | LogNormal | 0.26344 | 9600.75 | Normal | 0.27272 | [9 empty] | 26462.25 | LogNormal | 0.26344 | 139603.5 | Normal | 0.27272
B1052.013 | B1052.013 | Special reinforced masonry walls with fully grouted cells, 16" thick, flexure dominated up to 12' tall | 118 | LogNormal | 0.437 | 521 | Normal | 0.27215 | 4289 | Normal | 0.27467 | [6 empty] | 2794 | LogNormal | 0.437 | 12234 | Normal | 0.27215 | 62518 | Normal | 0.27467
B1052.014 | B1052.014 | Special reinforced masonry walls with fully grouted cells, 16" thick, flexure dominated greater than 12' tall | 265.5 | LogNormal | 0.437 | 1122.75 | LogNormal | 0.26344 | 9600.75 | Normal | 0.27272 | [6 empty] | 6286.5 | LogNormal | 0.437 | 26462.25 | LogNormal | 0.26344 | 139603.5 | Normal | 0.27272
B1061.001a | B1061.001a | Cold formed steel walls with wood structural panel sheathing, interior - gypsum board | 1773 | LogNormal | 0.40369 | 1911 | LogNormal | 0.46953 | 2485 | Normal | 0.27304 | [6 empty] | 19180 | LogNormal | 0.40369 | 21960 | LogNormal | 0.46953 | 39329 | Normal | 0.27304
B1061.001b | B1061.001b | Cold formed steel walls with wood structural panel sheathing, exterior - stucco one side | 2004 | LogNormal | 0.32717 | 2818 | LogNormal | 0.35424 | 3400 | Normal | 0.26942 | [6 empty] | 21166 | LogNormal | 0.32717 | 30520 | LogNormal | 0.35424 | 48121 | Normal | 0.26942
B1061.011a | B1061.011a | Cold formed steel walls with flat strap X-bracing, interior - gypsum board | 1954 | LogNormal | 0.34681 | 2326 | Normal | 0.26827 | [9 empty] | 25284 | LogNormal | 0.34681 | 36474 | Normal | 0.26827
B1061.011b | B1061.011b | Cold formed steel walls with flat strap X-bracing, exterior - stucco one side | 2108 | LogNormal | 0.31954 | 3296 | LogNormal | 0.28231 | [9 empty] | 27384 | LogNormal | 0.31954 | 46493 | LogNormal | 0.28231
B1061.021a | B1061.021a | Cold formed steel walls with 22 or 31 mil steel sheathing, interior - gypsum board | 1773 | LogNormal | 0.40369 | 2236 | Normal | 0.42087 | [9 empty] | 19180 | LogNormal | 0.40369 | 31186 | Normal | 0.42087
B1061.021b | B1061.021b | Cold formed steel walls with 22 or 31 mil steel sheathing, exterior - stucco one side | 2002 | LogNormal | 0.37556 | 3138 | LogNormal | 0.30222 | [9 empty] | 21121 | LogNormal | 0.37556 | 39672 | LogNormal | 0.30222
B1071.001 | B1071.001 | Light framed wood walls with structural panel sheathing, gypsum wallboard no hold-downs | 1764 | LogNormal | 0.35828 | 1904 | LogNormal | 0.44577 | 2210 | Normal | 0.27304 | [6 empty] | 18910 | LogNormal | 0.35828 | 21750 | LogNormal | 0.44577 | 30904 | Normal | 0.27304
B1071.012 | B1071.002 | Light framed wood walls with structural panel sheathing, stucco, hold-downs | 2377 | LogNormal | 0.31324 | 1995 | LogNormal | 0.33029 | 2988 | LogNormal | 0.2752 | [6 empty] | 24085 | LogNormal | 0.31324 | 20870 | LogNormal | 0.33029 | 38737 | LogNormal | 0.2752
B1071.011 | B1071.011 | Light framed wood walls with structural panel sheathing, stucco no hold-downs | 1764 | LogNormal | 0.35828 | 1904 | LogNormal | 0.44577 | 2210 | Normal | 0.27304 | [6 empty] | 18910 | LogNormal | 0.35828 | 21750 | LogNormal | 0.44577 | 30904 | Normal | 0.27304
B1071.002 | B1071.021 | Light framed wood walls with structural panel sheathing, gypsum wallboard and hold-downs | 2377 | LogNormal | 0.31324 | 1995 | LogNormal | 0.33029 | 3001 | LogNormal | 0.26225 | [6 empty] | 24085 | LogNormal | 0.31324 | 20870 | LogNormal | 0.33029 | 39073 | LogNormal | 0.26225
B1071.031 | B1071.031 | Wood walls with diagonal let-in bracing | 2184 | Normal | 0.27129 | [12 empty] | 30130 | Normal | 0.27129
B1071.041 | B1071.041 | Exterior Wall - Type: Gypsum with wood studs, Full Height, Fixed Below, Fixed Above | 234 | Normal | 0.52233 | 663 | Normal | 0.54646 | 35321 | LogNormal | 0.26811 | [6 empty] | 5603 | Normal | 0.52233 | 16562 | Normal | 0.54646 | 341224 | LogNormal | 0.26811
B2011.001a | B2011.001a | Exterior Wall - Cold formed steel walls with wood structural panel sheathing, interior - gypsum board | 1773 | LogNormal | 0.40369 | 1911 | LogNormal | 0.46953 | 2485 | Normal | 0.27304 | [6 empty] | 19180 | LogNormal | 0.40369 | 21960 | LogNormal | 0.46953 | 39329 | Normal | 0.27304
B2011.001b | B2011.001b | Exterior Wall - Cold formed steel walls with wood structural panel sheathing, exterior - stucco one side | 2004 | LogNormal | 0.32717 | 2818 | LogNormal | 0.35424 | 3400 | Normal | 0.26942 | [6 empty] | 21166 | LogNormal | 0.32717 | 30520 | LogNormal | 0.35424 | 48121 | Normal | 0.26942
B2011.011a | B2011.011a | Exterior Wall - Cold formed steel walls with flat strap X-bracing, interior - gypsum board | 1954 | LogNormal | 0.34681 | 2326 | Normal | 0.26827 | [9 empty] | 25284 | LogNormal | 0.34681 | 36474 | Normal | 0.26827
B2011.011b | B2011.011b | Exterior Wall - Cold formed steel walls with flat strap X-bracing, exterior - stucco one side | 2108 | LogNormal | 0.31954 | 3296 | LogNormal | 0.28231 | [9 empty] | 27384 | LogNormal | 0.31954 | 46493 | LogNormal | 0.28231
B2011.021a | B2011.021a | Exterior Wall - Cold formed steel walls with 22 or 31 mil steel sheathing, interior - gypsum board | 1773 | LogNormal | 0.40369 | 2236 | Normal | 0.42087 | [9 empty] | 19180 | LogNormal | 0.40369 | 31186 | Normal | 0.42087
B2011.021b | B2011.021b | Exterior Wall - Cold formed steel walls with 22 or 31 mil steel sheathing, exterior - stucco one side | 2002 | LogNormal | 0.37556 | 3138 | LogNormal | 0.30222 | [9 empty] | 21121 | LogNormal | 0.37556 | 39672 | LogNormal | 0.30222
B2011.101 | B2011.101 | Exterior Wall - Light framed wood walls with structural panel sheathing, gypsum wallboard no hold-downs | 1764 | LogNormal | 0.35828 | 1904 | LogNormal | 0.44577 | 2210 | Normal | 0.27304 | [6 empty] | 18910 | LogNormal | 0.35828 | 21750 | LogNormal | 0.44577 | 30904 | Normal | 0.27304
B2011.102 | B2011.102 | Exterior Wall - Light framed wood walls with structural panel sheathing, stucco, hold-downs | 2377 | LogNormal | 0.31324 | 1995 | LogNormal | 0.33029 | 2988 | LogNormal | 0.2752 | [6 empty] | 24085 | LogNormal | 0.31324 | 20870 | LogNormal | 0.33029 | 38737 | LogNormal | 0.2752
B2011.111 | B2011.111 | Exterior Wall - Light framed wood walls with structural panel sheathing, stucco no hold-downs | 1764 | LogNormal | 0.35828 | 1904 | LogNormal | 0.44577 | 2210 | Normal | 0.27304 | [6 empty] | 18910 | LogNormal | 0.35828 | 21750 | LogNormal | 0.44577 | 30904 | Normal | 0.27304
B2011.121 | B2011.121 | Exterior Wall - Light framed wood walls with structural panel sheathing, gypsum wallboard and hold-downs | 2377 | LogNormal | 0.31324 | 1995 | LogNormal | 0.33029 | 3001 | LogNormal | 0.26225 | [6 empty] | 24085 | LogNormal | 0.31324 | 20870 | LogNormal | 0.33029 | 39073 | LogNormal | 0.26225
B2011.131 | B2011.131 | Exterior Wall - Wood walls with diagonal let-in bracing | 2184 | Normal | 0.27129 | [12 empty] | 30130 | Normal | 0.27129
B2011.201a | B2011.201a | Precast Concrete Panels 4.5 inches thick - in plane deformation | 11544 | Normal | 0.31683 | 57712.2 | Normal | 0.31683 | [9 empty] | 163991.1 | Normal | 0.31683 | 819951.6 | Normal | 0.31683
B2011.201b | B2011.201b | Precast Concrete Panels 4.5 inches thick - out of plane deformation | 57712.2 | Normal | 0.31683 | [12 empty] | 819951.6 | Normal | 0.31683
B2022.001 | B2022.001 | Curtain Walls - Generic Midrise Stick-Built Curtain wall, Config: Monolithic, Lamination: Unknown, Glass Type: Unknown, Details: Aspect ratio = 6:5, Other details Unknown | 406.2 | LogNormal | 0.30054 | 406.2 | LogNormal | 0.30054 | [9 empty] | 9437.4 | LogNormal | 0.30054 | 9437.4 | LogNormal | 0.30054
B2022.002 | B2022.002 | Curtain Walls - Generic Midrise Stick-Built Curtain wall, Config: Insulating Glass Units (dual pane), Lamination: Unknown, Glass Type: Unknown, Details: Aspect ratio = 6:5, Other details Unknown | 1024.8 | LogNormal | 0.27666 | 1024.8 | LogNormal | 0.27666 | [9 empty] | 23784 | LogNormal | 0.27666 | 23784 | LogNormal | 0.27666
B2022.011 | B2022.011 | Midrise stick-built curtain wall, Config: Asymmetric insulating glass units (dual-pane, unequal-thickness IGU), Lamination: Laminated, Glass Type: Annealed, Details: 1/4 in. (6 mm) inner AN / 1/2 in. (13 mm) outer AN LAM (0.030 PVB) IGU; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 6:5 sealant = dry | 406.2 | LogNormal | 0.30054 | 1024.8 | LogNormal | 0.27666 | 1024.8 | LogNormal | 0.27666 | [6 empty] | 9437.4 | LogNormal | 0.30054 | 23784 | LogNormal | 0.27666 | 23784 | LogNormal | 0.27666
B2022.021 | B2022.021 | Midrise stick-built curtain wall, Config: Monolithic, Lamination: Laminated, Glass Type: Annealed, Details: 1/4 in. (6 mm) AN LAM (0.030 PVB); glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 6:5 sealant = dry | 1024.8 | LogNormal | 0.27666 | 1024.8 | LogNormal | 0.27666 | [9 empty] | 23784 | LogNormal | 0.27666 | 23784 | LogNormal | 0.27666
B2022.022 | B2022.022 | Midrise stick-built curtain wall, Config: Monolithic, Lamination: Laminated, Glass Type: Annealed, Details: 1/4 in. (6 mm) AN laminated, 2-sided SSG, Center Panel; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 6:5 sealant = wet | 406.2 | LogNormal | 0.30054 | 406.2 | LogNormal | 0.30054 | [9 empty] | 9437.4 | LogNormal | 0.30054 | 9437.4 | LogNormal | 0.30054
B2022.023 | B2022.023 | Midrise stick-built curtain wall, Config: Monolithic, Lamination: Laminated, Glass Type: Annealed, Details: 1/4 in. (6 mm) AN laminated, 2-sided SSG, Outside Panel; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 6:5 sealant = wet | 406.2 | LogNormal | 0.30054 | 406.2 | LogNormal | 0.30054 | [9 empty] | 9437.4 | LogNormal | 0.30054 | 9437.4 | LogNormal | 0.30054
B2022.031 | B2022.031 | Midrise stick-built curtain wall, Config: Monolithic, Lamination: Not laminated, Glass Type: Annealed, Details: 1/4 in. (6 mm) AN monolithic; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 6:5 sealant = dry | 406.2 | LogNormal | 0.30054 | 406.2 | LogNormal | 0.30054 | [9 empty] | 9437.4 | LogNormal | 0.30054 | 9437.4 | LogNormal | 0.30054
B2022.032 | B2022.032 | Midrise stick-built curtain wall, Config: Monolithic, Lamination: Not laminated, Glass Type: Annealed, Details: 1/4 in. (6 mm) AN monolithic; glass-frame clearance = 0 in. (0 mm); aspect ratio = 6:5 sealant = dry | 406.2 | LogNormal | 0.30054 | 406.2 | LogNormal | 0.30054 | [9 empty] | 9437.4 | LogNormal | 0.30054 | 9437.4 | LogNormal | 0.30054
B2022.033 | B2022.033 | Midrise stick-built curtain wall, Config: Monolithic, Lamination: Not laminated, Glass Type: Annealed, Details: 1/4 in. (6 mm) AN monolithic; glass-frame clearance = 0.13 in. (3 mm); aspect ratio = 6:5 sealant = dry | 406.2 | LogNormal | 0.27666 | 406.2 | LogNormal | 0.27666 | [9 empty] | 9437.4 | LogNormal | 0.27666 | 9437.4 | LogNormal | 0.27666
B2022.034 | B2022.034 | Midrise stick-built curtain wall, Config: Monolithic, Lamination: Not laminated, Glass Type: Annealed, Details: 1/4 in. (6 mm) AN monolithic; glass-frame clearance = 0.25 in. (6 mm); aspect ratio = 6:5 sealant = dry | 406.2 | LogNormal | 0.27666 | 406.2 | LogNormal | 0.27666 | [9 empty] | 9437.4 | LogNormal | 0.27666 | 9437.4 | LogNormal | 0.27666
B2022.035 | B2022.035 | Midrise stick-built curtain wall, Config: Monolithic, Lamination: Not laminated, Glass Type: Annealed, Details: 1/4 in. (6 mm) AN monolithic; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 2:1 sealant = dry | 649.92 | LogNormal | 0.27666 | 649.92 | LogNormal | 0.27666 | [9 empty] | 15099.84 | LogNormal | 0.27666 | 15099.84 | LogNormal | 0.27666
B2022.036 | B2022.036 | Midrise stick-built curtain wall, Config: Monolithic, Lamination: Not laminated, Glass Type: Annealed, Details: 1/4 in. (6 mm) AN monolithic; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 1:2 sealant = dry | 649.92 | LogNormal | 0.27666 | 649.92 | LogNormal | 0.27666 | [9 empty] | 15099.84 | LogNormal | 0.27666 | 15099.84 | LogNormal | 0.27666
B2022.037 | B2022.037 | Midrise stick-built curtain wall, Config: Monolithic, Lamination: Not laminated, Glass Type: Annealed, Details: 1/4 in. (6 mm) AN monolithic, 2-sided SSG, Center Panel; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 6:5 sealant = wet | 406.2 | LogNormal | 0.27666 | 406.2 | LogNormal | 0.27666 | [9 empty] | 9437.4 | LogNormal | 0.27666 | 9437.4 | LogNormal | 0.27666
B2022.038 | B2022.038 | Midrise stick-built curtain wall, Config: Monolithic, Lamination: Not laminated, Glass Type: Annealed, Details: 1/4 in. (6 mm) AN monolithic, 2-sided SSG, Outside Panel; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 6:5 sealant = wet | 406.2 | LogNormal | 0.27666 | 406.2 | LogNormal | 0.27666 | [9 empty] | 9437.4 | LogNormal | 0.27666 | 9437.4 | LogNormal | 0.27666
B2022.039 | B2022.039 | Midrise stick-built curtain wall, Config: Monolithic, Lamination: Not laminated, Glass Type: Annealed, Details: 1/4 in. (6 mm) AN monolithic; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 6:5 sealant = dry | 406.2 | LogNormal | 0.27666 | 406.2 | LogNormal | 0.27666 | [9 empty] | 9437.4 | LogNormal | 0.27666 | 9437.4 | LogNormal | 0.27666
B2022.040 | B2022.040 | Midrise stick-built curtain wall, Config: Monolithic, Lamination: Not laminated, Glass Type: Annealed, Details: 1/4 in. (6 mm) AN monolithic; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 2:1 sealant = dry | 406.2 | LogNormal | 0.27666 | 406.2 | LogNormal | 0.27666 | [9 empty] | 9437.4 | LogNormal | 0.27666 | 9437.4 | LogNormal | 0.27666
B2022.041 | B2022.041 | Midrise stick-built curtain wall, Config: Monolithic, Lamination: Not laminated, Glass Type: Annealed, Details: 1/4 in. (6 mm) AN monolithic; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 1:2 sealant = dry | 406.2 | LogNormal | 0.27666 | 406.2 | LogNormal | 0.27666 | [9 empty] | 9437.4 | LogNormal | 0.27666 | 9437.4 | LogNormal | 0.27666
B2022.051 | B2022.051 | Midrise stick-built curtain wall, Config: Monolithic, Lamination: Not laminated, Glass Type: Full tempered, Details: 1/4 in. (6 mm) FT monolithic, 2-sided SSG, Center Panel; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 6:5 sealant = wet | 406.2 | LogNormal | 0.27666 | 406.2 | LogNormal | 0.27666 | [9 empty] | 9437.4 | LogNormal | 0.27666 | 9437.4 | LogNormal | 0.27666
B2022.052 | B2022.052 | Midrise stick-built curtain wall, Config: Monolithic, Lamination: Not laminated, Glass Type: Full tempered, Details: 1/4 in. (6 mm) FT monolithic, 2-sided SSG, Outside Panel; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 6:5 sealant = wet | 406.2 | LogNormal | 0.27666 | 406.2 | LogNormal | 0.27666 | [9 empty] | 9437.4 | LogNormal | 0.27666 | 9437.4 | LogNormal | 0.27666
B2022.053 | B2022.053 | Midrise stick-built curtain wall, Config: Monolithic, Lamination: Not laminated, Glass Type: Full tempered, Details: 1/4 in. (6 mm) FT monolithic, Seamed Edge; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 6:5 sealant = dry | 406.2 | LogNormal | 0.27666 | 406.2 | LogNormal | 0.27666 | [9 empty] | 9437.4 | LogNormal | 0.27666 | 9437.4 | LogNormal | 0.27666
B2022.054 | B2022.054 | Midrise stick-built curtain wall, Config: Monolithic, Lamination: Not laminated, Glass Type: Full tempered, Details: 1/4 in. (6 mm) FT monolithic, Polished Edge; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 6:5 sealant = dry | 406.2 | LogNormal | 0.27666 | 406.2 | LogNormal | 0.27666 | [9 empty] | 9437.4 | LogNormal | 0.27666 | 9437.4 | LogNormal | 0.27666
B2022.061 | B2022.061 | Midrise stick-built curtain wall, Config: Monolithic, Lamination: Not laminated, Glass Type: Heat strengthened, Details: 1/4 in. (6 mm) HS monolithic; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 6:5 sealant = dry | 406.2 | LogNormal | 0.27666 | 406.2 | LogNormal | 0.27666 | [9 empty] | 9437.4 | LogNormal | 0.27666 | 9437.4 | LogNormal | 0.27666
B2022.071 | B2022.071 | Midrise stick-built curtain wall, Config: Symmetric insulating glass units (dual-pane, equal-thickness IGU), Lamination: Laminated, Glass Type: Annealed, Details: 1/4 in. (6 mm) inner AN / 1/4 in. (6 mm) outer AN LAM (0.030 PVB) IGU; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 6:5 sealant = dry | 406.2 | LogNormal | 0.30054 | 1024.8 | LogNormal | 0.27666 | 1024.8 | LogNormal | 0.27666 | [6 empty] | 9437.4 | LogNormal | 0.30054 | 23784 | LogNormal | 0.27666 | 23784 | LogNormal | 0.27666
B2022.072 | B2022.072 | Midrise stick-built curtain wall, Config: Symmetric insulating glass units (dual-pane, equal-thickness IGU), Lamination: Laminated, Glass Type: Annealed, Details: 1/4 in. (6 mm) inner AN / 1/4 in. (6 mm) outer AN LAM (0.060 PVB) IGU; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 6:5 sealant = dry | 406.2 | LogNormal | 0.30054 | 1024.8 | LogNormal | 0.27666 | 1024.8 | LogNormal | 0.27666 | [6 empty] | 9437.4 | LogNormal | 0.30054 | 23784 | LogNormal | 0.27666 | 23784 | LogNormal | 0.27666
B2022.081 | B2022.081 | Midrise stick-built curtain wall, Config: Symmetric insulating glass units (dual-pane, equal-thickness IGU), Lamination: Not laminated, Glass Type: Annealed, Details: 1 in. (25 mm) AN insulating glass unit (IGU) [1/4 in. (6 mm) inner and outer panes]; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 6:5 sealant = dry | 1024.8 | LogNormal | 0.27666 | 1024.8 | LogNormal | 0.27666 | [9 empty] | 23784 | LogNormal | 0.27666 | 23784 | LogNormal | 0.27666
B2022.082 | B2022.082 | Midrise stick-built curtain wall, Config: Symmetric insulating glass units (dual-pane, equal-thickness IGU), Lamination: Not laminated, Glass Type: Annealed, Details: 1 in. (25 mm) AN IGU [1/4 in. (6 mm) inner and outer panes]; glass-frame clearance = 0.25 in. (6 mm); aspect ratio = 6:5 sealant = dry | 1024.8 | LogNormal | 0.27666 | 1024.8 | LogNormal | 0.27666 | [9 empty] | 23784 | LogNormal | 0.27666 | 23784 | LogNormal | 0.27666
B2022.083 | B2022.083 | Midrise stick-built curtain wall, Config: Symmetric insulating glass units (dual-pane, equal-thickness IGU), Lamination: Not laminated, Glass Type: Annealed, Details: 1 in. (25 mm) AN IGU [1/4 in. (6 mm) inner and outer panes], 2-sided SSG, Center Panel; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 6:5 sealant = wet | 406.2 | LogNormal | 0.30054 | 1024.8 | LogNormal | 0.27666 | 1024.8 | LogNormal | 0.27666 | [6 empty] | 9437.4 | LogNormal | 0.30054 | 23784 | LogNormal | 0.27666 | 23784 | LogNormal | 0.27666
B2022.084 | B2022.084 | Midrise stick-built curtain wall, Config: Symmetric insulating glass units (dual-pane, equal-thickness IGU), Lamination: Not laminated, Glass Type: Annealed, Details: 1 in. (25 mm) AN IGU [1/4 in. (6 mm) inner and outer panes], 2-sided SSG, Outside Panel; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 6:5 sealant = wet | 406.2 | LogNormal | 0.30054 | 1024.8 | LogNormal | 0.27666 | 1024.8 | LogNormal | 0.27666 | [6 empty] | 9437.4 | LogNormal | 0.30054 | 23784 | LogNormal | 0.27666 | 23784 | LogNormal | 0.27666
B2022.091 | B2022.091 | Midrise stick-built curtain wall, Config: Symmetric insulating glass units (dual-pane, equal-thickness IGU), Lamination: Not laminated, Glass Type: Full tempered, Details: 1 in. (25 mm) FT IGU [1/4 in. (6 mm) inner and outer panes]; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 6:5 sealant = dry | 406.2 | LogNormal | 0.30054 | 1024.8 | LogNormal | 0.27666 | 1024.8 | LogNormal | 0.27666 | [6 empty] | 9437.4 | LogNormal | 0.30054 | 23784 | LogNormal | 0.27666 | 23784 | LogNormal | 0.27666
B2022.101 | B2022.101 | Midrise stick-built curtain wall, Config: Symmetric insulating glass units (dual-pane, equal-thickness IGU), Lamination: Not laminated, Glass Type: Heat strengthened, Details: 1 in. (25 mm) HS IGU [1/4 in. (6 mm) inner and outer panes]; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 6:5 sealant = dry | 406.2 | LogNormal | 0.30054 | 1024.8 | LogNormal | 0.27666 | 1024.8 | LogNormal | 0.27666 | [6 empty] | 9437.4 | LogNormal | 0.30054 | 23784 | LogNormal | 0.27666 | 23784 | LogNormal | 0.27666
B2022.201 | B2022.201 | Curtain Walls - Unitized curtain wall (also generic unitized curtain wall), Config: Symmetric insulating glass units (dual-pane, equal-thickness IGU), Lamination: Not laminated, Glass Type: Full tempered, Details: 1-1/4 in. (32 mm) FT IGU [1/4 in. (6 mm) inner and outer panes], 4-sided SSG, VHBTM SGTTM; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = Varies sealant = wet | 406.2 | LogNormal | 0.30054 | 1024.8 | LogNormal | 0.27666 | 1024.8 | LogNormal | 0.27666 | [6 empty] | 9437.4 | LogNormal | 0.30054 | 23784 | LogNormal | 0.27666 | 23784 | LogNormal | 0.27666
B2023.001 | B2023.001 | Generic Storefront, Config: Monolithic, Lamination: Unknown, Glass Type: Unknown, Details: Aspect ratio = 6:5, Other details Unknown | 406.2 | LogNormal | 0.37694 | 1024.8 | LogNormal | 0.30054 | 1024.8 | LogNormal | 0.30054 | [6 empty] | 9437.4 | LogNormal | 0.37694 | 23784 | LogNormal | 0.30054 | 23784 | LogNormal | 0.30054
B2023.002 | B2023.002 | Generic Storefront, Config: IGU, Lamination: Unknown, Glass Type: Unknown, Details: Aspect ratio = 6:5, Other details Unknown | 406.2 | LogNormal | 0.37694 | 1024.8 | LogNormal | 0.30054 | 1024.8 | LogNormal | 0.30054 | [6 empty] | 9437.4 | LogNormal | 0.37694 | 23784 | LogNormal | 0.30054 | 23784 | LogNormal | 0.30054
B2023.011 | B2023.011 | Storefront, Config: Monolithic, Lamination: Laminated, Glass Type: Annealed, Details: 1/4 in. (6 mm) AN LAM (0.030 PVB); glass-frame clearance = 0.41 in. (10 mm); aspect ratio = 6:5 sealant = dry | 406.2 | LogNormal | 0.37694 | 1024.8 | LogNormal | 0.30054 | 1024.8 | LogNormal | 0.30054 | [6 empty] | 9437.4 | LogNormal | 0.37694 | 23784 | LogNormal | 0.30054 | 23784 | LogNormal | 0.30054
B2023.021 | B2023.021 | Storefront, Config: Monolithic, Lamination: Not laminated, Glass Type: Annealed, Details: 1/4 in. (6 mm) AN monolithic; glass-frame clearance = 0.41 in. (10 mm); aspect ratio = 6:5 sealant = dry | 406.2 | LogNormal | 0.37694 | 1024.8 | LogNormal | 0.30054 | 1024.8 | LogNormal | 0.30054 | [6 empty] | 9437.4 | LogNormal | 0.37694 | 23784 | LogNormal | 0.30054 | 23784 | LogNormal | 0.30054
B2023.031 | B2023.031 | Storefront, Config: Monolithic, Lamination: Not laminated, Glass Type: Full tempered, Details: 3/8 in. (10 mm) FT monolithic, Planar Specimen; glass-frame clearance = 0.5 in. (13 mm); aspect ratio = 1.93:1 sealant = wet | 1024.8 | LogNormal | 0.30054 | 1024.8 | LogNormal | 0.30054 | [9 empty] | 23784 | LogNormal | 0.30054 | 23784 | LogNormal | 0.30054
B2023.032 | B2023.032 | Storefront, Config: Monolithic, Lamination: Not laminated, Glass Type: Full tempered, Details: 3/8 in. (10 mm) FT monolithic, Corner Cond. Specimen, in-plane; glass-frame clearance = 0.5 in. (13 mm); aspect ratio = 1.93:1 sealant = wet | 1024.8 | LogNormal | 0.30054 | 1024.8 | LogNormal | 0.30054 | [9 empty] | 23784 | LogNormal | 0.30054 | 23784 | LogNormal | 0.30054
B2023.033 | B2023.033 | Storefront, Config: Monolithic, Lamination: Not laminated, Glass Type: Full tempered, Details: 3/8 in. (10 mm) FT monolithic, Corner Cond. Specimen, combined; glass-frame clearance = 0.5 in. (13 mm); aspect ratio = 1.93:1 sealant = wet | 406.2 | LogNormal | 0.30054 | 1024.8 | LogNormal | 0.30054 | [9 empty] | 9437.4 | LogNormal | 0.30054 | 23784 | LogNormal | 0.30054
B2023.034 | B2023.034 | Storefront, Config: Monolithic, Lamination: Not laminated, Glass Type: Full tempered, Details: 3/8 in. (10 mm) FT monolithic, Corner Cond. Specimen, Short side; glass-frame clearance = 0.5 in. (13 mm); aspect ratio = 2.72:1 sealant = wet | 406.2 | LogNormal | 0.30054 | 1024.8 | LogNormal | 0.30054 | [9 empty] | 9437.4 | LogNormal | 0.30054 | 23784 | LogNormal | 0.30054
B2023.041 | B2023.041 | Storefront, Config: Symmetric insulating glass units (dual-pane, equal-thickness IGU), Lamination: Not laminated, Glass Type: Annealed, Details: 1 in. (25 mm) AN IGU; glass-frame clearance = 0.59 in. (15 mm); aspect ratio = 6:5 sealant = dry | 406.2 | LogNormal | 0.37694 | 1024.8 | LogNormal | 0.30054 | 1024.8 | LogNormal | 0.30054 | [6 empty] | 9437.4 | LogNormal | 0.37694 | 23784 | LogNormal | 0.30054 | 23784 | LogNormal | 0.30054
B2023.051 | B2023.051 | Storefront, Config: Symmetric insulating glass units (dual-pane, equal-thickness IGU), Lamination: Not laminated, Glass Type: Full tempered, Details: 1 in. (25 mm) FT IGU [1/4 in. (6 mm) inner and outer panes], Planar Specimen; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 1.89:1 sealant = dry | 1024.8 | LogNormal | 0.27666 | 1024.8 | LogNormal | 0.27666 | [9 empty] | 23784 | LogNormal | 0.27666 | 23784 | LogNormal | 0.27666
B2023.052 | B2023.052 | Storefront, Config: Symmetric insulating glass units (dual-pane, equal-thickness IGU), Lamination: Not laminated, Glass Type: Full tempered, Details: 1 in. (25 mm) FT IGU [1/4 in. (6 mm) inner and outer panes], Corner Cond. Specimen, in-plane; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 1.89:1 sealant = dry | 406.2 | LogNormal | 0.27666 | 1024.8 | LogNormal | 0.27666 | [9 empty] | 9437.4 | LogNormal | 0.27666 | 23784 | LogNormal | 0.27666
B2023.053 | B2023.053 | Storefront, Config: Symmetric insulating glass units (dual-pane, equal-thickness IGU), Lamination: Not laminated, Glass Type: Full tempered, Details: 1 in. (25 mm) FT IGU [1/4 in. (6 mm) inner and outer panes], Corner Cond. Specimen, combined; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 1.89:1 sealant = dry | 406.2 | LogNormal | 0.27666 | 1024.8 | LogNormal | 0.27666 | [9 empty] | 9437.4 | LogNormal | 0.27666 | 23784 | LogNormal | 0.27666
B2023.054 | B2023.054 | Storefront, Config: Symmetric insulating glass units (dual-pane, equal-thickness IGU), Lamination: Not laminated, Glass Type: Full tempered, Details: 1 in. (25 mm) FT IGU [1/4 in. (6 mm) inner and outer panes], Corner Cond. Specimen, Short side; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 2.83:1 sealant = dry | 406.2 | LogNormal | 0.27666 | 1024.8 | LogNormal | 0.27666 | [9 empty] | 9437.4 | LogNormal | 0.27666 | 23784 | LogNormal | 0.27666
B2023.055 | B2023.055 | Storefront, Config: Symmetric insulating glass units (dual-pane, equal-thickness IGU), Lamination: Not laminated, Glass Type: Full tempered, Details: 1 in. (25 mm) FT IGU [1/4 in. (6 mm) inner and outer panes], Planar Specimen; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 1.88:1 sealant = dry | 406.2 | LogNormal | 0.27666 | 1024.8 | LogNormal | 0.27666 | [9 empty] | 9437.4 | LogNormal | 0.27666 | 23784 | LogNormal | 0.27666
B2023.056 | B2023.056 | Storefront, Config: Symmetric insulating glass units (dual-pane, equal-thickness IGU), Lamination: Not laminated, Glass Type: Full tempered, Details: 1 in. (25 mm) FT IGU [1/4 in. (6 mm) inner and outer panes], Corner Cond. Specimen, in-plane; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 1.88:1 sealant = dry | 406.2 | LogNormal | 0.27666 | 1024.8 | LogNormal | 0.27666 | [9 empty] | 9437.4 | LogNormal | 0.27666 | 23784 | LogNormal | 0.27666
B2023.057 | B2023.057 | Storefront, Config: Symmetric insulating glass units (dual-pane, equal-thickness IGU), Lamination: Not laminated, Glass Type: Full tempered, Details: 1 in. (25 mm) FT IGU [1/4 in. (6 mm) inner and outer panes], Corner Cond. Specimen, combined; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 1.88:1 sealant = dry | 406.2 | LogNormal | 0.27666 | 1024.8 | LogNormal | 0.27666 | [9 empty] | 9437.4 | LogNormal | 0.27666 | 23784 | LogNormal | 0.27666
B2023.058 | B2023.058 | Storefront, Config: Symmetric insulating glass units (dual-pane, equal-thickness IGU), Lamination: Not laminated, Glass Type: Full tempered, Details: 1 in. (25 mm) FT IGU [1/4 in. (6 mm) inner and outer panes], Corner Cond. Specimen, Short side; glass-frame clearance = 0.43 in. (11 mm); aspect ratio = 2.82:1 sealant = dry | 406.2 | LogNormal | 0.27666 | 1024.8 | LogNormal | 0.27666 | [9 empty] | 9437.4 | LogNormal | 0.27666 | 23784 | LogNormal | 0.27666
B3011.011 | B3011.011 | Concrete tile roof, tiles secured and compliant with UBC94 | 41 | LogNormal | 0.62808 | 154 | LogNormal | 0.39625 | [9 empty] | 985 | LogNormal | 0.62808 | 3769 | LogNormal | 0.39625
B3011.012 | B3011.012 | Clay tile roof, tiles secured and compliant with UBC94 | 56 | LogNormal | 0.54151 | 213 | LogNormal | 0.44591 | [9 empty] | 1329 | LogNormal | 0.54151 | 5177 | LogNormal | 0.44591
B3011.013 | B3011.013 | Concrete tile roof, unsecured tiles | 24 | LogNormal | 0.68399 | 54 | LogNormal | 0.49834 | [9 empty] | 576 | LogNormal | 0.68399 | 1313 | LogNormal | 0.49834
B3011.014 | B3011.014 | Clay tile roof, unsecured tiles | 40 | LogNormal | 0.57241 | 113 | LogNormal | 0.53157 | [9 empty] | 920 | LogNormal | 0.57241 | 2721 | LogNormal | 0.53157
B3031.001a | B3031.001a | Masonry Chimney - unreinforced, non industrial, above roof 5 ft, replace with masonry | 2662.63 | LogNormal | 0.28817 | 2662.63 | LogNormal | 0.28817 | [9 empty] | 60052.19 | LogNormal | 0.28817 | 60052.19 | LogNormal | 0.28817
B3031.001b | B3031.001b | Masonry Chimney - unreinforced, non industrial, above roof 10 ft, replace with masonry | 4767.74 | LogNormal | 0.30354 | 4767.74 | LogNormal | 0.30354 | [9 empty] | 106732.9 | LogNormal | 0.30354 | 106732.9 | LogNormal | 0.30354
B3031.001c | B3031.001c | Masonry Chimney - unreinforced, non industrial, above roof 15 ft, replace with masonry | 6872.85 | LogNormal | 0.3115 | 6872.85 | LogNormal | 0.3115 | [9 empty] | 153413.62 | LogNormal | 0.3115 | 153413.62 | LogNormal | 0.3115
B3031.002a | B3031.002a | Masonry Chimney - unreinforced, non industrial, above roof 5 ft, replace with framing | 2016.25 | Normal | 0.33363 | 2016.25 | Normal | 0.33364 | [9 empty] | 45398.14 | Normal | 0.33363 | 45398.14 | Normal | 0.33364
B3031.002b | B3031.002b | Masonry Chimney - unreinforced, non industrial, above roof 10 ft, replace with framing | 3474.97 | LogNormal | 0.3042 | 3474.97 | LogNormal | 0.3042 | [9 empty] | 77424.81 | LogNormal | 0.3042 | 77424.81 | LogNormal | 0.3042
B3031.002c | B3031.002c | Masonry Chimney - unreinforced, non industrial, above roof 15 ft, replace with framing | 4933.7 | Normal | 0.29917 | 4933.7 | Normal | 0.29917 | [9 empty] | 109451.48 | Normal | 0.29917 | 109451.48 | Normal | 0.29917
B3041.001 | B3041.001 | Masonry Parapet - unreinforced, unbraced | 200.83 | Normal | 0.35298 | 200.83 | Normal | 0.35298 | [9 empty] | 5398.36 | Normal | 0.35298 | 5398.36 | Normal | 0.35298
C1011.001a | C1011.001a | Wall Partition, Type: Gypsum with metal studs, Full Height, Fixed Below, Fixed Above | 208 | Normal | 0.54243 | 585 | LogNormal | 0.60954 | 13026 | LogNormal | 0.31759 | [6 empty] | 4979 | Normal | 0.54243 | 14963 | LogNormal | 0.60954 | 151970 | LogNormal | 0.31759
C1011.001b | C1011.001b | Wall Partition, Type: Gypsum with metal studs, Partial Height, Fixed Below, Lateral Braced Above | 208 | Normal | 0.54243 | 585 | LogNormal | 0.60954 | 13026 | LogNormal | 0.31759 | [6 empty] | 4979 | Normal | 0.54243 | 14963 | LogNormal | 0.60954 | 151970 | LogNormal | 0.31759
C1011.001c | C1011.001c | Wall Partition, Type: Gypsum with metal studs, Full Height, Fixed Below, Slip Track Above with returns | 78 | Normal | 0.54243 | 234 | LogNormal | 0.60954 | 5213 | LogNormal | 0.31759 | [6 empty] | 1989 | Normal | 0.54243 | 5980 | LogNormal | 0.60954 | 60788 | LogNormal | 0.31759
C1011.001d | C1011.001d | Wall Partition, Type: Gypsum with metal studs, Full Height, Fixed Below, Slip Track Above w/o returns (friction connections) | 104 | Normal | 0.54243 | 299 | LogNormal | 0.60954 | [9 empty] | 2496 | Normal | 0.54243 | 7488 | LogNormal | 0.60954
C1011.011a | C1011.011a | Wall Partition, Type: Gypsum with wood studs, Full Height, Fixed Below, Fixed Above | 234 | Normal | 0.52233 | 663 | Normal | 0.54646 | 35321 | LogNormal | 0.26811 | [6 empty] | 5603 | Normal | 0.52233 | 16562 | Normal | 0.54646 | 341224 | LogNormal | 0.26811
C2011.001a | C2011.001a | Prefabricated steel stair with steel treads and landings with seismic joints that accommodate drift. | 39.53 | LogNormal | 1.021 | 339.59 | LogNormal | 0.63137 | 22330.11 | Normal | 0.46804 | [6 empty] | 940.85 | LogNormal | 1.021 | 8712.46 | LogNormal | 0.63137 | 301678.87 | Normal | 0.46804
C2011.001b | C2011.001b | Prefabricated steel stair with steel treads and landings with no seismic joint. | 39.53 | LogNormal | 1.021 | 339.59 | LogNormal | 0.63137 | 22330.11 | Normal | 0.46804 | [6 empty] | 940.85 | LogNormal | 1.021 | 8712.46 | LogNormal | 0.63137 | 301678.87 | Normal | 0.46804
C2011.011a | C2011.011a | Non-monolithic precast concrete stair assembly with concrete stringers and treads with seismic joints that accommodate drift. | 136.72 | LogNormal | 0.83956 | 725.04 | LogNormal | 0.62182 | 26019.78 | Normal | 0.43936 | [6 empty] | 3233.83 | LogNormal | 0.83956 | 20540.69 | LogNormal | 0.62182 | 352471.24 | Normal | 0.43936
C2011.011b | C2011.011b | Non-monolithic precast concrete stair assembly with concrete stringers and treads with no seismic joint. | 136.72 | LogNormal | 0.83956 | 725.04 | LogNormal | 0.62182 | 26019.78 | Normal | 0.43936 | [6 empty] | 3233.83 | LogNormal | 0.83956 | 20540.69 | LogNormal | 0.62182 | 352471.24 | Normal | 0.43936
C2011.021a | C2011.021a | Monolithic cast-in-place and precast concrete stairs with seismic joints that accommodate drift - replace in kind if replacement is required. | 136.72 | LogNormal | 0.83956 | 725.04 | LogNormal | 0.62182 | 28479.57 | Normal | 0.42461 | [6 empty] | 3233.83 | LogNormal | 0.83956 | 20540.69 | LogNormal | 0.62182 | 386332.81 | Normal | 0.42461
C2011.021b | C2011.021b | Monolithic cast-in-place and precast concrete stairs with no seismic joints - replace in kind if replacement is required. | 136.72 | LogNormal | 0.83956 | 725.04 | LogNormal | 0.62182 | 28479.57 | Normal | 0.42461 | [6 empty] | 3233.83 | LogNormal | 0.83956 | 20540.69 | LogNormal | 0.62182 | 386332.81 | Normal | 0.42461
C2011.021c | C2011.021c | Monolithic cast-in-place and precast concrete stairs with seismic joints that accommodate drift - replace with prefabricated steel stair if replacement is required. | 136.72 | LogNormal | 0.83956 | 725.04 | LogNormal | 0.62182 | 28479.57 | Normal | 0.42461 | [6 empty] | 3233.83 | LogNormal | 0.83956 | 20540.69 | LogNormal | 0.62182 | 386332.81 | Normal | 0.42461
C2011.021d | C2011.021d | Monolithic cast-in-place and precast concrete stairs with no seismic joints - replace with prefabricated steel stair if replacement is required. | 136.72 | LogNormal | 0.83956 | 725.04 | LogNormal | 0.62182 | 28479.57 | Normal | 0.42461 | [6 empty] | 3233.83 | LogNormal | 0.83956 | 20540.69 | LogNormal | 0.62182 | 386332.81 | Normal | 0.42461
C2011.031a | C2011.031a | Hybrid stair assembly with steel stringers and concrete treads and landings with seismic joints that accommodate drift. | 39.53 | LogNormal | 1.021 | 339.59 | LogNormal | 0.63137 | 23560 | Normal | 0.45742 | [6 empty] | 940.85 | LogNormal | 1.021 | 8712.46 | LogNormal | 0.63137 | 318609.66 | Normal | 0.45742
C2011.031b | C2011.031b | Hybrid stair assembly with steel stringers and concrete treads and landings with no seismic joints. | 39.53 | LogNormal | 1.021 | 339.59 | LogNormal | 0.63137 | 23560 | Normal | 0.45742 | [6 empty] | 940.85 | LogNormal | 1.021 | 8712.46 | LogNormal | 0.63137 | 318609.66 | Normal | 0.45742
C3011.001a | C3011.001a | Wall Partition, Type: Gypsum + Wallpaper, Full Height, Fixed Below, Fixed Above | 756 | LogNormal | 0.29375 | [12 empty] | 17991 | LogNormal | 0.29375
C3011.001b | C3011.001b | Wall Partition, Type: Gypsum + Wallpaper, Partial Height, Fixed Below, Lateral Braced Above | 756 | LogNormal | 0.29375 | [12 empty] | 17991 | LogNormal | 0.29375
C3011.001c | C3011.001c | Wall Partition, Type: Gypsum + Wallpaper, Full Height, Fixed Below, Slip Track Above w/ returns (friction connection) | 756 | LogNormal | 0.29375 | [12 empty] | 17991 | LogNormal | 0.29375
C3011.001d | C3011.001d | Wall Partition, Type: Gypsum + Wallpaper, Full Height, Fixed Below, Slip Track Above w/o returns (friction connection) | 756 | LogNormal | 0.29375 | [12 empty] | 17991 | LogNormal | 0.29375
C3011.002a | C3011.002a | Wall Partition, Type: Gypsum + Ceramic Tile, Full Height, Fixed Below, Fixed Above | 729 | Normal | 0.33357 | 14220 | LogNormal | 0.26736 | [9 empty] | 17262 | Normal | 0.33357 | 350118 | LogNormal | 0.26736
C3011.002b | C3011.002b | Wall Partition, Type: Gypsum + Ceramic Tile, Partial Height, Fixed Below, Lateral Braced Above | 729 | Normal | 0.33357 | 14220 | LogNormal | 0.26736 | [9 empty] | 17262 | Normal | 0.33357 | 350118 | LogNormal | 0.26736
C3011.002c | C3011.002c | Wall Partition, Type: Gypsum + Ceramic Tile, Full Height, Fixed Below, Slip Track Above w/ returns (friction connection) | 729 | Normal | 0.33357 | 14220 | LogNormal | 0.26736 | [9 empty] | 17262 | Normal | 0.33357 | 350118 | LogNormal | 0.26736
C3011.002d | C3011.002d | Wall Partition, Type: Gypsum + Ceramic Tile, Full Height, Fixed Below, Slip Track Above w/o returns (friction connection) | 729 | Normal | 0.33357 | 14220 | LogNormal | 0.26736 | [9 empty] | 17262 | Normal | 0.33357 | 350118 | LogNormal | 0.26736
C3011.003a | C3011.003a | Wall Partition, Type: High End Marble or Wood Panel, Full Height, Fixed Below, Fixed Above | 5067 | Normal | 0.36077 | 19224 | Normal | 0.40225 | [9 empty] | 119961 | Normal | 0.36077 | 451449 | Normal | 0.40225
C3011.003b | C3011.003b | Wall Partition, Type: High End Marble or Wood Panel, Partial Height, Fixed Below, Lateral Braced Above | 5067 | Normal | 0.36077 | 19224 | Normal | 0.40225 | [9 empty] | 119961 | Normal | 0.36077 | 451449 | Normal | 0.40225
C3011.003c | C3011.003c | Wall Partition, Type: High End Marble or Wood Panel, Full Height, Fixed Below, Slip Track Above w/ returns (friction connection) | 5067 | Normal | 0.36077 | 19224 | Normal | 0.40225 | [9 empty] | 119961 | Normal | 0.36077 | 451449 | Normal | 0.40225
C3011.003d | C3011.003d | Wall Partition, Type: High End Marble or Wood Panel, Full Height, Fixed Below, Slip Track Above w/o returns (friction connection) | 5067 | Normal | 0.36077 | 19224 | Normal | 0.40225 | [9 empty] | 119961 | Normal | 0.36077 | 451449 | Normal | 0.40225
C3021.001a | C3021.001a | Generic Floor Covering - Flooding of floor caused by failure of pipe - Office - Dry | 10.16 | Normal | 0.37911 | [12 empty] | 164.27 | Normal | 0.37911
C3021.001b | C3021.001b | Generic Floor Covering - Flooding of floor caused by failure of pipe - Office - Humid | 55.8 | Normal | 0.35854 | [12 empty] | 595.05 | Normal | 0.35854
C3021.001c | C3021.001c | Generic Floor Covering - Flooding of floor caused by failure of pipe - Laboratory - Dry | 12.47 | Normal | 0.39979 | [12 empty] | 221.46 | Normal | 0.39979
C3021.001d | C3021.001d | Generic Floor Covering - Flooding of floor caused by failure of pipe - Laboratory - Humid | 128.56 | Normal | 0.35906 | [12 empty] | 1322.91 | Normal | 0.35906
C3021.001e | C3021.001e | Generic Floor Covering - Flooding of floor caused by failure of pipe - Hospital - Dry | 14.85 | Normal | 0.36102 | [12 empty] | 245.99 | Normal | 0.36102
C3021.001f | C3021.001f | Generic Floor Covering - Flooding of floor caused by failure of pipe - Hospital - Humid | 172.94 | LogNormal | 0.34492 | [12 empty] | 1744.14 | LogNormal | 0.34492
C3021.001g | C3021.001g | Generic Floor Covering - Flooding of floor caused by failure of pipe - School - Dry | 5.73 | Normal | 0.33956 | [12 empty] | 103.93 | Normal | 0.33956
C3021.001h | C3021.001h | Generic Floor Covering - Flooding of floor caused by failure of pipe - School - Humid | 56.98 | Normal | 0.36484 | [12 empty] | 592.31 | Normal | 0.36484
C3021.001i | C3021.001i | Generic Floor Covering - Flooding of floor caused by failure of pipe - Apartments - Dry | 11.81 | Normal | 0.37155 | [12 empty] | 169.95 | Normal | 0.37155
C3021.001j | C3021.001j | Generic Floor Covering - Flooding of floor caused by failure of pipe - Apartments - Humid | 120.7 | LogNormal | 0.35428 | [12 empty] | 1201.9 | LogNormal | 0.35428
C3021.001k | C3021.001k | Generic Floor Covering - Flooding of floor caused by failure of pipe - Retail - Dry | 5.08 | Normal | 0.42652 | [12 empty] | 99.65 | Normal | 0.42652
C3021.001l | C3021.001l | Generic Floor Covering - Flooding of floor caused by failure of pipe - Retail - Humid | 51.11 | Normal | 0.38316 | [12 empty] | 537.46 | Normal | 0.38316
C3021.001m | C3021.001m | Generic Floor Covering - Flooding of floor caused by failure of pipe - Warehouse - Dry | 0.95 | Normal | 0.47214 | [12 empty] | 12.54 | Normal | 0.47214
C3021.001n | C3021.001n | Generic Floor Covering - Flooding of floor caused by failure of pipe - Warehouse - Humid | 27.06 | Normal | 0.41715 | [12 empty] | 260.13 | Normal | 0.41715
C3021.001o | C3021.001o | Generic Floor Covering - Flooding of floor caused by failure of pipe - Hospitality - Dry | 14.64 | Normal | 0.40699 | [12 empty] | 204.89 | Normal | 0.40699
C3021.001p | C3021.001p | Generic Floor Covering - Flooding of floor caused by failure of pipe - Hospitality - Humid | 118.67 | Normal | 0.35906 | [12 empty] | 1187.94 | Normal | 0.35906
C3027.001 | C3027.001 | Raised Access Floor, non seismically rated. | 6 | LogNormal | 1.3082 | [12 empty] | 155 | LogNormal | 1.3082
C3027.002 | C3027.002 | Raised Access Floor, seismically rated. | 6 | LogNormal | 1.3082 | [12 empty] | 155 | LogNormal | 1.3082
C3032.001a | C3032.001a | Suspended Ceiling, SDC A,B,C, Area (A): A < 250, Vert support only | 217.5 | Normal | 0.60488 | 2132.5 | LogNormal | 0.57546 | 8155 | LogNormal | 0.3218 | [6 empty] | 2160 | Normal | 0.60488 | 28870 | LogNormal | 0.57546 | 80755 | LogNormal | 0.3218
C3032.001b | C3032.001b | Suspended Ceiling, SDC A,B,C, Area (A): 250 < A < 1000, Vert support only | 522 | Normal | 0.60488 | 5118 | LogNormal | 0.57546 | 19572 | LogNormal | 0.3218 | [6 empty] | 5184 | Normal | 0.60488 | 69288 | LogNormal | 0.57546 | 193812 | LogNormal | 0.3218
C3032.001c | C3032.001c | Suspended Ceiling, SDC A,B,C, Area (A): 1000 < A < 2500, Vert support only | 1566 | Normal | 0.60488 | 15354 | LogNormal | 0.57546 | 58716 | LogNormal | 0.3218 | [6 empty] | 15552 | Normal | 0.60488 | 207864 | LogNormal | 0.57546 | 581436 | LogNormal | 0.3218
C3032.001d | C3032.001d | Suspended Ceiling, SDC A,B,C, Area (A): A > 2500, Vert support only | 2175 | Normal | 0.60488 | 21325 | LogNormal | 0.57546 | 81550 | LogNormal | 0.3218 | [6 empty] | 21600 | Normal | 0.60488 | 288700 | LogNormal | 0.57546 | 807550 | LogNormal | 0.3218
C3032.003a | C3032.003a | Suspended Ceiling, SDC D,E (Ip=1.0), Area (A): A < 250, Vert & Lat support | 217.5 | Normal | 0.60488 | 2132.5 | LogNormal | 0.57546 | 8155 | LogNormal | 0.3218 | [6 empty] | 2160 | Normal | 0.60488 | 28870 | LogNormal | 0.57546 | 80755 | LogNormal | 0.3218
C3032.003b | C3032.003b | Suspended Ceiling, SDC D,E (Ip=1.0), Area (A): 250 < A < 1000, Vert & Lat support | 522 | Normal | 0.60488 | 5118 | LogNormal | 0.57546 | 19572 | LogNormal | 0.3218 | [6 empty] | 5184 | Normal | 0.60488 | 69288 | LogNormal | 0.57546 | 193812 | LogNormal | 0.3218
C3032.003c | C3032.003c | Suspended Ceiling, SDC D,E (Ip=1.0), Area (A): 1000 < A < 2500, Vert & Lat support | 1566 | Normal | 0.60488 | 15354 | LogNormal | 0.57546 | 58716 | LogNormal | 0.3218 | [6 empty] | 15552 | Normal | 0.60488 | 207864 | LogNormal | 0.57546 | 581436 | LogNormal | 0.3218
C3032.003d | C3032.003d | Suspended Ceiling, SDC D,E (Ip=1.0), Area (A): A > 2500, Vert & Lat support | 2175 | Normal | 0.60488 | 21325 | LogNormal | 0.57546 | 81550 | LogNormal | 0.3218 | [6 empty] | 21600 | Normal | 0.60488 | 288700 | LogNormal | 0.57546 | 807550 | LogNormal | 0.3218
C3032.004a | C3032.004a | Suspended Ceiling, SDC D,E,F (Ip=1.5), Area (A): A < 250, Vert & Lat support | 217.5 | Normal | 0.60488 | 2132.5 | LogNormal | 0.57546 | 8155 | LogNormal | 0.3218 | [6 empty] | 2160 | Normal | 0.60488 | 28870 | LogNormal | 0.57546 | 80755 | LogNormal | 0.3218
C3032.004b | C3032.004b | Suspended Ceiling, SDC D,E,F (Ip=1.5), Area (A): 250 < A < 1000, Vert & Lat support | 522 | Normal | 0.60488 | 5118 | LogNormal | 0.57546 | 19572 | LogNormal | 0.3218 | [6 empty] | 5184 | Normal | 0.60488 | 69288 | LogNormal | 0.57546 | 193812 | LogNormal | 0.3218
C3032.004c | C3032.004c | Suspended Ceiling, SDC D,E,F (Ip=1.5), Area (A): 1000 < A < 2500, Vert & Lat support | 1566 | Normal | 0.60488 | 15354 | LogNormal | 0.57546 | 58716 | LogNormal | 0.3218 | [6 empty] | 15552 | Normal | 0.60488 | 207864 | LogNormal | 0.57546 | 581436 | LogNormal | 0.3218
C3032.004d | C3032.004d | Suspended Ceiling, SDC D,E,F (Ip=1.5), Area (A): A > 2500, Vert & Lat support | 2175 | Normal | 0.60488 | 21325 | LogNormal | 0.57546 | 81550 | LogNormal | 0.3218 | [6 empty] | 21600 | Normal | 0.60488 | 288700 | LogNormal | 0.57546 | 807550 | LogNormal | 0.3218
C3034.001 | C3034.001 | Independent Pendant Lighting - non seismic | 51.81 | LogNormal | 0.68425 | [12 empty] | 1009.88 | LogNormal | 0.68425
C3034.002 | C3034.002 | Independent Pendant Lighting - seismically rated | 51.81 | LogNormal | 0.68425 | [12 empty] | 1009.88 | LogNormal | 0.68425
D1014.011 | D1014.011 | Traction Elevator – Applies to most California Installations 1976 or later, most western states installations 1982 or later and most other U.S installations 1998 or later. | 377.55 | LogNormal | 0.90913 | 1604.57 | Normal | 0.37354 | 2745.78 | Normal | 0.47876 | 429.03 | Normal | 0.54803 |  |  |  | 9466.48 | LogNormal | 0.90913 | 40232.54 | Normal | 0.37354 | 68847.13 | Normal | 0.47876 | 10757.36 | Normal | 0.54803
D1014.012 | D1014.012 | Traction Elevator – Applies to most California Installations prior to 1976, most western states installations prior to 1982 and most other U.S installations prior to 1998. | 377.55 | LogNormal | 0.90913 | 1604.57 | Normal | 0.37354 | 2745.78 | Normal | 0.47876 | 429.03 | Normal | 0.54803 |  |  |  | 9466.48 | LogNormal | 0.90913 | 40232.54 | Normal | 0.37354 | 68847.13 | Normal | 0.47876 | 10757.36 | Normal | 0.54803
D1014.021 | D1014.021 | Hydraulic Elevator – Applies to most California Installations 1976 or later, most western states installations postdating 1982 and most U.S installations postdating 1998. | 240.26 | LogNormal | 0.85904 | 2110.82 | Normal | 0.40767 | 3603.84 | Normal | 0.50513 | 690.74 | LogNormal | 0.35605 |  |  |  | 6024.12 | LogNormal | 0.85904 | 52926.23 | Normal | 0.40767 | 90361.86 | Normal | 0.50513 | 17319.36 | LogNormal | 0.35605
D1014.022 | D1014.022 | Hydraulic Elevator – Applies to most California Installations prior to 1976, most western states installations prior to 1982 and most U.S installations prior to 1998. | 240.26 | LogNormal | 0.85904 | 2110.82 | Normal | 0.40767 | 3603.84 | Normal | 0.50513 | 690.74 | LogNormal | 0.35605 |  |  |  | 6024.12 | LogNormal | 0.85904 | 52926.23 | Normal | 0.40767 | 90361.86 | Normal | 0.50513 | 17319.36 | LogNormal | 0.35605
D2061.023a | D2061.023a | Steam Piping - Large Diameter Welded Steel - (greater than 2.5 inches in diameter), SDC D, E, or F, PIPING FRAGILITY | 33.07 | LogNormal | 0.69527 | 484.53 | LogNormal | 0.47493 | [9 empty] | 864.51 | LogNormal | 0.69527 | 12415.24 | LogNormal | 0.47493
D2061.023b | D2061.023b | Steam Piping - Large Diameter Welded Steel - (greater than 2.5 inches in diameter), SDC D, E, or F, BRACING FRAGILITY | 35.97 | LogNormal | 0.69527 | 35.97 | LogNormal | 0.69527 | [9 empty] | 1021.56 | LogNormal | 0.69527 | 1021.56 | LogNormal | 0.69527
D2061.024a | D2061.024a | Steam Piping - Large Diameter Welded Steel - (greater than 2.5 inches in diameter), SDC D, E, or F (OSHPD or sim), PIPING FRAGILITY | 33.07 | LogNormal | 0.69527 | 484.53 | LogNormal | 0.47493 | [9 empty] | 864.51 | LogNormal | 0.69527 | 12415.24 | LogNormal | 0.47493
D2061.024b | D2061.024b | Steam Piping - Large Diameter Welded Steel - (greater than 2.5 inches in diameter), SDC D, E, or F (OSHPD or sim), BRACING FRAGILITY | 35.97 | LogNormal | 0.69527 | 35.97 | LogNormal | 0.69527 | [9 empty] | 1021.56 | LogNormal | 0.69527 | 1021.56 | LogNormal | 0.69527
D3031.011a | D3031.011a | Chiller - Capacity: < 100 Ton - Unanchored equipment that is not vibration isolated - Equipment fragility only | 25564.37 | LogNormal | 0.30717 | [12 empty] | 296457.76 | LogNormal | 0.30717
D3031.011b | D3031.011b | Chiller - Capacity: 100 to <350 Ton - Unanchored equipment that is not vibration isolated - Equipment fragility only | 85253.48 | LogNormal | 0.30292 | [12 empty] | 987789.43 | LogNormal | 0.30292
D3031.011c | D3031.011c | Chiller - Capacity: 350 to <750 Ton - Unanchored equipment that is not vibration isolated - Equipment fragility only | 142390.7 | LogNormal | 0.30348 | [12 empty] | 1649767.03 | LogNormal | 0.30348
D3031.011d | D3031.011d | Chiller - Capacity: 750 to <1000 Ton - Unanchored equipment that is not vibration isolated - Equipment fragility only | 241055.69 | LogNormal | 0.30423 | [12 empty] | 2791588.1 | LogNormal | 0.30423
D3031.012a | D3031.012a | Chiller - Capacity: < 100 Ton - Vibration isolated equipment that is not snubbed or restrained - Anchorage fragility only | 110.49 | LogNormal | 0.5168 | 25674.86 | LogNormal | 0.31061 | [9 empty] | 3225.95 | LogNormal | 0.5168 | 299683.71 | LogNormal | 0.31061
D3031.012b | D3031.012b | Chiller - Capacity: < 100 Ton - Vibration isolated equipment that is not snubbed or restrained - Equipment fragility only | 25564.37 | LogNormal | 0.30717 | [12 empty] | 296457.76 | LogNormal | 0.30717
D3031.012c | D3031.012c | Chiller - Capacity: < 100 Ton - Vibration isolated equipment that is not snubbed or restrained - Combined anchorage/isolator & equipment fragility | 110.49 | LogNormal | 0.5168 | 25674.86 | LogNormal | 0.31061 | 25674.86 | LogNormal | 0.31061 | [6 empty] | 3225.95 | LogNormal | 0.5168 | 299683.71 | LogNormal | 0.31061 | 299683.71 | LogNormal | 0.31061
D3031.012d | D3031.012d | Chiller - Capacity: 100 to <350 Ton - Vibration isolated equipment that is not snubbed or restrained - Anchorage fragility only | 168.31 | Normal | 0.47039 | 85421.8 | LogNormal | 0.30422 | [9 empty] | 5000.18 | Normal | 0.47039 | 992789.62 | LogNormal | 0.30422
D3031.012e | D3031.012e | Chiller - Capacity: 100 to <350 Ton - Vibration isolated equipment that is not snubbed or restrained - Equipment fragility only | 85253.48 | LogNormal | 0.30292 | [12 empty] | 987789.43 | LogNormal | 0.30292
D3031.012f | D3031.012f | Chiller - Capacity: 100 to <350 Ton - Vibration isolated equipment that is not snubbed or restrained - Combined anchorage/isolator & equipment fragility | 168.31 | Normal | 0.47039 | 85421.8 | LogNormal | 0.30422 | 85421.8 | LogNormal | 0.30422 | [6 empty] | 5000.18 | Normal | 0.47039 | 992789.62 | LogNormal | 0.30422 | 992789.62 | LogNormal | 0.30422
D3031.012g | D3031.012g | Chiller - Capacity: 350 to <750 Ton - Vibration isolated equipment that is not snubbed or restrained - Anchorage fragility only | 245.4 | Normal | 0.3882 | 142636.11 | LogNormal | 0.30409 | [9 empty] | 7365.83 | Normal | 0.3882 | 1657132.86 | LogNormal | 0.30409
D3031.012h | D3031.012h | Chiller - Capacity: 350 to <750 Ton - Vibration isolated equipment that is not snubbed or restrained - Equipment fragility only | 142390.7 | LogNormal | 0.30348 | [12 empty] | 1649767.03 | LogNormal | 0.30348
D3031.012i | D3031.012i | Chiller - Capacity: 350 to <750 Ton - Vibration isolated equipment that is not snubbed or restrained - Combined anchorage/isolator & equipment fragility | 245.4 | Normal | 0.3882 | 142636.11 | LogNormal | 0.30409 | 142636.11 | LogNormal | 0.30409 | [6 empty] | 7365.83 | Normal | 0.3882 | 1657132.86 | LogNormal | 0.30409 | 1657132.86 | LogNormal | 0.30409
D3031.012j | D3031.012j | Chiller - Capacity: 750 to <1000 Ton - Vibration isolated equipment that is not snubbed or restrained - Anchorage fragility only | 245.4 | LogNormal | 0.38177 | 241301.09 | LogNormal | 0.30459 | [9 empty] | 7365.83 | LogNormal | 0.38177 | 2798953.93 | LogNormal | 0.30459
D3031.012k | D3031.012k | Chiller - Capacity: 750 to <1000 Ton - Vibration isolated equipment that is not snubbed or restrained - Equipment fragility only | 241055.69 | LogNormal | 0.30423 | [12 empty] | 2791588.1 | LogNormal | 0.30423
D3031.012l | D3031.012l | Chiller - Capacity: 750 to <1000 Ton - Vibration isolated equipment that is not snubbed or restrained - Combined anchorage/isolator & equipment fragility | 245.4 | LogNormal | 0.38177 | 241301.09 | LogNormal | 0.30459 | 241301.09 | LogNormal | 0.30459 | [6 empty] | 7365.83 | LogNormal | 0.38177 | 2798953.93 | LogNormal | 0.30459 | 2798953.93 | LogNormal | 0.30459
D3031.013a | D3031.013a | Chiller - Capacity: < 100 Ton - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only | 110.49 | LogNormal | 0.5168 | 25674.86 | LogNormal | 0.31061 | [9 empty] | 3225.95 | LogNormal | 0.5168 | 299683.71 | LogNormal | 0.31061
D3031.013b | D3031.013b | Chiller - Capacity: < 100 Ton - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only | 25564.37 | LogNormal | 0.30717 | [12 empty] | 296457.76 | LogNormal | 0.30717
D3031.013c | D3031.013c | Chiller - Capacity: < 100 Ton - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | 110.49 | LogNormal | 0.5168 | 25674.86 | LogNormal | 0.31061 | 25674.86 | LogNormal | 0.31061 | [6 empty] | 3225.95 | LogNormal | 0.5168 | 299683.71 | LogNormal | 0.31061 | 299683.71 | LogNormal | 0.31061
D3031.013d | D3031.013d | Chiller - Capacity: 100 to <350 Ton - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only | 168.31 | Normal | 0.47039 | 85421.8 | LogNormal | 0.30422 | [9 empty] | 5000.18 | Normal | 0.47039 | 992789.62 | LogNormal | 0.30422
D3031.013e | D3031.013e | Chiller - Capacity: 100 to <350 Ton - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only | 85253.48 | LogNormal | 0.30292 | [12 empty] | 987789.43 | LogNormal | 0.30292
D3031.013f | D3031.013f | Chiller - Capacity: 100 to <350 Ton - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | 168.31 | Normal | 0.47039 | 85421.8 | LogNormal | 0.30422 | 85421.8 | LogNormal | 0.30422 | [6 empty] | 5000.18 | Normal | 0.47039 | 992789.62 | LogNormal | 0.30422 | 992789.62 | LogNormal | 0.30422
D3031.013g | D3031.013g | Chiller - Capacity: 350 to <750 Ton - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only | 245.4 | Normal | 0.3882 | 142636.11 | LogNormal | 0.30409 | [9 empty] | 7365.83 | Normal | 0.3882 | 1657132.86 | LogNormal | 0.30409
D3031.013h | D3031.013h | Chiller - Capacity: 350 to <750 Ton - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only | 142390.7 | LogNormal | 0.30348 | [12 empty] | 1649767.03 | LogNormal | 0.30348
D3031.013i | D3031.013i | Chiller - Capacity: 350 to <750 Ton - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | 245.4 | Normal | 0.3882 | 142636.11 | LogNormal | 0.30409 | 142636.11 | LogNormal | 0.30409 | [6 empty] | 7365.83 | Normal | 0.3882 | 1657132.86 | LogNormal | 0.30409 | 1657132.86 | LogNormal | 0.30409
D3031.013j | D3031.013j | Chiller - Capacity: 750 to <1000 Ton - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only | 245.4 | LogNormal | 0.38177 | 241301.09 | LogNormal | 0.30459 | [9 empty] | 7365.83 | LogNormal | 0.38177 | 2798953.93 | LogNormal | 0.30459
D3031.013k | D3031.013k | Chiller - Capacity: 750 to <1000 Ton - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only | 241055.69 | LogNormal | 0.30423 | [12 empty] | 2791588.1 | LogNormal | 0.30423
D3031.013l | D3031.013l | Chiller - Capacity: 750 to <1000 Ton - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | 245.4 | LogNormal | 0.38177 | 241301.09 | LogNormal | 0.30459 | 241301.09 | LogNormal | 0.30459 | [6 empty] | 7365.83 | LogNormal | 0.38177 | 2798953.93 | LogNormal | 0.30459 | 2798953.93 | LogNormal | 0.30459
D3031.021a | D3031.021a | Cooling Tower - Capacity: < 100 Ton - Unanchored equipment that is not vibration isolated - Equipment fragility only | 12943.84 | LogNormal | 0.30343 | [12 empty] | 150447.45 | LogNormal | 0.30343
D3031.021b | D3031.021b | Cooling Tower - Capacity: 100 to <350 Ton - Unanchored equipment that is not vibration isolated - Equipment fragility only | 43185.06 | LogNormal | 0.3048 | [12 empty] | 501088.4 | LogNormal | 0.3048
D3031.021c | D3031.021c | Cooling Tower - Capacity: 350 to <750 Ton - Unanchored equipment that is not vibration isolated - Equipment fragility only | 72276.66 | LogNormal | 0.30599 | [12 empty] | 838598.65 | LogNormal | 0.30599
D3031.021d | D3031.021d | Cooling Tower - Capacity: 750 to <1000 Ton - Unanchored equipment that is not vibration isolated - Equipment fragility only | 121861.82 | LogNormal | 0.304 | [12 empty] | 1412601.85 | LogNormal | 0.304
D3031.022a | D3031.022a | Cooling Tower - Capacity: < 100 Ton - Vibration isolated equipment that is not snubbed or restrained - Anchorage fragility only | 110.49 | LogNormal | 0.5168 | 13054.34 | LogNormal | 0.31008 | [9 empty] | 3225.95 | LogNormal | 0.5168 | 153673.4 | LogNormal | 0.31008
D3031.022b | D3031.022b | Cooling Tower - Capacity: < 100 Ton - Vibration isolated equipment that is not snubbed or restrained - Equipment fragility only | 12943.84 | LogNormal | 0.30343 | [12 empty] | 150447.45 | LogNormal | 0.30343
D3031.022c | D3031.022c | Cooling Tower - Capacity: < 100 Ton - Vibration isolated equipment that is not snubbed or restrained - Combined anchorage/isolator & equipment fragility | 110.49 | LogNormal | 0.5168 | 13054.34 | LogNormal | 0.31008 | 12943.84 | LogNormal | 0.30343 | [6 empty] | 3225.95 | LogNormal | 0.5168 | 153673.4 | LogNormal | 0.31008 | 150447.45 | LogNormal | 0.30343
D3031.022d | D3031.022d | Cooling Tower - Capacity: 100 to <350 Ton - Vibration isolated equipment that is not snubbed or restrained - Anchorage fragility only | 168.31 | Normal | 0.47039 | 43353.37 | LogNormal | 0.30732 | [9 empty] | 5000.18 | Normal | 0.47039 | 506088.59 | LogNormal | 0.30732
D3031.022e | D3031.022e | Cooling Tower - Capacity: 100 to <350 Ton - Vibration isolated equipment that is not snubbed or restrained - Equipment fragility only | 43185.06 | LogNormal | 0.3048 | [12 empty] | 501088.4 | LogNormal | 0.3048
D3031.022f | D3031.022f | Cooling Tower - Capacity: 100 to <350 Ton - Vibration isolated equipment that is not snubbed or restrained - Combined anchorage/isolator & equipment fragility | 168.31 | Normal | 0.47039 | 43353.37 | LogNormal | 0.30732 | 43185.06 | LogNormal | 0.3048 | [6 empty] | 5000.18 | Normal | 0.47039 | 506088.59 | LogNormal | 0.30732 | 501088.4 | LogNormal | 0.3048
D3031.022g | D3031.022g | Cooling Tower - Capacity: 350 to <750 Ton - Vibration isolated equipment that is not snubbed or restrained - Anchorage fragility only | 245.4 | Normal | 0.3882 | 72522.07 | LogNormal | 0.30715 | [9 empty] | 7365.83 | Normal | 0.3882 | 845964.48 | LogNormal | 0.30715
D3031.022h | D3031.022h | Cooling Tower - Capacity: 350 to <750 Ton - Vibration isolated equipment that is not snubbed or restrained - Equipment fragility only | 72276.66 | LogNormal | 0.30599 | [12 empty] | 838598.65 | LogNormal | 0.30599
D3031.022i | D3031.022i | Cooling Tower - Capacity: 350 to <750 Ton - Vibration isolated equipment that is not snubbed or restrained - Combined anchorage/isolator & equipment fragility | 245.4 | Normal | 0.3882 | 72522.07 | LogNormal | 0.30715 | 72276.66 | LogNormal | 0.30599 | [6 empty] | 7365.83 | Normal | 0.3882 | 845964.48 | LogNormal | 0.30715 | 838598.65 | LogNormal | 0.30599
D3031.022j | D3031.022j | Cooling Tower - Capacity: 750 to <1000 Ton - Vibration isolated equipment that is not snubbed or restrained - Anchorage fragility only | 245.4 | LogNormal | 0.38177 | 122107.23 | LogNormal | 0.30471 | [9 empty] | 7365.83 | LogNormal | 0.38177 | 1419967.67 | LogNormal | 0.30471
D3031.022k | D3031.022k | Cooling Tower - Capacity: 750 to <1000 Ton - Vibration isolated equipment that is not snubbed or restrained - Equipment fragility only | 121861.82 | LogNormal | 0.304 | [12 empty] | 1412601.85 | LogNormal | 0.304
D3031.022l | D3031.022l | Cooling Tower - Capacity: 750 to <1000 Ton - Vibration isolated equipment that is not snubbed or restrained - Combined anchorage/isolator & equipment fragility | 245.4 | LogNormal | 0.38177 | 122107.23 | LogNormal | 0.30471 | 121861.82 | LogNormal | 0.304 | [6 empty] | 7365.83 | LogNormal | 0.38177 | 1419967.67 | LogNormal | 0.30471 | 1412601.85 | LogNormal | 0.304
D3031.023a | D3031.023a | Cooling Tower - Capacity: < 100 Ton - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only | 110.49 | LogNormal | 0.5168 | 13054.34 | LogNormal | 0.31008 | [9 empty] | 3225.95 | LogNormal | 0.5168 | 153673.4 | LogNormal | 0.31008
D3031.023b | D3031.023b | Cooling Tower - Capacity: < 100 Ton - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only | 12943.84 | LogNormal | 0.30343 | [12 empty] | 150447.45 | LogNormal | 0.30343
D3031.023c | D3031.023c | Cooling Tower - Capacity: < 100 Ton - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | 110.49 | LogNormal | 0.5168 | 13054.34 | LogNormal | 0.31008 | 12943.84 | LogNormal | 0.30343 | [6 empty] | 3225.95 | LogNormal | 0.5168 | 153673.4 | LogNormal | 0.31008 | 150447.45 | LogNormal | 0.30343
D3031.023d | D3031.023d | Cooling Tower - Capacity: 100 to <350 Ton - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only | 168.31 | Normal | 0.47039 | 43353.37 | LogNormal | 0.30732 | [9 empty] | 5000.18 | Normal | 0.47039 | 506088.59 | LogNormal | 0.30732
D3031.023e | D3031.023e | Cooling Tower - Capacity: 100 to <350 Ton - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only | 43185.06 | LogNormal | 0.3048 | [12 empty] | 501088.4 | LogNormal | 0.3048
D3031.023f | D3031.023f | Cooling Tower - Capacity: 100 to <350 Ton - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | 168.31 | Normal | 0.47039 | 43353.37 | LogNormal | 0.30732 | 43185.06 | LogNormal | 0.3048 | [6 empty] | 5000.18 | Normal | 0.47039 | 506088.59 | LogNormal | 0.30732 | 501088.4 | LogNormal | 0.3048
D3031.023g | D3031.023g | Cooling Tower - Capacity: 350 to <750 Ton - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only | 245.4 | Normal | 0.3882 | 72522.07 | LogNormal | 0.30715 | [9 empty] | 7365.83 | Normal | 0.3882 | 845964.48 | LogNormal | 0.30715
D3031.023h | D3031.023h | Cooling Tower - Capacity: 350 to <750 Ton - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only | 72276.66 | LogNormal | 0.30599 | [12 empty] | 838598.65 | LogNormal | 0.30599
D3031.023i | D3031.023i | Cooling Tower - Capacity: 350 to <750 Ton - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | 245.4 | Normal | 0.3882 | 72522.07 | LogNormal | 0.30715 | 72276.66 | LogNormal | 0.30599 | [6 empty] | 7365.83 | Normal | 0.3882 | 845964.48 | LogNormal | 0.30715 | 838598.65 | LogNormal | 0.30599
D3031.023j | D3031.023j | Cooling Tower - Capacity: 750 to <1000 Ton - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only | 245.4 | LogNormal | 0.38177 | 122107.23 | LogNormal | 0.30471 | [9 empty] | 7365.83 | LogNormal | 0.38177 | 1419967.67 | LogNormal | 0.30471
D3031.023k | D3031.023k | Cooling Tower - Capacity: 750 to <1000 Ton - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only | 121861.82 | LogNormal | 0.304 | [12 empty] | 1412601.85 | LogNormal | 0.304
D3031.023l | D3031.023l | Cooling Tower - Capacity: 750 to <1000 Ton - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | 245.4 | LogNormal | 0.38177 | 122107.23 | LogNormal | 0.30471 | 121861.82 | LogNormal | 0.304 | [6 empty] | 7365.83 | LogNormal | 0.38177 | 1419967.67 | LogNormal | 0.30471 | 1412601.85 | LogNormal | 0.304
D3032.011a | D3032.011a | Compressor - Capacity: Small non medical air supply - Unanchored equipment that is not vibration isolated - Equipment fragility only | 336.55 | LogNormal | 0.30364 | 1167.79 | LogNormal | 0.32411 | [9 empty] | 3893.61 | LogNormal | 0.30364 | 13811.74 | LogNormal | 0.32411
D3032.011b | D3032.011b | Compressor - Capacity: Large non medical air supply - Unanchored equipment that is not vibration isolated - Equipment fragility only | 1346.19 | LogNormal | 0.30308 | 3720.7 | LogNormal | 0.31582 | [9 empty] | 15574.43 | LogNormal | 0.30308 | 43855.64 | LogNormal | 0.31582
D3032.011c | D3032.011c | Compressor - Capacity: Small medical quality air supply - Unanchored equipment that is not vibration isolated - Equipment fragility only | 403.86 | LogNormal | 0.3018 | 3833.91 | LogNormal | 0.33299 | [9 empty] | 4672.33 | LogNormal | 0.3018 | 45843.34 | LogNormal | 0.33299
D3032.011d | D3032.011d | Compressor - Capacity: Large medical quality air supply - Unanchored equipment that is not vibration isolated - Equipment fragility only | 1794.92 | LogNormal | 0.30308 | 13762.57 | LogNormal | 0.31459 | [9 empty] | 20765.91 | LogNormal | 0.30308 | 161049.7 | LogNormal | 0.31459
D3032.012a | D3032.012a | Compressor - Capacity: Small non medical air supply - Vibration isolated equipment that is not snubbed or restrained - Anchorage fragility only | 52.68 | LogNormal | 0.60289 | 1220.46 | LogNormal | 0.3594 | [9 empty] | 1451.72 | LogNormal | 0.60289 | 15263.46 | LogNormal | 0.3594
D3032.012b | D3032.012b | Compressor - Capacity: Small non medical air supply - Vibration isolated equipment that is not snubbed or restrained - Equipment fragility only | 336.55 | LogNormal | 0.30364 | 1167.79 | LogNormal | 0.32411 | [9 empty] | 3893.61 | LogNormal | 0.30364 | 13811.74 | LogNormal | 0.32411
D3032.012c | D3032.012c | Compressor - Capacity: Small non medical air supply - Vibration isolated equipment that is not snubbed or restrained - Combined anchorage/isolator & equipment fragility | 52.68 | LogNormal | 0.60289 | 1220.46 | LogNormal | 0.3594 | 336.55 | LogNormal | 0.30364 | 1220.46 | LogNormal | 0.3594 |  |  |  | 1451.72 | LogNormal | 0.60289 | 15263.46 | LogNormal | 0.3594 | 3893.61 | LogNormal | 0.30364 | 15263.46 | LogNormal | 0.3594
D3032.012d | D3032.012d | Compressor - Capacity: Large non medical air supply - Vibration isolated equipment that is not snubbed or restrained - Anchorage fragility only | 91.22 | LogNormal | 0.50989 | 3811.93 | LogNormal | 0.33188 | [9 empty] | 2634.54 | LogNormal | 0.50989 | 46490.18 | LogNormal | 0.33188
D3032.012e | D3032.012e | Compressor - Capacity: Large non medical air supply - Vibration isolated equipment that is not snubbed or restrained - Equipment fragility only | 1346.19 | LogNormal | 0.30308 | 3720.7 | LogNormal | 0.31582 | [9 empty] | 15574.43 | LogNormal | 0.30308 | 43855.64 | LogNormal | 0.31582
D3032.012f | D3032.012f | Compressor - Capacity: Large non medical air supply - Vibration isolated equipment that is not snubbed or restrained - Combined anchorage/isolator & equipment fragility | 91.22 | LogNormal | 0.50989 | 3811.93 | LogNormal | 0.33188 | 1346.19 | LogNormal | 0.30308 | 3811.93 | LogNormal | 0.33188 |  |  |  | 2634.54 | LogNormal | 0.50989 | 46490.18 | LogNormal | 0.33188 | 15574.43 | LogNormal | 0.30308 | 46490.18 | LogNormal | 0.33188
D3032.012g | D3032.012g | Compressor - Capacity: Small medical quality air supply - Vibration isolated equipment that is not snubbed or restrained - Anchorage fragility only | 52.68 | LogNormal | 0.60289 | 3886.58 | LogNormal | 0.34531 | [9 empty] | 1451.72 | LogNormal | 0.60289 | 47295.06 | LogNormal | 0.34531
D3032.012h | D3032.012h | Compressor - Capacity: Small medical quality air supply - Vibration isolated equipment that is not snubbed or restrained - Equipment fragility only | 403.86 | LogNormal | 0.3018 | 3833.91 | LogNormal | 0.33299 | [9 empty] | 4672.33 | LogNormal | 0.3018 | 45843.34 | LogNormal | 0.33299
D3032.012i | D3032.012i | Compressor - Capacity: Small medical quality air supply - Vibration isolated equipment that is not snubbed or restrained - Combined anchorage/isolator & equipment fragility | 52.68 | LogNormal | 0.60289 | 3886.58 | LogNormal | 0.34531 | 403.86 | LogNormal | 0.3018 | 3886.58 | LogNormal | 0.34531 |  |  |  | 1451.72 | LogNormal | 0.60289 | 47295.06 | LogNormal | 0.34531 | 4672.33 | LogNormal | 0.3018 | 47295.06 | LogNormal | 0.34531
D3032.012j | D3032.012j | Compressor - Capacity: Large medical quality air supply - Vibration isolated equipment that is not snubbed or restrained - Anchorage fragility only | 91.22 | LogNormal | 0.50989 | 13853.79 | LogNormal | 0.31911 | [9 empty] | 2634.54 | LogNormal | 0.50989 | 163684.24 | LogNormal | 0.31911
D3032.012k | D3032.012k | Compressor - Capacity: Large medical quality air supply - Vibration isolated equipment that is not snubbed or restrained - Equipment fragility only | 1794.92 | LogNormal | 0.30308 | 13762.57 | LogNormal | 0.31459 | [9 empty] | 20765.91 | LogNormal | 0.30308 | 161049.7 | LogNormal | 0.31459
D3032.012l | D3032.012l | Compressor - Capacity: Large medical quality air supply - Vibration isolated equipment that is not snubbed or restrained - Combined anchorage/isolator & equipment fragility | 91.22 | LogNormal | 0.50989 | 13853.79 | LogNormal | 0.31911 | 1794.92 | LogNormal | 0.30308 | 13853.79 | LogNormal | 0.31911 |  |  |  | 2634.54 | LogNormal | 0.50989 | 163684.24 | LogNormal | 0.31911 | 20765.91 | LogNormal | 0.30308 | 163684.24 | LogNormal | 0.31911
D3032.013a | D3032.013a | Compressor - Capacity: Small non medical air supply - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only | 52.68 | LogNormal | 0.60289 | 1220.46 | LogNormal | 0.3594 | [9 empty] | 1451.72 | LogNormal | 0.60289 | 15263.46 | LogNormal | 0.3594
D3032.013b | D3032.013b | Compressor - Capacity: Small non medical air supply - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only | 336.55 | LogNormal | 0.30364 | 1167.79 | LogNormal | 0.32411 | [9 empty] | 3893.61 | LogNormal | 0.30364 | 13811.74 | LogNormal | 0.32411
D3032.013c | D3032.013c | Compressor - Capacity: Small non medical air supply - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | 52.68 | LogNormal | 0.60289 | 1220.46 | LogNormal | 0.3594 | 336.55 | LogNormal | 0.30364 | 1220.46 | LogNormal | 0.3594 |  |  |  | 1451.72 | LogNormal | 0.60289 | 15263.46 | LogNormal | 0.3594 | 3893.61 | LogNormal | 0.30364 | 15263.46 | LogNormal | 0.3594
D3032.013d | D3032.013d | Compressor - Capacity: Large non medical air supply - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only | 91.22 | LogNormal | 0.50989 | 3811.93 | LogNormal | 0.33188 | [9 empty] | 2634.54 | LogNormal | 0.50989 | 46490.18 | LogNormal | 0.33188
D3032.013e | D3032.013e | Compressor - Capacity: Large non medical air supply - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only | 1346.19 | LogNormal | 0.30308 | 3720.7 | LogNormal | 0.31582 | [9 empty] | 15574.43 | LogNormal | 0.30308 | 43855.64 | LogNormal | 0.31582
D3032.013f | D3032.013f | Compressor - Capacity: Large non medical air supply - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | 91.22 | LogNormal | 0.50989 | 3811.93 | LogNormal | 0.33188 | 1346.19 | LogNormal | 0.30308 | 3811.93 | LogNormal | 0.33188 |  |  |  | 2634.54 | LogNormal | 0.50989 | 46490.18 | LogNormal | 0.33188 | 15574.43 | LogNormal | 0.30308 | 46490.18 | LogNormal | 0.33188
D3032.013g | D3032.013g | Compressor - Capacity: Small medical quality air supply - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only | 52.68 | LogNormal | 0.60289 | 3886.58 | LogNormal | 0.34531 | [9 empty] | 1451.72 | LogNormal | 0.60289 | 47295.06 | LogNormal | 0.34531
D3032.013h | D3032.013h | Compressor - Capacity: Small medical quality air supply - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only | 403.86 | LogNormal | 0.3018 | 3833.91 | LogNormal | 0.33299 | [9 empty] | 4672.33 | LogNormal | 0.3018 | 45843.34 | LogNormal | 0.33299
D3032.013i | D3032.013i | Compressor - Capacity: Small medical quality air supply - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | 52.68 | LogNormal | 0.60289 | 3886.58 | LogNormal | 0.34531 | 403.86 | LogNormal | 0.3018 | 3886.58 | LogNormal | 0.34531 |  |  |  | 1451.72 | LogNormal | 0.60289 | 47295.06 | LogNormal | 0.34531 | 4672.33 | LogNormal | 0.3018 | 47295.06 | LogNormal | 0.34531
D3032.013j | D3032.013j | Compressor - Capacity: Large medical quality air supply - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only | 91.22 | LogNormal | 0.50989 | 13853.79 | LogNormal | 0.31911 | [9 empty] | 2634.54 | LogNormal | 0.50989 | 163684.24 | LogNormal | 0.31911
D3032.013k | D3032.013k | Compressor - Capacity: Large medical quality air supply - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only | 1794.92 | LogNormal | 0.30308 | 13762.57 | LogNormal | 0.31459 | [9 empty] | 20765.91 | LogNormal | 0.30308 | 161049.7 | LogNormal | 0.31459
D3032.013l | D3032.013l | Compressor - Capacity: Large medical quality air supply - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | 91.22 | LogNormal | 0.50989 | 13853.79 | LogNormal | 0.31911 | 1794.92 | LogNormal | 0.30308 | 13853.79 | LogNormal | 0.31911 |  |  |  | 2634.54 | LogNormal | 0.50989 | 163684.24 | LogNormal | 0.31911 | 20765.91 | LogNormal | 0.30308 | 163684.24 | LogNormal | 0.31911
D3041.001a | D3041.001a | HVAC Fan In Line Fan, Fan independently supported and vibration isolators, SDC A or B | 1566.4 | LogNormal | 0.42405 | 11288.9 | LogNormal | 0.26657 | [9 empty] | 18649.4 | LogNormal | 0.42405 | 131131.4 | LogNormal | 0.26657
D3041.001b | D3041.001b | HVAC Fan In Line Fan, Fan independently supported and vibration isolators, SDC C | 1566.4 | LogNormal | 0.42405 | 11288.9 | LogNormal | 0.26657 | [9 empty] | 18649.4 | LogNormal | 0.42405 | 131131.4 | LogNormal | 0.26657
D3041.001c | D3041.001c | HVAC Fan In Line Fan, Fan independently supported and vibration isolators, SDC D, E, F | 1566.4 | LogNormal | 0.42405 | 11288.9 | LogNormal | 0.26657 | [9 empty] | 18649.4 | LogNormal | 0.42405 | 131131.4 | LogNormal | 0.26657
D3041.001d | D3041.001d | HVAC Fan In Line Fan, Fan independently supported and vibration isolators, SDC D, E, F (OSHPD or sim) | 1566.4 | LogNormal | 0.42405 | 11288.9 | LogNormal | 0.26657 | [9 empty] | 18649.4 | LogNormal | 0.42405 | 131131.4 | LogNormal | 0.26657
D3041.002a | D3041.002a | HVAC Fan In Line Fan, Fan independently supported but not on vibration isolators, SDC A or B | 1566.4 | LogNormal | 0.42405 | [12 empty] | 18649.4 | LogNormal | 0.42405
D3041.002b | D3041.002b | HVAC Fan In Line Fan, Fan independently supported but not on vibration isolators, SDC C | 1566.4 | LogNormal | 0.42405 | [12 empty] | 18649.4 | LogNormal | 0.42405
D3041.002c | D3041.002c | HVAC Fan In Line Fan, Fan independently supported but not on vibration isolators, SDC D, E, F | 1566.4 | LogNormal | 0.42405 | [12 empty] | 18649.4 | LogNormal | 0.42405
D3041.002d | D3041.002d | HVAC Fan In Line Fan, Fan independently supported but not on vibration isolators, SDC D, E, F (OSHPD or sim) | 1566.4 | LogNormal | 0.42405 | [12 empty] | 18649.4 | LogNormal | 0.42405
D3041.011a | D3041.011a | HVAC Galvanized Sheet Metal Ducting less than 6 sq. ft in cross sectional area, SDC A or B | 181.81 | LogNormal | 0.44436 | 2372.82 | LogNormal | 0.26933 | [9 empty] | 2708.79 | LogNormal | 0.44436 | 30267.85 | LogNormal | 0.26933
D3041.011b | D3041.011b | HVAC Galvanized Sheet Metal Ducting less than 6 sq. ft in cross sectional area, SDC C | 181.81 | LogNormal | 0.44436 | 2372.82 | LogNormal | 0.26933 | [9 empty] | 2708.79 | LogNormal | 0.44436 | 30267.85 | LogNormal | 0.26933
D3041.011c | D3041.011c | HVAC Galvanized Sheet Metal Ducting less than 6 sq. ft in cross sectional area, SDC D, E, or F | 181.81 | LogNormal | 0.44436 | 2372.82 | LogNormal | 0.26933 | [9 empty] | 2708.79 | LogNormal | 0.44436 | 30267.85 | LogNormal | 0.26933
D3041.011d | D3041.011d | HVAC Galvanized Sheet Metal Ducting less than 6 sq. ft in cross sectional area, SDC D, E, or F (OSHPD or sim) | 181.81 | LogNormal | 0.44436 | 2372.82 | LogNormal | 0.26933 | [9 empty] | 2708.79 | LogNormal | 0.44436 | 30267.85 | LogNormal | 0.26933
D3041.012a | D3041.012a | HVAC Galvanized Sheet Metal Ducting - 6 sq. ft cross sectional area or greater, SDC A or B | 298.31 | LogNormal | 0.35779 | 2921.66 | LogNormal | 0.26266 | [9 empty] | 4425.03 | LogNormal | 0.35779 | 38459.64 | LogNormal | 0.26266
D3041.012b | D3041.012b | HVAC Galvanized Sheet Metal Ducting - 6 sq. ft cross sectional area or greater, SDC C | 298.31 | LogNormal | 0.35779 | 2921.66 | LogNormal | 0.26266 | [9 empty] | 4425.03 | LogNormal | 0.35779 | 38459.64 | LogNormal | 0.26266
D3041.012c | D3041.012c | HVAC Galvanized Sheet Metal Ducting - 6 sq. ft cross sectional area or greater, SDC D, E, or F | 298.31 | LogNormal | 0.35779 | 2921.66 | LogNormal | 0.26266 | [9 empty] | 4425.03 | LogNormal | 0.35779 | 38459.64 | LogNormal | 0.26266
D3041.012d | D3041.012d | HVAC Galvanized Sheet Metal Ducting - 6 sq. ft cross sectional area or greater, SDC D, E, or F (OSHPD or sim) | 298.31 | LogNormal | 0.35779 | 2921.66 | LogNormal | 0.26266 | [9 empty] | 4425.03 | LogNormal | 0.35779 | 38459.64 | LogNormal | 0.26266
D3041.021a | D3041.021a | HVAC Stainless Steel Ducting less than 6 sq. ft in cross sectional area, SDC A or B | 473.49 | LogNormal | 0.31794 | 6321.65 | LogNormal | 0.31085 | [9 empty] | 6083.26 | LogNormal | 0.31794 | 75952.85 | LogNormal | 0.31085
D3041.021b | D3041.021b | HVAC Stainless Steel Ducting less than 6 sq. ft in cross sectional area, SDC C | 473.49 | LogNormal | 0.31794 | 6321.65 | LogNormal | 0.31085 | [9 empty] | 6083.26 | LogNormal | 0.31794 | 75952.85 | LogNormal | 0.31085
D3041.021c | D3041.021c | HVAC Stainless Steel Ducting less than 6 sq. ft in cross sectional area, SDC D, E, or F | 473.49 | LogNormal | 0.31794 | 6321.65 | LogNormal | 0.31085 | [9 empty] | 6083.26 | LogNormal | 0.31794 | 75952.85 | LogNormal | 0.31085
D3041.021d | D3041.021d | HVAC Stainless Steel Ducting less than 6 sq. ft in cross sectional area, SDC D, E, or F (OSHPD or sim) | 473.49 | LogNormal | 0.31794 | 6321.65 | LogNormal | 0.31085 | [9 empty] | 6083.26 | LogNormal | 0.31794 | 75952.85 | LogNormal | 0.31085
D3041.022a | D3041.022a | HVAC Stainless Steel Ducting - 6 sq. ft cross sectional area or greater, SDC A or B | 784.43 | LogNormal | 0.28057 | 8474.69 | LogNormal | 0.28448 | [9 empty] | 10049.13 | LogNormal | 0.28057 | 102704.18 | LogNormal | 0.28448
D3041.022b | D3041.022b | HVAC Stainless Steel Ducting - 6 sq. ft cross sectional area or greater, SDC C | 784.43 | LogNormal | 0.28057 | 8474.69 | LogNormal | 0.28448 | [9 empty] | 10049.13 | LogNormal | 0.28057 | 102704.18 | LogNormal | 0.28448
D3041.022c | D3041.022c | HVAC Stainless Steel Ducting - 6 sq. ft cross sectional area or greater, SDC D, E, or F | 784.43 | LogNormal | 0.28057 | 8474.69 | LogNormal | 0.28448 | [9 empty] | 10049.13 | LogNormal | 0.28057 | 102704.18 | LogNormal | 0.28448
D3041.022d | D3041.022d | HVAC Stainless Steel Ducting - 6 sq. ft cross sectional area or greater, SDC D, E, or F (OSHPD or sim) | 784.43 | LogNormal | 0.28057 | 8474.69 | LogNormal | 0.28448 | [9 empty] | 10049.13 | LogNormal | 0.28057 | 102704.18 | LogNormal | 0.28448
D3041.031a | D3041.031a | HVAC Drops / Diffusers in suspended ceilings - No independent safety wires, SDC A or B | 729.3 | Normal | 0.32429 | [12 empty] | 7977.8 | Normal | 0.32429
D3041.031b | D3041.031b | HVAC Drops / Diffusers in suspended ceilings - No independent safety wires, SDC C | 729.3 | Normal | 0.32429 | [12 empty] | 7977.8 | Normal | 0.32429
D3041.032a | D3041.032a | HVAC Drops / Diffusers without ceilings - supported by ducting only - No independent safety wires, SDC A or B | 729.3 | Normal | 0.32429 | [12 empty] | 7977.8 | Normal | 0.32429
D3041.032b | D3041.032b | HVAC Drops / Diffusers without ceilings - supported by ducting only - No independent safety wires, SDC C | 729.3 | Normal | 0.32429 | [12 empty] | 7977.8 | Normal | 0.32429
D3041.032c | D3041.032c | HVAC Drops / Diffusers without ceilings - supported by ducting only - No independent safety wires, SDC D, E, or F | 729.3 | Normal | 0.32429 | [12 empty] | 7977.8 | Normal | 0.32429
D3041.032d | D3041.032d | HVAC Drops / Diffusers without ceilings - supported by ducting only - No independent safety wires, SDC D, E, or F (OSHPD or sim) | 729.3 | Normal | 0.32429 | [12 empty] | 7977.8 | Normal | 0.32429
D3041.041a | D3041.041a | Variable Air Volume (VAV) box with in-line coil, SDC A or B | 5526.1 | LogNormal | 0.38604 | [12 empty] | 64986.7 | LogNormal | 0.38604
D3041.041b | D3041.041b | Variable Air Volume (VAV) box with in-line coil, SDC C | 5526.1 | LogNormal | 0.38604 | [12 empty] | 64986.7 | LogNormal | 0.38604
D3041.101a | D3041.101a | HVAC Fan - Capacity: all - Unanchored equipment that is not vibration isolated - Equipment fragility only | 1419.94 | LogNormal | 0.28625 | [12 empty] | 16559.49 | LogNormal | 0.28625
D3041.102a | D3041.102a | HVAC Fan - Capacity: all - Vibration isolated equipment that is not snubbed or restrained - Anchorage fragility only | 103.43 | LogNormal | 0.42405 | 1523.37 | LogNormal | 0.31019 | [9 empty] | 3091.5 | LogNormal | 0.42405 | 19650.99 | LogNormal | 0.31019
D3041.102b | D3041.102b | HVAC Fan - Capacity: all - Vibration isolated equipment that is not snubbed or restrained - Equipment fragility only | 1419.94 | LogNormal | 0.28625 | [12 empty] | 16559.49 | LogNormal | 0.28625
D3041.102c | D3041.102c | HVAC Fan - Capacity: all - Vibration isolated equipment that is not snubbed or restrained - Combined anchorage/isolator & equipment fragility | 103.43 | LogNormal | 0.42405 | 1523.37 | LogNormal | 0.31019 | 1419.94 | LogNormal | 0.28625 | [6 empty] | 3091.5 | LogNormal | 0.42405 | 19650.99 | LogNormal | 0.31019 | 16559.49 | LogNormal | 0.28625
D3041.103a | D3041.103a | HVAC Fan - Capacity: all - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only | 103.43 | LogNormal | 0.42405 | 1523.37 | LogNormal | 0.31019 | [9 empty] | 3091.5 | LogNormal | 0.42405 | 19650.99 | LogNormal | 0.31019
D3041.103b | D3041.103b | HVAC Fan - Capacity: all - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only | 1419.94 | LogNormal | 0.28625 | [12 empty] | 16559.49 | LogNormal | 0.28625
D3041.103c | D3041.103c | HVAC Fan - Capacity: all - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | 103.43 | LogNormal | 0.42405 | 1523.37 | LogNormal | 0.31019 | 1419.94 | LogNormal | 0.28625 | [6 empty] | 3091.5 | LogNormal | 0.42405 | 19650.99 | LogNormal | 0.31019 | 16559.49 | LogNormal | 0.28625
D3052.011a | D3052.011a | Air Handling Unit - Capacity: <5000 CFM - Unanchored equipment that is not vibration isolated - Equipment fragility only | 70.65 | LogNormal | 0.2921 | 16028.86 | LogNormal | 0.29981 | [9 empty] | 1344.48 | LogNormal | 0.2921 | 186138.86 | LogNormal | 0.29981
D3052.011b | D3052.011b | Air Handling Unit - Capacity: 5000 to <10000 CFM - Unanchored equipment that is not vibration isolated - Equipment fragility only | 105.97 | LogNormal | 0.30589 | 32527.73 | LogNormal | 0.30374 | [9 empty] | 2016.71 | LogNormal | 0.30589 | 377790.81 | LogNormal | 0.30374
D3052.011c | D3052.011c | Air Handling Unit - Capacity: 10000 to <25000 CFM - Unanchored equipment that is not vibration isolated - Equipment fragility only | 141.3 | LogNormal | 0.30308 | 69472.1 | LogNormal | 0.30483 | [9 empty] | 2688.95 | LogNormal | 0.30308 | 806151.91 | LogNormal | 0.30483
D3052.011d | D3052.011d | Air Handling Unit - Capacity: 25000 to <40000 CFM - Unanchored equipment that is not vibration isolated - Equipment fragility only | 141.3 | LogNormal | 0.30308 | 103632.17 | LogNormal | 0.30491 | [9 empty] | 2688.95 | LogNormal | 0.30308 | 1201698.07 | LogNormal | 0.30491
D3052.013a | D3052.013a | Air Handling Unit - Capacity: <5000 CFM - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only | 110.49 | LogNormal | 0.5168 | 16139.35 | LogNormal | 0.30521 | [9 empty] | 3225.95 | LogNormal | 0.5168 | 189364.81 | LogNormal | 0.30521
D3052.013b | D3052.013b | Air Handling Unit - Capacity: <5000 CFM - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only | 70.65 | LogNormal | 0.2921 | 16028.86 | LogNormal | 0.29981 | [9 empty] | 1344.48 | LogNormal | 0.2921 | 186138.86 | LogNormal | 0.29981
D3052.013c | D3052.013c | Air Handling Unit - Capacity: <5000 CFM - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | 110.49 | LogNormal | 0.5168 | 16139.35 | LogNormal | 0.30521 | 70.65 | LogNormal | 0.2921 | 16028.86 | LogNormal | 0.29981 |  |  |  | 3225.95 | LogNormal | 0.5168 | 189364.81 | LogNormal | 0.30521 | 1344.48 | LogNormal | 0.2921 | 186138.86 | LogNormal | 0.29981
D3052.013d | D3052.013d | Air Handling Unit - Capacity: 5000 to <10000 CFM - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only | 168.31 | Normal | 0.47039 | 32696.04 | LogNormal | 0.30706 | [9 empty] | 5000.18 | Normal | 0.47039 | 382790.99 | LogNormal | 0.30706
D3052.013e | D3052.013e | Air Handling Unit - Capacity: 5000 to <10000 CFM - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only | 105.97 | LogNormal | 0.30589 | 32527.73 | LogNormal | 0.30374 | [9 empty] | 2016.71 | LogNormal | 0.30589 | 377790.81 | LogNormal | 0.30374
D3052.013f | D3052.013f | Air Handling Unit - Capacity: 5000 to <10000 CFM - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | 168.31 | Normal | 0.47039 | 32696.04 | LogNormal | 0.30706 | 105.97 | LogNormal | 0.30589 | 32527.73 | LogNormal | 0.30374 |  |  |  | 5000.18 | Normal | 0.47039 | 382790.99 | LogNormal | 0.30706 | 2016.71 | LogNormal | 0.30589 | 377790.81 | LogNormal | 0.30374
D3052.013g | D3052.013g | Air Handling Unit - Capacity: 10000 to <25000 CFM - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only | 245.4 | Normal | 0.3882 | 69717.51 | LogNormal | 0.30605 | [9 empty] | 7365.83 | Normal | 0.3882 | 813517.74 | LogNormal | 0.30605
D3052.013h | D3052.013h | Air Handling Unit - Capacity: 10000 to <25000 CFM - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only | 141.3 | LogNormal | 0.30308 | 69472.1 | LogNormal | 0.30483 | [9 empty] | 2688.95 | LogNormal | 0.30308 | 806151.91 | LogNormal | 0.30483
D3052.013i | D3052.013i | Air Handling Unit - Capacity: 10000 to <25000 CFM - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | 245.4 | Normal | 0.3882 | 69717.51 | LogNormal | 0.30605 | 141.3 | LogNormal | 0.30308 | 69472.1 | LogNormal | 0.30483 |  |  |  | 7365.83 | Normal | 0.3882 | 813517.74 | LogNormal | 0.30605 | 2688.95 | LogNormal | 0.30308 | 806151.91 | LogNormal | 0.30483
D3052.013j | D3052.013j | Air Handling Unit - Capacity: 25000 to <40000 CFM - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only | 245.4 | LogNormal | 0.38177 | 103877.58 | LogNormal | 0.30573 | [9 empty] | 7365.83 | LogNormal | 0.38177 | 1209063.9 | LogNormal | 0.30573
D3052.013k | D3052.013k | Air Handling Unit - Capacity: 25000 to <40000 CFM - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only | 141.3 | LogNormal | 0.30308 | 103632.17 | LogNormal | 0.30491 | [9 empty] | 2688.95 | LogNormal | 0.30308 | 1201698.07 | LogNormal | 0.30491
D3052.013l | D3052.013l | Air Handling Unit - Capacity: 25000 to <40000 CFM - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | 245.4 | LogNormal | 0.38177 | 103877.58 | LogNormal | 0.30573 | 141.3 | LogNormal | 0.30308 | 103632.17 | LogNormal | 0.30491 |  |  |  | 7365.83 | LogNormal | 0.38177 | 1209063.9 | LogNormal | 0.30573 | 2688.95 | LogNormal | 0.30308 | 1201698.07 | LogNormal | 0.30491
D3067.011a | D3067.011a | Control Panel - Capacity: all - Unanchored equipment that is not vibration isolated - Equipment fragility only | 865.45 | Normal | 0.30958 | [12 empty] | 16469.83 | Normal | 0.30958
D3067.012a | D3067.012a | Control Panel - Capacity: all - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only | 64.88 | Normal | 0.37725 | 930.33 | Normal | 0.31582 | [9 empty] | 1908.68 | Normal | 0.37725 | 18378.51 | Normal | 0.31582
D3067.012b | D3067.012b | Control Panel - Capacity: all - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only | 865.45 | Normal | 0.30958 | [12 empty] | 16469.83 | Normal | 0.30958
D3067.012c | D3067.012c | Control Panel - Capacity: all - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | 64.88 | Normal | 0.37725 | 930.33 | Normal | 0.31582 | 865.45 | Normal | 0.30958 | [6 empty] | 1908.68 | Normal | 0.37725 | 18378.51 | Normal | 0.31582 | 16469.83 | Normal | 0.30958
D4011.021a | D4011.021a | Fire Sprinkler Water Piping - Horizontal Mains and Branches - Old Style Victaulic - Thin Wall Steel - No bracing, SDC A or B, PIPING FRAGILITY | 33 | LogNormal | 0.69527 | 363.5 | LogNormal | 0.47626 | [9 empty] | 864.5 | LogNormal | 0.69527 | 9221.5 | LogNormal | 0.47626
D4011.022a | D4011.022a | Fire Sprinkler Water Piping - Horizontal Mains and Branches - Old Style Victaulic - Thin Wall Steel - No bracing, SDC C, PIPING FRAGILITY | 33 | LogNormal | 0.69527 | 363.5 | LogNormal | 0.47626 | [9 empty] | 864.5 | LogNormal | 0.69527 | 9221.5 | LogNormal | 0.47626
D4011.023a | D4011.023a | Fire Sprinkler Water Piping - Horizontal Mains and Branches - Old Style Victaulic - Thin Wall Steel - Poorly designed bracing, SDC D, E, or F , PIPING FRAGILITY | 33 | LogNormal | 0.69527 | 363.5 | LogNormal | 0.47626 | [9 empty] | 864.5 | LogNormal | 0.69527 | 9221.5 | LogNormal | 0.47626
D4011.024a | D4011.024a | Fire Sprinkler Water Piping - Horizontal Mains and Branches - Old Style Victaulic - Thin Wall Steel - with designed bracing, SDC D, E, or F (OSHPD or sim), PIPING FRAGILITY | 33 | LogNormal | 0.69527 | 363.5 | LogNormal | 0.47626 | [9 empty] | 864.5 | LogNormal | 0.69527 | 9221.5 | LogNormal | 0.47626
D4011.031a | D4011.031a | Fire Sprinkler Drop Standard Threaded Steel - Dropping into unbraced lay-in tile SOFT ceiling - 6 ft. long drop maximum, SDC A or B | 75 | LogNormal | 0.44368 | 75 | LogNormal | 0.44368 | [9 empty] | 865 | LogNormal | 0.44368 | 865 | LogNormal | 0.44368
D4011.032a | D4011.032a | Fire Sprinkler Drop Standard Threaded Steel - Dropping into unbraced lay-in tile SOFT ceiling - 6 ft. long drop maximum, SDC C | 75 | LogNormal | 0.44368 | 75 | LogNormal | 0.44368 | [9 empty] | 865 | LogNormal | 0.44368 | 865 | LogNormal | 0.44368
D4011.033a | D4011.033a | Fire Sprinkler Drop Standard Threaded Steel - Dropping into unbraced lay-in tile SOFT ceiling - 6 ft. long drop maximum, SDC D, E, or F | 75 | LogNormal | 0.44368 | [12 empty] | 865 | LogNormal | 0.44368
D4011.034a | D4011.034a | Fire Sprinkler Drop Standard Threaded Steel - Dropping into unbraced lay-in tile SOFT ceiling - 6 ft. long drop maximum, SDC D, E, or F (OSHPD or sim) | 75 | LogNormal | 0.44368 | [12 empty] | 865 | LogNormal | 0.44368
D4011.041a | D4011.041a | Fire Sprinkler Drop Standard Threaded Steel - Dropping into unbraced lay-in tile HARD ceiling - 6 ft. long drop maximum, SDC A or B | 75 | LogNormal | 0.44368 | 75 | LogNormal | 0.44368 | [9 empty] | 865 | LogNormal | 0.44368 | 865 | LogNormal | 0.44368
D4011.042a | D4011.042a | Fire Sprinkler Drop Standard Threaded Steel - Dropping into unbraced lay-in tile HARD ceiling - 6 ft. long drop maximum, SDC C | 75 | LogNormal | 0.44368 | 75 | LogNormal | 0.44368 | [9 empty] | 865 | LogNormal | 0.44368 | 865 | LogNormal | 0.44368
D4011.053a | D4011.053a | Fire Sprinkler Drop Standard Threaded Steel - Dropping into braced lay-in tile SOFT ceiling - 6 ft. long drop maximum, SDC D, E, or F | 75 | LogNormal | 0.44368 | 75 | LogNormal | 0.44368 | [9 empty] | 865 | LogNormal | 0.44368 | 865 | LogNormal | 0.44368
D4011.054a | D4011.054a | Fire Sprinkler Drop Standard Threaded Steel - Dropping into braced lay-in tile SOFT ceiling - 6 ft. long drop maximum, SDC D, E, or F (OSHPD or sim) | 75 | LogNormal | 0.44368 | 75 | LogNormal | 0.44368 | [9 empty] | 865 | LogNormal | 0.44368 | 865 | LogNormal | 0.44368
D4011.063a | D4011.063a | Fire Sprinkler Drop Standard Threaded Steel - Dropping into braced lay-in tile HARD ceiling - 6 ft. long drop maximum, SDC D, E, or F | 75 | LogNormal | 0.44368 | 75 | LogNormal | 0.44368 | [9 empty] | 865 | LogNormal | 0.44368 | 865 | LogNormal | 0.44368
D4011.064a | D4011.064a | Fire Sprinkler Drop Standard Threaded Steel - Dropping into braced lay-in tile HARD ceiling - 6 ft. long drop maximum, SDC D, E, or F (OSHPD or sim) | 75 | LogNormal | 0.44368 | 75 | LogNormal | 0.44368 | [9 empty] | 865 | LogNormal | 0.44368 | 865 | LogNormal | 0.44368
D4011.071a | D4011.071a | Fire Sprinkler Drop Standard Threaded Steel - No Ceiling - 6 ft. long drop maximum, SDC A or B | 75 | LogNormal | 0.44368 | 75 | LogNormal | 0.44368 | [9 empty] | 865 | LogNormal | 0.44368 | 865 | LogNormal | 0.44368
D4011.072a | D4011.072a | Fire Sprinkler Drop Standard Threaded Steel - No Ceiling - 6 ft. long drop maximum, SDC C | 75 | LogNormal | 0.44368 | 75 | LogNormal | 0.44368 | [9 empty] | 865 | LogNormal | 0.44368 | 865 | LogNormal | 0.44368
D4011.073a | D4011.073a | Fire Sprinkler Drop Standard Threaded Steel - No Ceiling - 6 ft. long drop maximum, SDC D, E, or F | 75 | LogNormal | 0.44368 | 75 | LogNormal | 0.44368 | [9 empty] | 865 | LogNormal | 0.44368 | 865 | LogNormal | 0.44368
D4011.074a | D4011.074a | Fire Sprinkler Drop Standard Threaded Steel - No Ceiling - 6 ft. long drop maximum, SDC D, E, or F (OSHPD or sim) | 75 | LogNormal | 0.44368 | 75 | LogNormal | 0.44368 | [9 empty] | 865 | LogNormal | 0.44368 | 865 | LogNormal | 0.44368
D5011.011a | D5011.011a | Transformer/primary service - Capacity: <100 kVA - Unanchored equipment that is not vibration isolated - Equipment fragility only | 1674.47 | LogNormal | 0.3125 | [12 empty] | 30150.25 | LogNormal | 0.3125
D5011.011b | D5011.011b | Transformer/primary service - Capacity: 100 to <350 kVA - Unanchored equipment that is not vibration isolated - Equipment fragility only | 5620.5 | LogNormal | 0.31069 | [12 empty] | 100097.72 | LogNormal | 0.31069
D5011.011c | D5011.011c | Transformer/primary service - Capacity: 350 to <750 kVA - Unanchored equipment that is not vibration isolated - Equipment fragility only | 10110.63 | LogNormal | 0.30878 | [12 empty] | 178683.82 | LogNormal | 0.30878
D5011.011d | D5011.011d | Transformer/primary service - Capacity: 750 to 1500 kVA - Unanchored equipment that is not vibration isolated - Equipment fragility only | 13477.24 | LogNormal | 0.30952 | [12 empty] | 239320.43 | LogNormal | 0.30952
D5011.013a | D5011.013a | Transformer/primary service - Capacity: <100 kVA - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only | 110.49 | LogNormal | 0.5168 | 1784.97 | LogNormal | 0.33232 | [9 empty] | 3225.95 | LogNormal | 0.5168 | 33376.2 | LogNormal | 0.33232
D5011.013b | D5011.013b | Transformer/primary service - Capacity: <100 kVA - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only | 1674.47 | LogNormal | 0.3125 | [12 empty] | 30150.25 | LogNormal | 0.3125
D5011.013c | D5011.013c | Transformer/primary service - Capacity: <100 kVA - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | 110.49 | LogNormal | 0.5168 | 1784.97 | LogNormal | 0.33232 | 1674.47 | LogNormal | 0.3125 | [6 empty] | 3225.95 | LogNormal | 0.5168 | 33376.2 | LogNormal | 0.33232 | 30150.25 | LogNormal | 0.3125
D5011.013d | D5011.013d | Transformer/primary service - Capacity: 100 to <350 kVA - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only | 168.31 | Normal | 0.47039 | 5788.82 | LogNormal | 0.31851 | [9 empty] | 5000.18 | Normal | 0.47039 | 105097.91 | LogNormal | 0.31851
D5011.013e | D5011.013e | Transformer/primary service - Capacity: 100 to <350 kVA - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only | 5620.5 | LogNormal | 0.31069 | [12 empty] | 100097.72 | LogNormal | 0.31069
D5011.013f | D5011.013f | Transformer/primary service - Capacity: 100 to <350 kVA - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | 168.31 | Normal | 0.47039 | 5788.82 | LogNormal | 0.31851 | 5620.5 | LogNormal | 0.31069 | [6 empty] | 5000.18 | Normal | 0.47039 | 105097.91 | LogNormal | 0.31851 | 100097.72 | LogNormal | 0.31069
D5011.013g | D5011.013g | Transformer/primary service - Capacity: 350 to <750 kVA - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only | 245.4 | Normal | 0.3882 | 10356.03 | LogNormal | 0.31214 | [9 empty] | 7365.83 | Normal | 0.3882 | 186049.65 | LogNormal | 0.31214
D5011.013h | D5011.013h | Transformer/primary service - Capacity: 350 to <750 kVA - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only | 10110.63 | LogNormal | 0.30878 | [12 empty] | 178683.82 | LogNormal | 0.30878
D5011.013i | D5011.013i | Transformer/primary service - Capacity: 350 to <750 kVA - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | 245.4 | Normal | 0.3882 | 10356.03 | LogNormal | 0.31214 | 10110.63 | LogNormal | 0.30878 | [6 empty] | 7365.83 | Normal | 0.3882 | 186049.65 | LogNormal | 0.31214 | 178683.82 | LogNormal | 0.30878
D5011.013j | D5011.013j | Transformer/primary service - Capacity: 750 to 1500 kVA - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only | 245.4 | LogNormal | 0.38177 | 13722.64 | LogNormal | 0.31204 | [9 empty] | 7365.83 | LogNormal | 0.38177 | 246686.26 | LogNormal | 0.31204
D5011.013k | D5011.013k | Transformer/primary service - Capacity: 750 to 1500 kVA - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only | 13477.24 | LogNormal | 0.30952 | [12 empty] | 239320.43 | LogNormal | 0.30952
D5011.013l | D5011.013l | Transformer/primary service - Capacity: 750 to 1500 kVA - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | 245.4 | LogNormal | 0.38177 | 13722.64 | LogNormal | 0.31204 | 13477.24 | LogNormal | 0.30952 | [6 empty] | 7365.83 | LogNormal | 0.38177 | 246686.26 | LogNormal | 0.31204 | 239320.43 | LogNormal | 0.30952
D5012.013a | D5012.013a | Motor Control Center - Capacity: all - Unanchored equipment that is not vibration isolated - Equipment fragility only | 865.45 | Normal | 0.30958 | [12 empty] | 16469.83 | Normal | 0.30958
D5012.013b | D5012.013b | Motor Control Center - Capacity: all - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only | 64.88 | Normal | 0.37725 | 930.33 | Normal | 0.31582 | [9 empty] | 1908.68 | Normal | 0.37725 | 18378.51 | Normal | 0.31582
D5012.013c | D5012.013c | Motor Control Center - Capacity: all - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only | 865.45 | Normal | 0.30958 | [12 empty] | 16469.83 | Normal | 0.30958
D5012.013d | D5012.013d | Motor Control Center - Capacity: all - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | 64.88 | Normal | 0.37725 | 930.33 | Normal | 0.31582 | 865.45 | Normal | 0.30958 | [6 empty] | 1908.68 | Normal | 0.37725 | 18378.51 | Normal | 0.31582 | 16469.83 | Normal | 0.30958
D5012.021a | D5012.021a | Low Voltage Switchgear - Capacity: 100 to <350 Amp - Unanchored equipment that is not vibration isolated - Equipment fragility only | 1992.39 | LogNormal | 0.29532 | [12 empty] | 36200.39 | LogNormal | 0.29532
D5012.021b | D5012.021b | Low Voltage Switchgear - Capacity: 350 to <750 Amp - Unanchored equipment that is not vibration isolated - Equipment fragility only | 4083.89 | Normal | 0.25751 | [12 empty] | 70855.37 | Normal | 0.25751
D5012.021c | D5012.021c | Low Voltage Switchgear - Capacity: 750 to <1200 Amp - Unanchored equipment that is not vibration isolated - Equipment fragility only | 7249.35 | Normal | 0.26039 | [12 empty] | 124232.54 | Normal | 0.26039
D5012.021d | D5012.021d | Low Voltage Switchgear - Capacity: 1200 to 2000 Amp - Unanchored equipment that is not vibration isolated - Equipment fragility only | 12163.17 | Normal | 0.25916 | [12 empty] | 214313.18 | Normal | 0.25916
D5012.023a | D5012.023a | Low Voltage Switchgear - Capacity: 100 to <350 Amp - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only | 64.88 | Normal | 0.37725 | 2057.28 | LogNormal | 0.2985 | [9 empty] | 1908.68 | Normal | 0.37725 | 38109.07 | LogNormal | 0.2985
D5012.023b | D5012.023b | Low Voltage Switchgear - Capacity: 100 to <350 Amp - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only | 1992.39 | LogNormal | 0.29532 | [12 empty] | 36200.39 | LogNormal | 0.29532
D5012.023c | D5012.023c | Low Voltage Switchgear - Capacity: 100 to <350 Amp - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | 64.88 | Normal | 0.37725 | 2057.28 | LogNormal | 0.2985 | 1992.39 | LogNormal | 0.29532 | [6 empty] | 1908.68 | Normal | 0.37725 | 38109.07 | LogNormal | 0.2985 | 36200.39 | LogNormal | 0.29532
D5012.023d | D5012.023d | Low Voltage Switchgear - Capacity: 350 to <750 Amp - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only | 91.22 | LogNormal | 0.48342 | 4175.11 | LogNormal | 0.31195 | [9 empty] | 2634.54 | LogNormal | 0.48342 | 73489.91 | LogNormal | 0.31195
D5012.023e | D5012.023e | Low Voltage Switchgear - Capacity: 350 to <750 Amp - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only | 4083.89 | Normal | 0.25751 | [12 empty] | 70855.37 | Normal | 0.25751
D5012.023f | D5012.023f | Low Voltage Switchgear - Capacity: 350 to <750 Amp - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | 91.22 | LogNormal | 0.48342 | 4175.11 | LogNormal | 0.31195 | 4083.89 | Normal | 0.25751 | [6 empty] | 2634.54 | LogNormal | 0.48342 | 73489.91 | LogNormal | 0.31195 | 70855.37 | Normal | 0.25751
D5012.023g | D5012.023g | Low Voltage Switchgear - Capacity: 750 to <1200 Amp - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only | 129.77 | LogNormal | 0.41813 | 7379.11 | LogNormal | 0.31645 | [9 empty] | 3817.36 | LogNormal | 0.41813 | 128049.91 | LogNormal | 0.31645
D5012.023h | D5012.023h | Low Voltage Switchgear - Capacity: 750 to <1200 Amp - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only | 7249.35 | Normal | 0.26039 | [12 empty] | 124232.54 | Normal | 0.26039
D5012.023i | D5012.023i | Low Voltage Switchgear - Capacity: 750 to <1200 Amp - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | 129.77 | LogNormal | 0.41813 | 7379.11 | LogNormal | 0.31645 | 7249.35 | Normal | 0.26038 | [6 empty] | 3817.36 | LogNormal | 0.41813 | 128049.91 | LogNormal | 0.31645 | 124232.54 | Normal | 0.26038
D5012.023j | D5012.023j | Low Voltage Switchgear - Capacity: 1200 to 2000 Amp - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only | 129.77 | LogNormal | 0.41813 | 12292.93 | LogNormal | 0.31155 | [9 empty] | 3817.36 | LogNormal | 0.41813 | 218130.54 | LogNormal | 0.31155
D5012.023k | D5012.023k | Low Voltage Switchgear - Capacity: 1200 to 2000 Amp - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only | 12163.17 | Normal | 0.25916 | [12 empty] | 214313.18 | Normal | 0.25916
D5012.023l | D5012.023l | Low Voltage Switchgear - Capacity: 1200 to 2000 Amp - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | 129.77 | LogNormal | 0.41813 | 12292.93 | LogNormal | 0.31155 | 12163.17 | Normal | 0.25916 | [6 empty] | 3817.36 | LogNormal | 0.41813 | 218130.54 | LogNormal | 0.31155 | 214313.18 | Normal | 0.25916
D5012.031a | D5012.031a | Distribution Panel - Capacity: 100 to <350 Amp - Unanchored equipment that is not vibration isolated - Equipment fragility only | 1992.39 | LogNormal | 0.29532 | [12 empty] | 36200.39 | LogNormal | 0.29532
D5012.031b | D5012.031b | Distribution Panel - Capacity: 350 to <750 Amp - Unanchored equipment that is not vibration isolated - Equipment fragility only | 4083.89 | Normal | 0.25751 | [12 empty] | 70855.37 | Normal | 0.25751
D5012.031c | D5012.031c | Distribution Panel - Capacity: 750 to <1200 Amp - Unanchored equipment that is not vibration isolated - Equipment fragility only | 7249.35 | Normal | 0.26039 | [12 empty] | 124232.54 | Normal | 0.26039
D5012.031d | D5012.031d | Distribution Panel - Capacity: 1200 to 2000 Amp - Unanchored equipment that is not vibration isolated - Equipment fragility only | 12163.17 | Normal | 0.25916 | [12 empty] | 214313.18 | Normal | 0.25916
D5012.033a | D5012.033a | Distribution Panel - Capacity: 100 to <350 Amp - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only | 64.88 | Normal | 0.37725 | 2057.28 | LogNormal | 0.2985 | [9 empty] | 1908.68 | Normal | 0.37725 | 38109.07 | LogNormal | 0.2985
D5012.033b | D5012.033b | Distribution Panel - Capacity: 100 to <350 Amp - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only | 1992.39 | LogNormal | 0.29532 | [12 empty] | 36200.39 | LogNormal | 0.29532
D5012.033c | D5012.033c | Distribution Panel - Capacity: 100 to <350 Amp - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | 64.88 | Normal | 0.37725 | 2057.28 | LogNormal | 0.2985 | 1992.39 | LogNormal | 0.29532 | [6 empty] | 1908.68 | Normal | 0.37725 | 38109.07 | LogNormal | 0.2985 | 36200.39 | LogNormal | 0.29532
D5012.033d | D5012.033d | Distribution Panel - Capacity: 350 to <750 Amp - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only | 91.22 | LogNormal | 0.48342 | 4175.11 | LogNormal | 0.31195 | [9 empty] | 2634.54 | LogNormal | 0.48342 | 73489.91 | LogNormal | 0.31195
D5012.033e | D5012.033e | Distribution Panel - Capacity: 350 to <750 Amp - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only | 4083.89 | Normal | 0.25751 | [12 empty] | 70855.37 | Normal | 0.25751
D5012.033f | D5012.033f | Distribution Panel - Capacity: 350 to <750 Amp - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | 91.22 | LogNormal | 0.48342 | 4175.11 | LogNormal | 0.31195 | 4083.89 | Normal | 0.25751 | [6 empty] | 2634.54 | LogNormal | 0.48342 | 73489.91 | LogNormal | 0.31195 | 70855.37 | Normal | 0.25751
D5012.033g | D5012.033g | Distribution Panel - Capacity: 750 to <1200 Amp - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only | 129.77 | LogNormal | 0.41813 | 7379.11 | LogNormal | 0.31645 | [9 empty] | 3817.36 | LogNormal | 0.41813 | 128049.91 | LogNormal | 0.31645
D5012.033h | D5012.033h | Distribution Panel - Capacity: 750 to <1200 Amp - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only | 7249.35 | Normal | 0.26039 | [12 empty] | 124232.54 | Normal | 0.26039
D5012.033i | D5012.033i | Distribution Panel - Capacity: 750 to <1200 Amp - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | 129.77 | LogNormal | 0.41813 | 7379.11 | LogNormal | 0.31645 | 7249.35 | Normal | 0.26038 | [6 empty] | 3817.36 | LogNormal | 0.41813 | 128049.91 | LogNormal | 0.31645 | 124232.54 | Normal | 0.26038
D5012.033j | D5012.033j | Distribution Panel - Capacity: 1200 to 2000 Amp - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only | 129.77 | LogNormal | 0.41813 | 12292.93 | LogNormal | 0.31155 | [9 empty] | 3817.36 | LogNormal | 0.41813 | 218130.54 | LogNormal | 0.31155
D5012.033k | D5012.033k | Distribution Panel - Capacity: 1200 to 2000 Amp - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only | 12163.17 | Normal | 0.25916 | [12 empty] | 214313.18 | Normal | 0.25916
D5012.033l | D5012.033l | Distribution Panel - Capacity: 1200 to 2000 Amp - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | 129.77 | LogNormal | 0.41813 | 12292.93 | LogNormal | 0.31155 | 12163.17 | Normal | 0.25916 | [6 empty] | 3817.36 | LogNormal | 0.41813 | 218130.54 | LogNormal | 0.31155 | 214313.18 | Normal | 0.25916
D5092.011a | D5092.011a | Battery Rack - Capacity: all - Unanchored equipment that is not vibration isolated - Equipment fragility only | 1695.57 | LogNormal | 0.26787 | 63.49 | Normal | 0.37947 | 1301.3 | Normal | 0.34673 | [6 empty] | 32267.43 | LogNormal | 0.26787 | 1584.24 | Normal | 0.37947 | 29003.39 | Normal | 0.34673
D5092.013a | D5092.013a | Battery Rack - Capacity: all - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only | 161.25 | Normal | 0.28598 | 3158.12 | LogNormal | 0.28029 | [9 empty] | 4865.74 | Normal | 0.28598 | 66136.55 | LogNormal | 0.28029
D5092.013b | D5092.013b | Battery Rack - Capacity: all - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only | 1695.57 | LogNormal | 0.26787 | 63.49 | Normal | 0.37947 | 1301.3 | Normal | 0.34673 | [6 empty] | 32267.43 | LogNormal | 0.26787 | 1584.24 | Normal | 0.37947 | 29003.39 | Normal | 0.34673
D5092.013c | D5092.013c | Battery Rack - Capacity: all - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | 161.25 | Normal | 0.28598 | 3158.12 | LogNormal | 0.28029 | 1695.57 | LogNormal | 0.26787 | 1759.07 | LogNormal | 0.27154 | 3221.61 | LogNormal | 0.28311 | 4865.74 | Normal | 0.28598 | 66136.55 | LogNormal | 0.28029 | 32267.43 | LogNormal | 0.26787 | 33851.66 | LogNormal | 0.27154 | 67720.79 | LogNormal | 0.28311
D5092.021a | D5092.021a | Battery Charger - Capacity: all - Unanchored equipment that is not vibration isolated - Equipment fragility only | 203.47 | Normal | 0.29293 | 2561.02 | Normal | 0.28026 | [9 empty] | 3872.09 | Normal | 0.29293 | 48737.26 | Normal | 0.28026
D5092.023a | D5092.023a | Battery Charger - Capacity: all - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only | 103.43 | Normal | 0.32005 | 2664.45 | Normal | 0.28204 | [9 empty] | 3091.5 | Normal | 0.32005 | 51828.76 | Normal | 0.28204
D5092.023b | D5092.023b | Battery Charger - Capacity: all - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only | 203.47 | Normal | 0.29293 | 2561.02 | Normal | 0.28026 | [9 empty] | 3872.09 | Normal | 0.29293 | 48737.26 | Normal | 0.28026
D5092.023c | D5092.023c | Battery Charger - Capacity: all - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | 103.43 | Normal | 0.32005 | 2664.45 | Normal | 0.28204 | 2561.02 | Normal | 0.28026 | 2561.02 | Normal | 0.28026 |  |  |  | 3091.5 | Normal | 0.32005 | 51828.76 | Normal | 0.28204 | 48737.26 | Normal | 0.28026 | 48737.26 | Normal | 0.28026
D5092.031a | D5092.031a | Diesel generator - Capacity: 100 to <350 kVA - Unanchored equipment that is not vibration isolated - Equipment fragility only | 8.28 | LogNormal | 0.30308 | 103.5 | LogNormal | 0.30262 | 20.7 | LogNormal | 0.30079 | 20.7 | LogNormal | 0.30079 |  |  |  | 182.89 | LogNormal | 0.30308 | 2286.09 | LogNormal | 0.30262 | 457.22 | LogNormal | 0.30079 | 457.22 | LogNormal | 0.30079
D5092.031b | D5092.031b | Diesel generator - Capacity: 350 to <750 kVA - Unanchored equipment that is not vibration isolated - Equipment fragility only | 16.56 | LogNormal | 0.30308 | 206.99 | LogNormal | 0.30308 | 22.61 | LogNormal | 0.30308 | 33.12 | LogNormal | 0.30308 |  |  |  | 365.77 | LogNormal | 0.30308 | 4572.17 | LogNormal | 0.30308 | 430.23 | LogNormal | 0.30308 | 731.55 | LogNormal | 0.30308
D5092.031c | D5092.031c | Diesel generator - Capacity: 750 to 1200 kVA - Unanchored equipment that is not vibration isolated - Equipment fragility only | 37.26 | LogNormal | 0.3018 | 331.19 | LogNormal | 0.30308 | 33.91 | LogNormal | 0.30308 | 49.68 | LogNormal | 0.30308 |  |  |  | 822.99 | LogNormal | 0.3018 | 7315.48 | LogNormal | 0.30308 | 645.35 | LogNormal | 0.30308 | 1097.32 | LogNormal | 0.30308
D5092.031d | D5092.031d | Diesel generator - Capacity: 1200 to 2000 kVa - Unanchored equipment that is not vibration isolated - Equipment fragility only | 62.1 | LogNormal | 0.30231 | 413.99 | LogNormal | 0.30308 | 33.91 | LogNormal | 0.30308 | 49.68 | LogNormal | 0.30308 |  |  |  | 1371.65 | LogNormal | 0.30231 | 9144.35 | LogNormal | 0.30308 | 645.35 | LogNormal | 0.30308 | 1097.32 | LogNormal | 0.30308
D5092.032a | D5092.032a | Diesel generator - Capacity: 100 to <350 kVA - Vibration isolated equipment that is not snubbed or restrained - Anchorage fragility only | 110.49 | LogNormal | 0.5168 | 24454.43 | LogNormal | 0.30495 | [9 empty] | 3225.95 | LogNormal | 0.5168 | 464784.95 | LogNormal | 0.30495
D5092.032b | D5092.032b | Diesel generator - Capacity: 100 to <350 kVA - Vibration isolated equipment that is not snubbed or restrained - Equipment fragility only | 8.28 | LogNormal | 0.30308 | 103.5 | LogNormal | 0.30262 | 20.7 | LogNormal | 0.30079 | 20.7 | LogNormal | 0.30079 |  |  |  | 182.89 | LogNormal | 0.30308 | 2286.09 | LogNormal | 0.30262 | 457.22 | LogNormal | 0.30079 | 457.22 | LogNormal | 0.30079
D5092.032c | D5092.032c | Diesel generator - Capacity: 100 to <350 kVA - Vibration isolated equipment that is not snubbed or restrained - Combined anchorage/isolator & equipment fragility | 110.49 | LogNormal | 0.5168 | 24454.43 | LogNormal | 0.30495 | 8.28 | LogNormal | 0.30308 | 103.5 | LogNormal | 0.30262 | 14.13 | LogNormal | 0.30079 | 3225.95 | LogNormal | 0.5168 | 464784.95 | LogNormal | 0.30495 | 182.89 | LogNormal | 0.30308 | 2286.09 | LogNormal | 0.30262 | 268.9 | LogNormal | 0.30079
D5092.032d | D5092.032d | Diesel generator - Capacity: 350 to <750 kVA - Vibration isolated equipment that is not snubbed or restrained - Anchorage fragility only | 168.31 | Normal | 0.47039 | 49326.2 | LogNormal | 0.30451 | [9 empty] | 5000.18 | Normal | 0.47039 | 933631.28 | LogNormal | 0.30451
D5092.032e | D5092.032e | Diesel generator - Capacity: 350 to <750 kVA - Vibration isolated equipment that is not snubbed or restrained - Equipment fragility only | 16.56 | LogNormal | 0.30308 | 206.99 | LogNormal | 0.30308 | 22.61 | LogNormal | 0.30308 | 33.12 | LogNormal | 0.30308 |  |  |  | 365.77 | LogNormal | 0.30308 | 4572.17 | LogNormal | 0.30308 | 430.23 | LogNormal | 0.30308 | 731.55 | LogNormal | 0.30308
D5092.032f | D5092.032f | Diesel generator - Capacity: 350 to <750 kVA - Vibration isolated equipment that is not snubbed or restrained - Combined anchorage/isolator & equipment fragility | 168.31 | Normal | 0.47039 | 49326.2 | LogNormal | 0.30451 | 16.56 | LogNormal | 0.30308 | 206.99 | LogNormal | 0.30308 | 22.61 | LogNormal | 0.30308 | 5000.18 | Normal | 0.47039 | 933631.28 | LogNormal | 0.30451 | 365.77 | LogNormal | 0.30308 | 4572.17 | LogNormal | 0.30308 | 430.23 | LogNormal | 0.30308
D5092.032g | D5092.032g | Diesel generator - Capacity: 750 to 1200 kVA - Vibration isolated equipment that is not snubbed or restrained - Anchorage fragility only | 245.4 | Normal | 0.3882 | 92485.37 | LogNormal | 0.30417 | [9 empty] | 7365.83 | Normal | 0.3882 | 1749003.08 | LogNormal | 0.30417
D5092.032h | D5092.032h | Diesel generator - Capacity: 750 to 1200 kVA - Vibration isolated equipment that is not snubbed or restrained - Equipment fragility only | 37.26 | LogNormal | 0.3018 | 331.19 | LogNormal | 0.30308 | 33.91 | LogNormal | 0.30308 | 49.68 | LogNormal | 0.30308 |  |  |  | 822.99 | LogNormal | 0.3018 | 7315.48 | LogNormal | 0.30308 | 645.35 | LogNormal | 0.30308 | 1097.32 | LogNormal | 0.30308
D5092.032i | D5092.032i | Diesel generator - Capacity: 750 to 1200 kVA - Vibration isolated equipment that is not snubbed or restrained - Combined anchorage/isolator & equipment fragility | 245.4 | Normal | 0.3882 | 92485.37 | LogNormal | 0.30417 | 37.26 | LogNormal | 0.3018 | 331.19 | LogNormal | 0.30308 | 33.91 | LogNormal | 0.30308 | 7365.83 | Normal | 0.3882 | 1749003.08 | LogNormal | 0.30417 | 822.99 | LogNormal | 0.3018 | 7315.48 | LogNormal | 0.30308 | 645.35 | LogNormal | 0.30308
D5092.032j | D5092.032j | Diesel generator - Capacity: 1200 to 2000 kVa - Vibration isolated equipment that is not snubbed or restrained - Anchorage fragility only | 245.4 | LogNormal | 0.38177 | 138029.37 | LogNormal | 0.30391 | [9 empty] | 7365.83 | LogNormal | 0.38177 | 2612291.91 | LogNormal | 0.30391
D5092.032k | D5092.032k | Diesel generator - Capacity: 1200 to 2000 kVa - Vibration isolated equipment that is not snubbed or restrained - Equipment fragility only | 62.1 | LogNormal | 0.30231 | 413.99 | LogNormal | 0.30308 | 33.91 | LogNormal | 0.30308 | 49.68 | LogNormal | 0.30308 |  |  |  | 1371.65 | LogNormal | 0.30231 | 9144.35 | LogNormal | 0.30308 | 645.35 | LogNormal | 0.30308 | 1097.32 | LogNormal | 0.30308
D5092.032l | D5092.032l | Diesel generator - Capacity: 1200 to 2000 kVa - Vibration isolated equipment that is not snubbed or restrained - Combined anchorage/isolator & equipment fragility | 245.4 | LogNormal | 0.38177 | 138029.37 | LogNormal | 0.30391 | 62.1 | LogNormal | 0.30231 | 413.99 | LogNormal | 0.30308 | 33.91 | LogNormal | 0.30308 | 7365.83 | LogNormal | 0.38177 | 2612291.91 | LogNormal | 0.30391 | 1371.65 | LogNormal | 0.30231 | 9144.35 | LogNormal | 0.30308 | 645.35 | LogNormal | 0.30308
D5092.033a | D5092.033a | Diesel generator - Capacity: 100 to <350 kVA - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only | 110.49 | LogNormal | 0.5168 | 24454.43 | LogNormal | 0.30495 | [9 empty] | 3225.95 | LogNormal | 0.5168 | 464784.95 | LogNormal | 0.30495
D5092.033b | D5092.033b | Diesel generator - Capacity: 100 to <350 kVA - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only | 8.28 | LogNormal | 0.30308 | 103.5 | LogNormal | 0.30262 | 20.7 | LogNormal | 0.30079 | 20.7 | LogNormal | 0.30079 |  |  |  | 182.89 | LogNormal | 0.30308 | 2286.09 | LogNormal | 0.30262 | 457.22 | LogNormal | 0.30079 | 457.22 | LogNormal | 0.30079
D5092.033c | D5092.033c | Diesel generator - Capacity: 100 to <350 kVA - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | 110.49 | LogNormal | 0.5168 | 24454.43 | LogNormal | 0.30495 | 8.28 | LogNormal | 0.30308 | 103.5 | LogNormal | 0.30262 | 14.13 | LogNormal | 0.30079 | 3225.95 | LogNormal | 0.5168 | 464784.95 | LogNormal | 0.30495 | 182.89 | LogNormal | 0.30308 | 2286.09 | LogNormal | 0.30262 | 268.9 | LogNormal | 0.30079
D5092.033d | D5092.033d | Diesel generator - Capacity: 350 to <750 kVA - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only | 168.31 | Normal | 0.47039 | 49326.2 | LogNormal | 0.30451 | [9 empty] | 5000.18 | Normal | 0.47039 | 933631.28 | LogNormal | 0.30451
D5092.033e | D5092.033e | Diesel generator - Capacity: 350 to <750 kVA - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only | 16.56 | LogNormal | 0.30308 | 206.99 | LogNormal | 0.30308 | 22.61 | LogNormal | 0.30308 | 33.12 | LogNormal | 0.30308 |  |  |  | 365.77 | LogNormal | 0.30308 | 4572.17 | LogNormal | 0.30308 | 430.23 | LogNormal | 0.30308 | 731.55 | LogNormal | 0.30308
D5092.033f | D5092.033f | Diesel generator - Capacity: 350 to <750 kVA - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | 168.31 | Normal | 0.47039 | 49326.2 | LogNormal | 0.30451 | 16.56 | LogNormal | 0.30308 | 206.99 | LogNormal | 0.30308 | 22.61 | LogNormal | 0.30308 | 5000.18 | Normal | 0.47039 | 933631.28 | LogNormal | 0.30451 | 365.77 | LogNormal | 0.30308 | 4572.17 | LogNormal | 0.30308 | 430.23 | LogNormal | 0.30308
D5092.033g | D5092.033g | Diesel generator - Capacity: 750 to 1200 kVA - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only | 245.4 | Normal | 0.3882 | 92485.37 | LogNormal | 0.30417 | [9 empty] | 7365.83 | Normal | 0.3882 | 1749003.08 | LogNormal | 0.30417
D5092.033h | D5092.033h | Diesel generator - Capacity: 750 to 1200 kVA - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only | 37.26 | LogNormal | 0.3018 | 331.19 | LogNormal | 0.30308 | 33.91 | LogNormal | 0.30308 | 49.68 | LogNormal | 0.30308 |  |  |  | 822.99 | LogNormal | 0.3018 | 7315.48 | LogNormal | 0.30308 | 645.35 | LogNormal | 0.30308 | 1097.32 | LogNormal | 0.30308
D5092.033i | D5092.033i | Diesel generator - Capacity: 750 to 1200 kVA - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | 245.4 | Normal | 0.3882 | 92485.37 | LogNormal | 0.30417 | 37.26 | LogNormal | 0.3018 | 331.19 | LogNormal | 0.30308 | 33.91 | LogNormal | 0.30308 | 7365.83 | Normal | 0.3882 | 1749003.08 | LogNormal | 0.30417 | 822.99 | LogNormal | 0.3018 | 7315.48 | LogNormal | 0.30308 | 645.35 | LogNormal | 0.30308
D5092.033j | D5092.033j | Diesel generator - Capacity: 1200 to 2000 kVa - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Anchorage fragility only | 245.4 | LogNormal | 0.38177 | 138029.37 | LogNormal | 0.30391 | [9 empty] | 7365.83 | LogNormal | 0.38177 | 2612291.91 | LogNormal | 0.30391
D5092.033k | D5092.033k | Diesel generator - Capacity: 1200 to 2000 kVa - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Equipment fragility only | 62.1 | LogNormal | 0.30231 | 413.99 | LogNormal | 0.30308 | 33.91 | LogNormal | 0.30308 | 49.68 | LogNormal | 0.30308 |  |  |  | 1371.65 | LogNormal | 0.30231 | 9144.35 | LogNormal | 0.30308 | 645.35 | LogNormal | 0.30308 | 1097.32 | LogNormal | 0.30308
D5092.033l | D5092.033l | Diesel generator - Capacity: 1200 to 2000 kVa - Equipment that is either hard anchored or is vibration isolated with seismic snubbers/restraints - Combined anchorage/isolator & equipment fragility | 245.4 | LogNormal | 0.38177 | 138029.37 | LogNormal | 0.30391 | 62.1 | LogNormal | 0.30231 | 413.99 | LogNormal | 0.30308 | 33.91 | LogNormal | 0.30308 | 7365.83 | LogNormal | 0.38177 | 2612291.91 | LogNormal | 0.30391 | 1371.65 | LogNormal | 0.30231 | 9144.35 | LogNormal | 0.30308 | 645.35 | LogNormal | 0.30308
E2022.001 | E2022.001 | Modular office work stations. | BY USER | BY USER | BY USER | [12 empty] | BY USER | BY USER | BY USER
E2022.010 | E2022.010 | Unsecured fragile objects on shelves, unknown restraint | BY USER | BY USER | BY USER | [12 empty] | BY USER | BY USER | BY USER
E2022.011 | E2022.011 | Fragile contents secured by museum putty, Velcro or other weak but sticky stuff | BY USER | BY USER | BY USER | [12 empty] | BY USER | BY USER | BY USER
E2022.012 | E2022.012 | Fragile contents on shelves in storage cabinets with latches | BY USER | BY USER | BY USER | [12 empty] | BY USER | BY USER | BY USER
E2022.013 | E2022.013 | Unsecured fragile objects on shelves, low friction surface | BY USER | BY USER | BY USER | [12 empty] | BY USER | BY USER | BY USER
E2022.020 | E2022.020 | Home entertainment equipment, unknown installation | BY USER | BY USER | BY USER | [12 empty] | BY USER | BY USER | BY USER
E2022.021 | E2022.021 | Electronic equipment on wall mount brackets | BY USER | BY USER | BY USER | [12 empty] | BY USER | BY USER | BY USER
E2022.022 | E2022.022 | Desktop electronics including computers, monitors, stereos, etc on a slip resistant surface | BY USER | BY USER | BY USER | [12 empty] | BY USER | BY USER | BY USER
E2022.023 | E2022.023 | Desktop electronics including computers, monitors, stereos, etc, smooth surface | BY USER | BY USER | BY USER | [12 empty] | BY USER | BY USER | BY USER
E2022.102a | E2022.102a | Bookcase, 2 shelves, unanchored laterally | BY USER | BY USER | BY USER | [12 empty] | BY USER | BY USER | BY USER
E2022.102b | E2022.102b | Bookcase, 2 shelves, anchored laterally | BY USER | BY USER | BY USER | [12 empty] | BY USER | BY USER | BY USER
E2022.103a | E2022.103a | Bookcase, 3 shelves, unanchored laterally | BY USER | BY USER | BY USER | [12 empty] | BY USER | BY USER | BY USER
E2022.103b | E2022.103b | Bookcase, 3 shelves, anchored laterally | BY USER | BY USER | BY USER | [12 empty] | BY USER | BY USER | BY USER
E2022.104a | E2022.104a | Bookcase, 4 shelves, unanchored laterally | BY USER | BY USER | BY USER | [12 empty] | BY USER | BY USER | BY USER
E2022.104b | E2022.104b | Bookcase, 4 shelves, anchored laterally | BY USER | BY USER | BY USER | [12 empty] | BY USER | BY USER | BY USER
E2022.105a | E2022.105a | Bookcase, 5 shelves, unanchored laterally | BY USER | BY USER | BY USER | [12 empty] | BY USER | BY USER | BY USER
E2022.105b | E2022.105b | Bookcase, 5 shelves, anchored laterally | BY USER | BY USER | BY USER | [12 empty] | BY USER | BY USER | BY USER
E2022.106a | E2022.106a | Bookcase, 6 shelves, unanchored laterally | BY USER | BY USER | BY USER | [12 empty] | BY USER | BY USER | BY USER
E2022.106b | E2022.106b | Bookcase, 6 shelves, anchored laterally | BY USER | BY USER | BY USER | [12 empty] | BY USER | BY USER | BY USER
E2022.112a | E2022.112a | Vertical Filing Cabinet, 2 drawer, unanchored laterally | BY USER | BY USER | BY USER | [12 empty] | BY USER | BY USER | BY USER
E2022.112b | E2022.112b | Vertical Filing Cabinet, 2 drawer, anchored laterally | BY USER | BY USER | BY USER | [12 empty] | BY USER | BY USER | BY USER
E2022.114a | E2022.114a | Vertical Filing Cabinet, 4 drawer, unanchored laterally | BY USER | BY USER | BY USER | [12 empty] | BY USER | BY USER | BY USER
E2022.114b | E2022.114b | Vertical Filing Cabinet, 4 drawer, anchored laterally | BY USER | BY USER | BY USER | [12 empty] | BY USER | BY USER | BY USER
E2022.124a | E2022.124a | Lateral Filing Cabinet, 2 drawer, unanchored laterally | BY USER | BY USER | BY USER | [12 empty] | BY USER | BY USER | BY USER
E2022.124b | E2022.124b | Lateral Filing Cabinet, 2 drawer, anchored laterally | BY USER | BY USER | BY USER | [12 empty] | BY USER | BY USER | BY USER
E2022.125a | E2022.125a | Lateral Filing Cabinet, 4 drawer, unanchored laterally | BY USER | BY USER | BY USER | [12 empty] | BY USER | BY USER | BY USER
E2022.125b | E2022.125b | Lateral Filing Cabinet, 4 drawer, anchored laterally | BY USER | BY USER | BY USER | [12 empty] | BY USER | BY USER | BY USER
F1012.001 | F1012.001 | Storage racks designed and installed before 2007, big box retail (12' to 15' tall) | 14.5 | LogNormal | 0.44007 | 8496 | LogNormal | 0.38146 | [9 empty] | 443.5 | LogNormal | 0.44007 | 260247 | LogNormal | 0.38146
D2021.011a | D2021.011a | Cold or Hot Potable - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC A or B, PIPING FRAGILITY | 33.07 | LogNormal | 0.80357 | 484.53 | LogNormal | 0.47626 | [9 empty] | 864.51 | LogNormal | 0.80357 | 12415.24 | LogNormal | 0.47626
D2021.011b | D2021.011b | Cold or Hot Potable - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC A or B, BRACING FRAGILITY | 33.07 | LogNormal | 0.65274 | 484.53 | LogNormal | 0.25857 | [9 empty] | 864.51 | LogNormal | 0.65274 | 12415.24 | LogNormal | 0.25857
D2021.012a | D2021.012a | Cold or Hot Potable - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC C, PIPING FRAGILITY | 33.07 | LogNormal | 0.80357 | 484.53 | LogNormal | 0.47626 | [9 empty] | 864.51 | LogNormal | 0.80357 | 12415.24 | LogNormal | 0.47626
D2021.012b | D2021.012b | Cold or Hot Potable - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC C, BRACING FRAGILITY | 35.97 | LogNormal | 0.65274 | 35.97 | LogNormal | 0.25857 | [9 empty] | 1021.56 | LogNormal | 0.65274 | 1021.56 | LogNormal | 0.25857
D2021.013a | D2021.013a | Cold or Hot Potable - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC D, E, or F, PIPING FRAGILITY | 33.07 | LogNormal | 0.80357 | 484.53 | LogNormal | 0.47626 | [9 empty] | 864.51 | LogNormal | 0.80357 | 12415.24 | LogNormal | 0.47626
D2021.013b | D2021.013b | Cold or Hot Potable - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC D, E, or F, BRACING FRAGILITY | 35.97 | LogNormal | 0.65274 | [12 empty] | 1021.56 | LogNormal | 0.65274
D2021.014a | D2021.014a | Cold or Hot Potable - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC D, E, or F (OSHPD or sim), PIPING FRAGILITY | 33.07 | LogNormal | 0.80357 | 484.53 | LogNormal | 0.47626 | [9 empty] | 864.51 | LogNormal | 0.80357 | 12415.24 | LogNormal | 0.47626
D2021.014b | D2021.014b | Cold or Hot Potable - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC D, E, or F (OSHPD or sim), BRACING FRAGILITY | 35.97 | LogNormal | 0.65274 | [12 empty] | 1021.56 | LogNormal | 0.65274
D2021.021a | D2021.021a | Cold or Hot Potable Water Piping (dia > 2.5 inches), SDC A or B, PIPING FRAGILITY | 22.67 | LogNormal | 0.69527 | 363.7 | LogNormal | 0.47493 | [9 empty] | 572.49 | LogNormal | 0.69527 | 9221.31 | LogNormal | 0.47493
D2021.022a | D2021.022a | Cold or Hot Potable Water Piping (dia > 2.5 inches), SDC C, PIPING FRAGILITY | 22.67 | LogNormal | 0.69527 | 363.7 | LogNormal | 0.47493 | [9 empty] | 572.49 | LogNormal | 0.69527 | 9221.31 | LogNormal | 0.47493
D2021.023a | D2021.023a | Cold or Hot Potable Water Piping (dia > 2.5 inches), SDC D,E,F, PIPING FRAGILITY | 22.67 | LogNormal | 0.69527 | 363.7 | LogNormal | 0.47493 | [9 empty] | 572.49 | LogNormal | 0.69527 | 9221.31 | LogNormal | 0.47493
D2021.023b | D2021.023b | Cold or Hot Potable Water Piping (dia > 2.5 inches), SDC D,E,F, BRACING FRAGILITY | 40.01 | LogNormal | 0.69527 | 0 | LogNormal | 0.69527 | [9 empty] | 1104.76 | LogNormal | 0.69527 | 0 | LogNormal | 0.69527
D2021.024a | D2021.024a | Cold or Hot Potable Water Piping (dia > 2.5 inches), SDC D,E,F (OSPHD or sim), PIPING FRAGILITY | 22.67 | LogNormal | 0.69527 | 363.7 | LogNormal | 0.47493 | [9 empty] | 572.49 | LogNormal | 0.69527 | 9221.31 | LogNormal | 0.47493
D2021.024b | D2021.024b | Cold or Hot Potable Water Piping (dia > 2.5 inches), SDC D,E,F (OSPHD or sim), BRACING FRAGILITY | 40.01 | LogNormal | 0.69527 | 0 | LogNormal | 0.69527 | [9 empty] | 1104.76 | LogNormal | 0.69527 | 0 | LogNormal | 0.69527
D2022.011a | D2022.011a | Heating hot Water Piping - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC A or B, PIPING FRAGILITY | 22.67 | LogNormal | 0.80357 | 363.7 | LogNormal | 0.47626 | [9 empty] | 572.49 | LogNormal | 0.80357 | 9221.31 | LogNormal | 0.47626
D2022.011b | D2022.011b | Heating hot Water Piping - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC A or B, BRACING FRAGILITY | 40.01 | LogNormal | 0.65274 | 628.49 | LogNormal | 0.25857 | [9 empty] | 1104.76 | LogNormal | 0.65274 | 16560.36 | LogNormal | 0.25857
D2022.012a | D2022.012a | Heating hot Water Piping - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC C, PIPING FRAGILITY | 22.67 | LogNormal | 0.80357 | 363.7 | LogNormal | 0.47626 | [9 empty] | 572.49 | LogNormal | 0.80357 | 9221.31 | LogNormal | 0.47626
D2022.012b | D2022.012b | Heating hot Water Piping - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC C, BRACING FRAGILITY | 40.01 | LogNormal | 0.65274 | 628.49 | LogNormal | 0.25857 | [9 empty] | 1104.76 | LogNormal | 0.65274 | 16560.36 | LogNormal | 0.25857
D2022.013a | D2022.013a | Heating hot Water Piping - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC D, E, or F, PIPING FRAGILITY | 22.67 | LogNormal | 0.80357 | 363.7 | LogNormal | 0.47626 | [9 empty] | 572.49 | LogNormal | 0.80357 | 9221.31 | LogNormal | 0.47626
D2022.013b | D2022.013b | Heating hot Water Piping - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC D, E, or F, BRACING FRAGILITY | 40.01 | LogNormal | 0.65274 | [12 empty] | 1104.76 | LogNormal | 0.65274
D2022.014a | D2022.014a | Heating hot Water Piping - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC D, E, or F (OSHPD or sim), PIPING FRAGILITY | 22.67 | LogNormal | 0.80357 | 363.7 | LogNormal | 0.47626 | [9 empty] | 572.49 | LogNormal | 0.80357 | 9221.31 | LogNormal | 0.47626
D2022.014b | D2022.014b | Heating hot Water Piping - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC D, E, or F (OSHPD or sim), BRACING FRAGILITY | 40.01 | LogNormal | 0.65274 | [12 empty] | 1104.76 | LogNormal | 0.65274
D2022.021a | D2022.021a | Heating hot Water Piping - Large Diameter Welded Steel - (greater than 2.5 inches in diameter), SDC A or B, PIPING FRAGILITY | 33.07 | LogNormal | 0.69527 | 484.53 | LogNormal | 0.47493 | [9 empty] | 864.51 | LogNormal | 0.69527 | 12415.24 | LogNormal | 0.47493
D2022.022a | D2022.022a | Heating hot Water Piping - Large Diameter Welded Steel - (greater than 2.5 inches in diameter), SDC C, PIPING FRAGILITY | 33.07 | LogNormal | 0.69527 | 484.53 | LogNormal | 0.47493 | [9 empty] | 864.51 | LogNormal | 0.69527 | 12415.24 | LogNormal | 0.47493
D2022.023a | D2022.023a | Heating hot Water Piping - Large Diameter Welded Steel - (greater than 2.5 inches in diameter), SDC D, E, or F, PIPING FRAGILITY | 33.07 | LogNormal | 0.69527 | 484.53 | LogNormal | 0.47493 | [9 empty] | 864.51 | LogNormal | 0.69527 | 12415.24 | LogNormal | 0.47493
D2022.023b | D2022.023b | Heating hot Water Piping - Large Diameter Welded Steel - (greater than 2.5 inches in diameter), SDC D, E, or F, BRACING FRAGILITY | 35.97 | LogNormal | 0.69527 | 35.97 | LogNormal | 0.69527 | [9 empty] | 1021.56 | LogNormal | 0.69527 | 1021.56 | LogNormal | 0.69527
D2022.024a | D2022.024a | Heating hot Water Piping - Large Diameter Welded Steel - (greater than 2.5 inches in diameter), SDC D, E, or F (OSHPD or sim), PIPING FRAGILITY | 33.07 | LogNormal | 0.69527 | 484.53 | LogNormal | 0.47493 | [9 empty] | 864.51 | LogNormal | 0.69527 | 12415.24 | LogNormal | 0.47493
D2022.024b | D2022.024b | Heating hot Water Piping - Large Diameter Welded Steel - (greater than 2.5 inches in diameter), SDC D, E, or F (OSHPD or sim), BRACING FRAGILITY | 35.97 | LogNormal | 0.69527 | 35.97 | LogNormal | 0.69527 | [9 empty] | 1021.56 | LogNormal | 0.69527 | 1021.56 | LogNormal | 0.69527
D2031.011b | D2031.011b | Sanitary Waste Piping - Cast Iron w/flexible couplings, SDC A,B, BRACING FRAGILITY | 45.61 | LogNormal | 0.62772 | 398.23 | LogNormal | 0.42209 | [9 empty] | 1317.27 | LogNormal | 0.62772 | 10133.86 | LogNormal | 0.42209
D2031.012b | D2031.012b | Sanitary Waste Piping - Cast Iron w/flexible couplings, SDC C, BRACING FRAGILITY | 45.61 | LogNormal | 0.62772 | 398.23 | LogNormal | 0.42209 | [9 empty] | 1317.27 | LogNormal | 0.62772 | 10133.86 | LogNormal | 0.42209
D2031.013b | D2031.013b | Sanitary Waste Piping - Cast Iron w/flexible couplings, SDC D,E,F, BRACING FRAGILITY | 45.61 | LogNormal | 0.62772 | [12 empty] | 1317.27 | LogNormal | 0.62772
D2031.014b | D2031.014b | Sanitary Waste Piping - Cast Iron w/flexible couplings, SDC D,E,F (OSHPD or sim), BRACING FRAGILITY | 45.61 | LogNormal | 0.62772 | [12 empty] | 1317.27 | LogNormal | 0.62772
D2031.021a | D2031.021a | Sanitary Waste Piping - Cast Iron w/bell and spigot couplings, SDC A,B, PIPING FRAGILITY | 484.53 | Normal | 0.40151 | [12 empty] | 12415.24 | Normal | 0.40151
D2031.021b | D2031.021b | Sanitary Waste Piping - Cast Iron w/bell and spigot couplings, SDC A,B, BRACING FRAGILITY | 45.61 | LogNormal | 0.74853 | 657.15 | Normal | 0.37855 | [9 empty] | 1317.27 | LogNormal | 0.74853 | 16977.99 | Normal | 0.37855
D2031.022a | D2031.022a | Sanitary Waste Piping - Cast Iron w/bell and spigot couplings, SDC C, PIPING FRAGILITY | 484.53 | Normal | 0.40151 | [12 empty] | 12415.24 | Normal | 0.40151
D2031.022b | D2031.022b | Sanitary Waste Piping - Cast Iron w/bell and spigot couplings, SDC C, BRACING FRAGILITY | 45.61 | LogNormal | 0.74853 | 657.15 | Normal | 0.37855 | [9 empty] | 1317.27 | LogNormal | 0.74853 | 16977.99 | Normal | 0.37855
D2031.023a | D2031.023a | Sanitary Waste Piping - Cast Iron w/bell and spigot couplings, SDC D,E,F, PIPING FRAGILITY | 484.53 | Normal | 0.40151 | [12 empty] | 12415.24 | Normal | 0.40151
D2031.023b | D2031.023b | Sanitary Waste Piping - Cast Iron w/bell and spigot couplings, SDC D,E,F, BRACING FRAGILITY | 45.61 | LogNormal | 0.74853 | [12 empty] | 1317.27 | LogNormal | 0.74853
D2031.024a | D2031.024a | Sanitary Waste Piping - Cast Iron w/bell and spigot couplings, SDC D,E,F (OSHPD or sim), PIPING FRAGILITY | 484.53 | Normal | 0.40151 | [12 empty] | 12415.24 | Normal | 0.40151
D2031.024b | D2031.024b | Sanitary Waste Piping - Cast Iron w/bell and spigot couplings, SDC D,E,F (OSHPD or sim), BRACING FRAGILITY | 45.61 | LogNormal | 0.74853 | [12 empty] | 1317.27 | LogNormal | 0.74853
D2051.011a | D2051.011a | Chilled Water Piping - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC A or B, PIPING FRAGILITY | 22.67 | LogNormal | 0.80357 | 363.7 | LogNormal | 0.47626 | [9 empty] | 572.49 | LogNormal | 0.80357 | 9221.31 | LogNormal | 0.47626
D2051.011b | D2051.011b | Chilled Water Piping - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC A or B, BRACING FRAGILITY | 40.01 | LogNormal | 0.65274 | 628.49 | LogNormal | 0.25857 | [9 empty] | 1104.76 | LogNormal | 0.65274 | 16560.36 | LogNormal | 0.25857
D2051.012a | D2051.012a | Chilled Water Piping - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC C, PIPING FRAGILITY | 22.67 | LogNormal | 0.80357 | 363.7 | LogNormal | 0.47626 | [9 empty] | 572.49 | LogNormal | 0.80357 | 9221.31 | LogNormal | 0.47626
D2051.012b | D2051.012b | Chilled Water Piping - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC C, BRACING FRAGILITY | 40.01 | LogNormal | 0.65274 | 628.49 | LogNormal | 0.25857 | [9 empty] | 1104.76 | LogNormal | 0.65274 | 16560.36 | LogNormal | 0.25857
D2051.013a | D2051.013a | Chilled Water Piping - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC D, E, or F, PIPING FRAGILITY | 22.67 | LogNormal | 0.80357 | 363.7 | LogNormal | 0.47626 | [9 empty] | 572.49 | LogNormal | 0.80357 | 9221.31 | LogNormal | 0.47626
D2051.013b | D2051.013b | Chilled Water Piping - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC D, E, or F, BRACING FRAGILITY | 40.01 | LogNormal | 0.65274 | [12 empty] | 1104.76 | LogNormal | 0.65274
D2051.014a | D2051.014a | Chilled Water Piping - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC D, E, or F (OSHPD or sim), PIPING FRAGILITY | 22.67 | LogNormal | 0.80357 | 363.7 | LogNormal | 0.47626 | [9 empty] | 572.49 | LogNormal | 0.80357 | 9221.31 | LogNormal | 0.47626
D2051.014b | D2051.014b | Chilled Water Piping - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC D, E, or F (OSHPD or sim), BRACING FRAGILITY | 40.01 | LogNormal | 0.65274 | [12 empty] | 1104.76 | LogNormal | 0.65274
D2051.021a | D2051.021a | Chilled Water Piping - Large Diameter Welded Steel - (greater than 2.5 inches in diameter), SDC A or B, PIPING FRAGILITY | 33.07 | LogNormal | 0.69527 | 484.53 | LogNormal | 0.47493 | [9 empty] | 864.51 | LogNormal | 0.69527 | 12415.24 | LogNormal | 0.47493
D2051.021b | D2051.021b | Chilled Water Piping - Large Diameter Welded Steel - (greater than 2.5 inches in diameter), SDC A or B, BRACING FRAGILITY | 33.07 | LogNormal | 0.69527 | [12 empty] | 864.51 | LogNormal | 0.69527
D2051.022a | D2051.022a | Chilled Water Piping - Large Diameter Welded Steel - (greater than 2.5 inches in diameter), SDC C, PIPING FRAGILITY | 33.07 | LogNormal | 0.69527 | 484.53 | LogNormal | 0.47493 | [9 empty] | 864.51 | LogNormal | 0.69527 | 12415.24 | LogNormal | 0.47493
D2051.023a | D2051.023a | Chilled Water Piping - Large Diameter Welded Steel - (greater than 2.5 inches in diameter), SDC D, E, or F, PIPING FRAGILITY | 35.97 | LogNormal | 0.69527 | 35.97 | LogNormal | 0.47493 | [9 empty] | 1021.56 | LogNormal | 0.69527 | 1021.56 | LogNormal | 0.47493
D2051.023b | D2051.023b | Chilled Water Piping - Large Diameter Welded Steel - (greater than 2.5 inches in diameter), SDC D, E, or F, BRACING FRAGILITY | 33.07 | LogNormal | 0.69527 | 484.53 | LogNormal | 0.69527 | [9 empty] | 864.51 | LogNormal | 0.69527 | 12415.24 | LogNormal | 0.69527
D2051.024a | D2051.024a | Chilled Water Piping - Large Diameter Welded Steel - (greater than 2.5 inches in diameter), SDC D, E, or F (OSHPD or sim), PIPING FRAGILITY | 35.97 | LogNormal | 0.69527 | 35.97 | LogNormal | 0.47493 | [9 empty] | 1021.56 | LogNormal | 0.69527 | 1021.56 | LogNormal | 0.47493
D2051.024b | D2051.024b | Chilled Water Piping - Large Diameter Welded Steel - (greater than 2.5 inches in diameter), SDC D, E, or F (OSHPD or sim), BRACING FRAGILITY | 33.07 | LogNormal | 0.69527 | 484.53 | LogNormal | 0.69527 | [9 empty] | 864.51 | LogNormal | 0.69527 | 12415.24 | LogNormal | 0.69527
D2061.011a | D2061.011a | Steam Piping - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC A or B, PIPING FRAGILITY | 22.67 | LogNormal | 0.80357 | 363.7 | LogNormal | 0.47626 | [9 empty] | 572.49 | LogNormal | 0.80357 | 9221.31 | LogNormal | 0.47626
D2061.011b | D2061.011b | Steam Piping - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC A or B, BRACING FRAGILITY | 40.01 | LogNormal | 0.65274 | 628.49 | LogNormal | 0.25857 | [9 empty] | 1104.76 | LogNormal | 0.65274 | 16560.36 | LogNormal | 0.25857
D2061.012a | D2061.012a | Steam Piping - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC C, PIPING FRAGILITY | 22.67 | LogNormal | 0.80357 | 363.7 | LogNormal | 0.47626 | [9 empty] | 572.49 | LogNormal | 0.80357 | 9221.31 | LogNormal | 0.47626
D2061.012b | D2061.012b | Steam Piping - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC C, BRACING FRAGILITY | 40.01 | LogNormal | 0.65274 | 628.49 | LogNormal | 0.25857 | [9 empty] | 1104.76 | LogNormal | 0.65274 | 16560.36 | LogNormal | 0.25857
D2061.013a | D2061.013a | Steam Piping - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC D, E, or F, PIPING FRAGILITY | 22.67 | LogNormal | 0.80357 | 363.7 | LogNormal | 0.47626 | [9 empty] | 572.49 | LogNormal | 0.80357 | 9221.31 | LogNormal | 0.47626
D2061.013b | D2061.013b | Steam Piping - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC D, E, or F, BRACING FRAGILITY | 40.01 | LogNormal | 0.65274 | [12 empty] | 1104.76 | LogNormal | 0.65274
D2061.014a | D2061.014a | Steam Piping - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC D, E, or F (OSHPD or sim), PIPING FRAGILITY | 22.67 | LogNormal | 0.80357 | 363.7 | LogNormal | 0.47626 | [9 empty] | 572.49 | LogNormal | 0.80357 | 9221.31 | LogNormal | 0.47626
D2061.014b | D2061.014b | Steam Piping - Small Diameter Threaded Steel - (2.5 inches in diameter or less), SDC D, E, or F (OSHPD or sim), BRACING FRAGILITY | 40.01 | LogNormal | 0.65274 | [12 empty] | 1104.76 | LogNormal | 0.65274
D2061.021a | D2061.021a | Steam Piping - Large Diameter Welded Steel - (greater than 2.5 inches in diameter), SDC A or B, PIPING FRAGILITY | 33.07 | LogNormal | 0.69527 | 484.53 | LogNormal | 0.47493 | [9 empty] | 864.51 | LogNormal | 0.69527 | 12415.24 | LogNormal | 0.47493
D2061.022a | D2061.022a | Steam Piping - Large Diameter Welded Steel - (greater than 2.5 inches in diameter), SDC C, PIPING FRAGILITY | 33.07 | LogNormal | 0.69527 | 484.53 | LogNormal | 0.47493 | [9 empty] | 864.51 | LogNormal | 0.69527 | 12415.24 | LogNormal | 0.47493
0
0
0